## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-505_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-505_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-505_0_6_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_261-505_0_6_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_261-505_0_6_node_40 | 0.4 | n |  | TRUE
5 | bus_LV_261-505_0_6_node_88 | 0.4 | n |  | TRUE
6 | bus_LV_261-505_0_6_node_41 | 0.4 | n |  | TRUE
7 | bus_LV_261-505_0_6_node_153 | 0.4 | n |  | TRUE
8 | bus_LV_261-505_0_6_node_29 | 0.4 | n |  | TRUE
9 | bus_LV_261-505_0_6_node_156 | 0.4 | n |  | TRUE
10 | bus_LV_261-505_0_6_node_39 | 0.4 | n |  | TRUE
11 | bus_LV_261-505_0_6_node_26 | 0.4 | n |  | TRUE
12 | bus_LV_261-505_0_6_node_19 | 0.4 | n |  | TRUE
13 | bus_LV_261-505_0_6_node_36 | 0.4 | n |  | TRUE
14 | bus_LV_261-505_0_6_node_116 | 0.4 | n |  | TRUE
15 | bus_LV_261-505_0_6_node_155 | 0.4 | n |  | TRUE
16 | bus_LV_261-505_0_6_node_9 | 0.4 | n |  | TRUE
17 | bus_LV_261-505_0_6_node_38 | 0.4 | n |  | TRUE
18 | bus_LV_261-505_0_6_node_7 | 0.4 | n |  | TRUE
19 | bus_LV_261-505_0_6_node_13 | 0.4 | n |  | TRUE
20 | bus_LV_261-505_0_6_node_17 | 0.4 | n |  | TRUE
21 | bus_LV_261-505_0_6_node_15 | 0.4 | n |  | TRUE
22 | bus_LV_261-505_0_6_node_12 | 0.4 | n |  | TRUE
23 | bus_LV_261-505_0_6_node_44 | 0.4 | n |  | TRUE
24 | bus_LV_261-505_0_6_node_21 | 0.4 | n |  | TRUE
25 | bus_LV_261-505_0_6_node_95 | 0.4 | n |  | TRUE
26 | bus_LV_261-505_0_6_node_115 | 0.4 | n |  | TRUE
27 | bus_LV_261-505_0_6_node_22 | 0.4 | n |  | TRUE
28 | bus_LV_261-505_0_6_node_105 | 0.4 | n |  | TRUE
29 | bus_LV_261-505_0_6_node_106 | 0.4 | n |  | TRUE
30 | bus_LV_261-505_0_6_node_104 | 0.4 | n |  | TRUE
31 | bus_LV_261-505_0_6_node_138 | 0.4 | n |  | TRUE
32 | bus_LV_261-505_0_6_node_28 | 0.4 | n |  | TRUE
33 | bus_LV_261-505_0_6_node_43 | 0.4 | n |  | TRUE
34 | bus_LV_261-505_0_6_node_140 | 0.4 | n |  | TRUE
35 | bus_LV_261-505_0_6_node_30 | 0.4 | n |  | TRUE
36 | bus_LV_261-505_0_6_node_56 | 0.4 | n |  | TRUE
37 | bus_LV_261-505_0_6_node_53 | 0.4 | n |  | TRUE
38 | bus_LV_261-505_0_6_node_32 | 0.4 | n |  | TRUE
39 | bus_LV_261-505_0_6_node_149 | 0.4 | n |  | TRUE
40 | bus_LV_261-505_0_6_node_147 | 0.4 | n |  | TRUE
41 | bus_LV_261-505_0_6_node_33 | 0.4 | n |  | TRUE
42 | bus_LV_261-505_0_6_node_97 | 0.4 | n |  | TRUE
43 | bus_LV_261-505_0_6_node_107 | 0.4 | n |  | TRUE
44 | bus_LV_261-505_0_6_node_34 | 0.4 | n |  | TRUE
45 | bus_LV_261-505_0_6_node_35 | 0.4 | n |  | TRUE
46 | bus_LV_261-505_0_6_node_102 | 0.4 | n |  | TRUE
47 | bus_LV_261-505_0_6_node_101 | 0.4 | n |  | TRUE
48 | bus_LV_261-505_0_6_node_37 | 0.4 | n |  | TRUE
49 | bus_LV_261-505_0_6_node_63 | 0.4 | n |  | TRUE
50 | bus_LV_261-505_0_6_node_91 | 0.4 | n |  | TRUE
51 | bus_LV_261-505_0_6_node_42 | 0.4 | n |  | TRUE
52 | bus_LV_261-505_0_6_node_72 | 0.4 | n |  | TRUE
53 | bus_LV_261-505_0_6_node_136 | 0.4 | n |  | TRUE
54 | bus_LV_261-505_0_6_node_75 | 0.4 | n |  | TRUE
55 | bus_LV_261-505_0_6_node_68 | 0.4 | n |  | TRUE
56 | bus_LV_261-505_0_6_node_69 | 0.4 | n |  | TRUE
57 | bus_LV_261-505_0_6_node_92 | 0.4 | n |  | TRUE
58 | bus_LV_261-505_0_6_node_5 | 0.4 | n |  | TRUE
59 | bus_LV_261-505_0_6_node_6 | 0.4 | n |  | TRUE
60 | bus_LV_261-505_0_6_node_8 | 0.4 | n |  | TRUE
61 | bus_LV_261-505_0_6_node_14 | 0.4 | n |  | TRUE
62 | bus_LV_261-505_0_6_node_11 | 0.4 | n |  | TRUE
63 | bus_LV_261-505_0_6_node_46 | 0.4 | n |  | TRUE
64 | bus_LV_261-505_0_6_node_10 | 0.4 | n |  | TRUE
65 | bus_LV_261-505_0_6_node_47 | 0.4 | n |  | TRUE
66 | bus_LV_261-505_0_6_node_55 | 0.4 | n |  | TRUE
67 | bus_LV_261-505_0_6_node_100 | 0.4 | n |  | TRUE
68 | bus_LV_261-505_0_6_node_93 | 0.4 | n |  | TRUE
69 | bus_LV_261-505_0_6_node_114 | 0.4 | n |  | TRUE
70 | bus_LV_261-505_0_6_node_129 | 0.4 | n |  | TRUE
71 | bus_LV_261-505_0_6_node_131 | 0.4 | n |  | TRUE
72 | bus_LV_261-505_0_6_node_139 | 0.4 | n |  | TRUE
73 | bus_LV_261-505_0_6_node_99 | 0.4 | n |  | TRUE
74 | bus_LV_261-505_0_6_node_130 | 0.4 | n |  | TRUE
75 | bus_LV_261-505_0_6_node_96 | 0.4 | n |  | TRUE
76 | bus_LV_261-505_0_6_node_103 | 0.4 | n |  | TRUE
77 | bus_LV_261-505_0_6_node_128 | 0.4 | n |  | TRUE
78 | bus_LV_261-505_0_6_node_74 | 0.4 | n |  | TRUE
79 | bus_LV_261-505_0_6_node_85 | 0.4 | n |  | TRUE
80 | bus_LV_261-505_0_6_node_57 | 0.4 | n |  | TRUE
81 | bus_LV_261-505_0_6_node_119 | 0.4 | n |  | TRUE
82 | bus_LV_261-505_0_6_node_54 | 0.4 | n |  | TRUE
83 | bus_LV_261-505_0_6_node_98 | 0.4 | n |  | TRUE
84 | bus_LV_261-505_0_6_node_113 | 0.4 | n |  | TRUE
85 | bus_LV_261-505_0_6_node_110 | 0.4 | n |  | TRUE
86 | bus_LV_261-505_0_6_node_108 | 0.4 | n |  | TRUE
87 | bus_LV_261-505_0_6_node_109 | 0.4 | n |  | TRUE
88 | bus_LV_261-505_0_6_node_145 | 0.4 | n |  | TRUE
89 | bus_LV_261-505_0_6_node_154 | 0.4 | n |  | TRUE
90 | bus_LV_261-505_0_6_node_62 | 0.4 | n |  | TRUE
91 | bus_LV_261-505_0_6_node_89 | 0.4 | n |  | TRUE
92 | bus_LV_261-505_0_6_node_117 | 0.4 | n |  | TRUE
93 | bus_LV_261-505_0_6_node_118 | 0.4 | n |  | TRUE
94 | bus_LV_261-505_0_6_node_71 | 0.4 | n |  | TRUE
95 | bus_LV_261-505_0_6_node_152 | 0.4 | n |  | TRUE
96 | bus_LV_261-505_0_6_node_135 | 0.4 | n |  | TRUE
97 | bus_LV_261-505_0_6_node_76 | 0.4 | n |  | TRUE
98 | bus_LV_261-505_0_6_node_141 | 0.4 | n |  | TRUE
99 | bus_LV_261-505_0_6_node_124 | 0.4 | n |  | TRUE
100 | bus_LV_261-505_0_6_node_66 | 0.4 | n |  | TRUE
101 | bus_LV_261-505_0_6_node_90 | 0.4 | n |  | TRUE
102 | bus_LV_261-505_0_6_node_48 | 0.4 | n |  | TRUE
103 | bus_LV_261-505_0_6_node_49 | 0.4 | n |  | TRUE
104 | bus_LV_261-505_0_6_node_50 | 0.4 | n |  | TRUE
105 | bus_LV_261-505_0_6_node_51 | 0.4 | n |  | TRUE
106 | bus_LV_261-505_0_6_node_52 | 0.4 | n |  | TRUE
107 | bus_LV_261-505_0_6_node_59 | 0.4 | n |  | TRUE
108 | bus_LV_261-505_0_6_node_58 | 0.4 | n |  | TRUE
109 | bus_LV_261-505_0_6_node_73 | 0.4 | n |  | TRUE
110 | bus_LV_261-505_0_6_node_84 | 0.4 | n |  | TRUE
111 | bus_LV_261-505_0_6_node_120 | 0.4 | n |  | TRUE
112 | bus_LV_261-505_0_6_node_60 | 0.4 | n |  | TRUE
113 | bus_LV_261-505_0_6_node_61 | 0.4 | n |  | TRUE
114 | bus_LV_261-505_0_6_node_64 | 0.4 | n |  | TRUE
115 | bus_LV_261-505_0_6_node_65 | 0.4 | n |  | TRUE
116 | bus_LV_261-505_0_6_node_67 | 0.4 | n |  | TRUE
117 | bus_LV_261-505_0_6_node_70 | 0.4 | n |  | TRUE
118 | bus_LV_261-505_0_6_node_81 | 0.4 | n |  | TRUE
119 | bus_LV_261-505_0_6_node_125 | 0.4 | n |  | TRUE
120 | bus_LV_261-505_0_6_node_82 | 0.4 | n |  | TRUE
121 | bus_LV_261-505_0_6_node_142 | 0.4 | n |  | TRUE
122 | bus_LV_261-505_0_6_node_123 | 0.4 | n |  | TRUE
123 | bus_LV_261-505_0_6_node_126 | 0.4 | n |  | TRUE
124 | bus_LV_261-505_0_6_node_77 | 0.4 | n |  | TRUE
125 | bus_LV_261-505_0_6_node_78 | 0.4 | n |  | TRUE
126 | bus_LV_261-505_0_6_node_79 | 0.4 | n |  | TRUE
127 | bus_LV_261-505_0_6_node_80 | 0.4 | n |  | TRUE
128 | bus_LV_261-505_0_6_node_132 | 0.4 | n |  | TRUE
129 | bus_LV_261-505_0_6_node_133 | 0.4 | n |  | TRUE
130 | bus_LV_261-505_0_6_node_134 | 0.4 | n |  | TRUE
131 | bus_LV_261-505_0_6_node_83 | 0.4 | n |  | TRUE
132 | bus_LV_261-505_0_6_node_87 | 0.4 | n |  | TRUE
133 | bus_LV_261-505_0_6_node_86 | 0.4 | n |  | TRUE
134 | bus_LV_261-505_0_6_node_111 | 0.4 | n |  | TRUE
135 | bus_LV_261-505_0_6_node_112 | 0.4 | n |  | TRUE
136 | bus_LV_261-505_0_6_node_121 | 0.4 | n |  | TRUE
137 | bus_LV_261-505_0_6_node_122 | 0.4 | n |  | TRUE
138 | bus_LV_261-505_0_6_node_127 | 0.4 | n |  | TRUE
139 | bus_LV_261-505_0_6_node_146 | 0.4 | n |  | TRUE
140 | bus_LV_261-505_0_6_node_143 | 0.4 | n |  | TRUE
141 | bus_LV_261-505_0_6_node_144 | 0.4 | n |  | TRUE
142 | bus_LV_261-505_0_6_node_148 | 0.4 | n |  | TRUE
143 | bus_LV_261-505_0_6_node_150 | 0.4 | n |  | TRUE
144 | bus_LV_261-505_0_6_node_151 | 0.4 | n |  | TRUE
145 | bus_MV_542_0_node_47 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-505_0_6_load_0 | 0 | 0.001939 | 0.00048595 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-505_0_6_load_1 | 1 | 0.0013335 | 0.0003342 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-505_0_6_load_2 | 2 | 0.0031941 | 0.00080052 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-505_0_6_load_88 | 5 | 0.0030387 | 0.00076158 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-505_0_6_load_153 | 7 | 0.0067946 | 0.0017029 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-505_0_6_load_156 | 9 | 0.022446 | 0.0056256 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-505_0_6_load_116 | 14 | 0.0053065 | 0.0013299 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-505_0_6_load_155 | 15 | 0.0075799 | 0.0018997 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-505_0_6_load_7 | 18 | 0.005263 | 0.001319 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-505_0_6_load_15 | 21 | 0.0078601 | 0.0019699 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-505_0_6_load_12 | 22 | 0.003943 | 0.00098822 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-505_0_6_load_44 | 23 | 0.0025152 | 0.00063036 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-505_0_6_load_115 | 26 | 0.0047074 | 0.0011798 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-505_0_6_load_105 | 28 | 0.0044358 | 0.0011117 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-505_0_6_load_106 | 29 | 0.0041542 | 0.0010411 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-505_0_6_load_104 | 30 | 0.0025648 | 0.00064279 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-505_0_6_load_138 | 31 | 0.0063047 | 0.0015801 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_261-505_0_6_load_140 | 34 | 0.0050367 | 0.0012623 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_261-505_0_6_load_53 | 37 | 0.0083194 | 0.002085 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_261-505_0_6_load_149 | 39 | 0.0020744 | 0.00051989 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_261-505_0_6_load_147 | 40 | 0.0044325 | 0.0011109 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_261-505_0_6_load_107 | 43 | 0.0046434 | 0.0011637 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_261-505_0_6_load_102 | 46 | 0.0056891 | 0.0014258 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_261-505_0_6_load_101 | 47 | 0.0035568 | 0.00089143 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_261-505_0_6_load_63 | 49 | 0.012691 | 0.0031806 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_261-505_0_6_load_72 | 52 | 0.0051318 | 0.0012861 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_261-505_0_6_load_136 | 53 | 0.010586 | 0.0026531 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_261-505_0_6_load_75 | 54 | 0.0075134 | 0.001883 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_261-505_0_6_load_92 | 57 | 0.0041876 | 0.0010495 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_261-505_0_6_load_5 | 58 | 0.00598 | 0.0014987 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_261-505_0_6_load_6 | 59 | 0.002294 | 0.00057494 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_261-505_0_6_load_14 | 61 | 0.0061676 | 0.0015457 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_261-505_0_6_load_11 | 62 | 0.0057009 | 0.0014288 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_261-505_0_6_load_46 | 63 | 0.0083482 | 0.0020923 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_261-505_0_6_load_10 | 64 | 0.0036857 | 0.00092373 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_261-505_0_6_load_47 | 65 | 0.0095725 | 0.0023991 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_261-505_0_6_load_55 | 66 | 0.005767 | 0.0014454 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_261-505_0_6_load_100 | 67 | 0.0041578 | 0.0010421 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_261-505_0_6_load_93 | 68 | 0.0019475 | 0.0004881 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_261-505_0_6_load_114 | 69 | 0.0044767 | 0.001122 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_261-505_0_6_load_131 | 71 | 0.0058891 | 0.0014759 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_261-505_0_6_load_139 | 72 | 0.0035677 | 0.00089415 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_261-505_0_6_load_130 | 74 | 0.0041501 | 0.0010401 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_261-505_0_6_load_103 | 76 | 0.004407 | 0.0011045 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_261-505_0_6_load_128 | 77 | 0.004576 | 0.0011469 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_261-505_0_6_load_74 | 78 | 0.0083315 | 0.0020881 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_261-505_0_6_load_85 | 79 | 0.0106 | 0.0026565 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_261-505_0_6_load_57 | 80 | 0.0083292 | 0.0020875 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_261-505_0_6_load_119 | 81 | 0.0083961 | 0.0021043 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_261-505_0_6_load_54 | 82 | 0.0084899 | 0.0021278 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_261-505_0_6_load_113 | 84 | 0.0045482 | 0.0011399 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_261-505_0_6_load_110 | 85 | 0.0043863 | 0.0010993 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_261-505_0_6_load_108 | 86 | 0.0036054 | 0.00090359 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_261-505_0_6_load_109 | 87 | 0.003607 | 0.00090401 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_261-505_0_6_load_154 | 89 | 0.0069823 | 0.0017499 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_261-505_0_6_load_62 | 90 | 0.0017769 | 0.00044535 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_261-505_0_6_load_89 | 91 | 0.011299 | 0.0028317 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_261-505_0_6_load_117 | 92 | 0.004874 | 0.0012215 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_261-505_0_6_load_118 | 93 | 0.0046655 | 0.0011693 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_261-505_0_6_load_71 | 94 | 0.010373 | 0.0025998 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_261-505_0_6_load_152 | 95 | 0.0063712 | 0.0015968 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_261-505_0_6_load_135 | 96 | 0.0067953 | 0.0017031 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_261-505_0_6_load_76 | 97 | 0.015251 | 0.0038222 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_261-505_0_6_load_141 | 98 | 0.0039574 | 0.00099182 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_261-505_0_6_load_124 | 99 | 0.0048772 | 0.0012223 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_261-505_0_6_load_90 | 101 | 0.0041359 | 0.0010366 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_261-505_0_6_load_48 | 102 | 0.0016895 | 0.00042343 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_261-505_0_6_load_49 | 103 | 0.001667 | 0.00041778 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_261-505_0_6_load_50 | 104 | 0.0016912 | 0.00042385 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_261-505_0_6_load_51 | 105 | 0.0067421 | 0.0016897 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_261-505_0_6_load_52 | 106 | 0.0017758 | 0.00044506 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_261-505_0_6_load_59 | 107 | 0.0069056 | 0.0017307 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_261-505_0_6_load_58 | 108 | 0.0038901 | 0.00097495 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_261-505_0_6_load_73 | 109 | 0.0083308 | 0.0020879 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_261-505_0_6_load_84 | 110 | 0.010599 | 0.0026565 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_261-505_0_6_load_120 | 111 | 0.0048756 | 0.0012219 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_261-505_0_6_load_60 | 112 | 0.0072206 | 0.0018097 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_261-505_0_6_load_61 | 113 | 0.0072189 | 0.0018092 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_261-505_0_6_load_64 | 114 | 0.0056398 | 0.0014135 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_261-505_0_6_load_65 | 115 | 0.0017039 | 0.00042704 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_261-505_0_6_load_67 | 116 | 0.0055508 | 0.0013912 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_261-505_0_6_load_70 | 117 | 0.0043875 | 0.0010996 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_261-505_0_6_load_81 | 118 | 0.0018231 | 0.00045691 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_261-505_0_6_load_125 | 119 | 0.0044293 | 0.0011101 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_261-505_0_6_load_82 | 120 | 0.0018239 | 0.00045711 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_261-505_0_6_load_142 | 121 | 0.0037746 | 0.00094601 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_261-505_0_6_load_123 | 122 | 0.0049133 | 0.0012314 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_261-505_0_6_load_126 | 123 | 0.0027358 | 0.00068565 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_261-505_0_6_load_77 | 124 | 0.0068055 | 0.0017056 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_261-505_0_6_load_79 | 126 | 0.0066738 | 0.0016726 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_261-505_0_6_load_80 | 127 | 0.0036712 | 0.00092009 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_261-505_0_6_load_133 | 129 | 0.0063703 | 0.0015966 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_261-505_0_6_load_134 | 130 | 0.014214 | 0.0035624 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_261-505_0_6_load_83 | 131 | 0.0016963 | 0.00042513 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_261-505_0_6_load_87 | 132 | 0.0031311 | 0.00078473 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_261-505_0_6_load_86 | 133 | 0.0031019 | 0.0007774 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_261-505_0_6_load_111 | 134 | 0.0034299 | 0.00085962 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_261-505_0_6_load_112 | 135 | 0.0044753 | 0.0011216 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_261-505_0_6_load_121 | 136 | 0.0049277 | 0.001235 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_261-505_0_6_load_122 | 137 | 0.0049934 | 0.0012515 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_261-505_0_6_load_127 | 138 | 0.0035501 | 0.00088973 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_261-505_0_6_load_146 | 139 | 0.0043877 | 0.0010997 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_261-505_0_6_load_143 | 140 | 0.0040303 | 0.0010101 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_261-505_0_6_load_144 | 141 | 0.0044496 | 0.0011152 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_261-505_0_6_load_148 | 142 | 0.0044503 | 0.0011154 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_261-505_0_6_load_150 | 143 | 0.0074708 | 0.0018724 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_261-505_0_6_load_151 | 144 | 0.0066753 | 0.001673 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 133 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-505_0_6_line_0 |  | 0 | 1 | 0.01052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-505_0_6_line_1 |  | 0 | 2 | 0.014341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-505_0_6_line_2 |  | 1 | 3 | 0.044325 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-505_0_6_line_3 |  | 3 | 4 | 0.051331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-505_0_6_line_4 |  | 3 | 5 | 0.043574 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_261-505_0_6_line_5 |  | 4 | 6 | 0.0059524 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
6 | LV_261-505_0_6_line_6 |  | 4 | 7 | 0.017457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
7 | LV_261-505_0_6_line_7 |  | 6 | 51 | 0.012761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
8 | LV_261-505_0_6_line_8 |  | 6 | 53 | 0.026824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_261-505_0_6_line_9 |  | 7 | 95 | 0.014827 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
10 | LV_261-505_0_6_line_10 |  | 8 | 9 | 0.012061 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_261-505_0_6_line_11 |  | 8 | 10 | 0.029202 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
12 | LV_261-505_0_6_line_12 |  | 8 | 11 | 0.09506 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
13 | LV_261-505_0_6_line_13 |  | 10 | 51 | 0.032649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
14 | LV_261-505_0_6_line_14 |  | 10 | 52 | 0.01064 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
15 | LV_261-505_0_6_line_15 |  | 11 | 31 | 0.0093606 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
16 | LV_261-505_0_6_line_16 |  | 12 | 13 | 0.006862 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
17 | LV_261-505_0_6_line_17 |  | 12 | 14 | 0.02131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
18 | LV_261-505_0_6_line_18 |  | 13 | 15 | 0.015336 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
19 | LV_261-505_0_6_line_19 |  | 14 | 66 | 0.028092 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
20 | LV_261-505_0_6_line_20 |  | 15 | 89 | 0.016061 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
21 | LV_261-505_0_6_line_21 |  | 16 | 17 | 0.031355 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_261-505_0_6_line_22 |  | 16 | 18 | 0.042854 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_261-505_0_6_line_23 |  | 17 | 50 | 0.036032 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_261-505_0_6_line_24 |  | 18 | 58 | 0.017753 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_261-505_0_6_line_25 |  | 19 | 20 | 0.009126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_261-505_0_6_line_26 |  | 19 | 21 | 0.02216 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_261-505_0_6_line_27 |  | 19 | 22 | 0.015831 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_261-505_0_6_line_28 |  | 20 | 23 | 0.011608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_261-505_0_6_line_29 |  | 22 | 64 | 0.02429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_261-505_0_6_line_30 |  | 24 | 25 | 0.010745 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_261-505_0_6_line_31 |  | 24 | 26 | 0.014685 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_261-505_0_6_line_32 |  | 25 | 67 | 0.017813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_261-505_0_6_line_33 |  | 25 | 68 | 0.010115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_261-505_0_6_line_34 |  | 26 | 69 | 0.017403 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
35 | LV_261-505_0_6_line_35 |  | 27 | 28 | 0.01419 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_261-505_0_6_line_36 |  | 27 | 29 | 0.030236 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_261-505_0_6_line_37 |  | 27 | 30 | 0.010874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_261-505_0_6_line_38 |  | 28 | 43 | 0.017148 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_261-505_0_6_line_39 |  | 29 | 70 | 0.012553 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_261-505_0_6_line_40 |  | 31 | 72 | 0.017185 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
41 | LV_261-505_0_6_line_41 |  | 32 | 33 | 0.039755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_261-505_0_6_line_42 |  | 32 | 34 | 0.01426 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_261-505_0_6_line_43 |  | 33 | 55 | 0.002392 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_261-505_0_6_line_44 |  | 33 | 56 | 0.003723 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_261-505_0_6_line_45 |  | 33 | 57 | 0.013006 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_261-505_0_6_line_46 |  | 35 | 36 | 0.007168 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
47 | LV_261-505_0_6_line_47 |  | 35 | 37 | 0.018661 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
48 | LV_261-505_0_6_line_48 |  | 36 | 78 | 0.012091 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
49 | LV_261-505_0_6_line_49 |  | 36 | 79 | 0.036983 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
50 | LV_261-505_0_6_line_50 |  | 37 | 82 | 0.010022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
51 | LV_261-505_0_6_line_51 |  | 38 | 39 | 0.023726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_261-505_0_6_line_52 |  | 38 | 40 | 0.024879 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_261-505_0_6_line_53 |  | 40 | 88 | 0.025421 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_261-505_0_6_line_54 |  | 41 | 42 | 0.001794 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_261-505_0_6_line_55 |  | 41 | 43 | 0.013238 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_261-505_0_6_line_56 |  | 42 | 86 | 0.010664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_261-505_0_6_line_57 |  | 44 | 45 | 0.032849 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_261-505_0_6_line_58 |  | 44 | 46 | 0.034746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_261-505_0_6_line_59 |  | 45 | 47 | 0.027372 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_261-505_0_6_line_60 |  | 46 | 76 | 0.019382 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_261-505_0_6_line_61 |  | 47 | 67 | 0.015136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_261-505_0_6_line_62 |  | 48 | 49 | 0.019563 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_261-505_0_6_line_63 |  | 48 | 50 | 0.006876 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_261-505_0_6_line_64 |  | 49 | 90 | 0.025579 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
65 | LV_261-505_0_6_line_65 |  | 50 | 91 | 0.017418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_261-505_0_6_line_66 |  | 51 | 54 | 0.012407 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_261-505_0_6_line_67 |  | 52 | 94 | 0.016915 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
68 | LV_261-505_0_6_line_68 |  | 53 | 96 | 0.010315 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_261-505_0_6_line_69 |  | 54 | 97 | 0.0021188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_261-505_0_6_line_70 |  | 55 | 98 | 0.013687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_261-505_0_6_line_71 |  | 56 | 93 | 0.018219 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_261-505_0_6_line_72 |  | 56 | 99 | 0.040167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_261-505_0_6_line_73 |  | 56 | 100 | 0.002118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_261-505_0_6_line_74 |  | 57 | 101 | 0.017968 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_261-505_0_6_line_75 |  | 58 | 59 | 0.0092996 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_261-505_0_6_line_76 |  | 59 | 60 | 0.029166 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_261-505_0_6_line_77 |  | 60 | 61 | 0.012202 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_261-505_0_6_line_78 |  | 60 | 62 | 0.038442 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_261-505_0_6_line_79 |  | 61 | 63 | 0.028349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_261-505_0_6_line_80 |  | 62 | 64 | 0.00083391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_261-505_0_6_line_81 |  | 63 | 65 | 0.0069029 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_261-505_0_6_line_82 |  | 65 | 71 | 0.038107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_261-505_0_6_line_83 |  | 66 | 82 | 0.0065628 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
84 | LV_261-505_0_6_line_84 |  | 69 | 135 | 0.027541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
85 | LV_261-505_0_6_line_85 |  | 70 | 74 | 0.029776 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_261-505_0_6_line_86 |  | 70 | 77 | 0.014008 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_261-505_0_6_line_87 |  | 72 | 84 | 0.015118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
88 | LV_261-505_0_6_line_88 |  | 73 | 74 | 0.0029658 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_261-505_0_6_line_89 |  | 73 | 75 | 0.047092 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_261-505_0_6_line_90 |  | 75 | 76 | 0.011463 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_261-505_0_6_line_91 |  | 78 | 109 | 0.018071 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
92 | LV_261-505_0_6_line_92 |  | 79 | 110 | 0.019826 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
93 | LV_261-505_0_6_line_93 |  | 80 | 81 | 0.026216 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_261-505_0_6_line_94 |  | 81 | 111 | 0.014191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_261-505_0_6_line_95 |  | 83 | 84 | 0.014662 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
96 | LV_261-505_0_6_line_96 |  | 83 | 85 | 0.013255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
97 | LV_261-505_0_6_line_97 |  | 85 | 134 | 0.015099 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
98 | LV_261-505_0_6_line_98 |  | 86 | 87 | 0.013905 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_261-505_0_6_line_99 |  | 88 | 142 | 0.015215 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
100 | LV_261-505_0_6_line_100 |  | 88 | 141 | 0.023857 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
101 | LV_261-505_0_6_line_101 |  | 89 | 113 | 0.014011 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
102 | LV_261-505_0_6_line_102 |  | 90 | 106 | 0.0076672 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
103 | LV_261-505_0_6_line_103 |  | 92 | 93 | 0.01764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_261-505_0_6_line_104 |  | 94 | 109 | 0.030955 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
105 | LV_261-505_0_6_line_105 |  | 95 | 144 | 0.014993 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
106 | LV_261-505_0_6_line_106 |  | 96 | 129 | 0.014827 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_261-505_0_6_line_107 |  | 98 | 121 | 0.014246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_261-505_0_6_line_108 |  | 99 | 122 | 0.014356 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_261-505_0_6_line_109 |  | 100 | 117 | 0.018193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_261-505_0_6_line_110 |  | 102 | 103 | 0.014528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
111 | LV_261-505_0_6_line_111 |  | 102 | 104 | 0.0076394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
112 | LV_261-505_0_6_line_112 |  | 103 | 105 | 0.012145 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
113 | LV_261-505_0_6_line_113 |  | 104 | 106 | 0.014686 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
114 | LV_261-505_0_6_line_114 |  | 105 | 107 | 0.015021 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
115 | LV_261-505_0_6_line_115 |  | 107 | 108 | 0.023179 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
116 | LV_261-505_0_6_line_116 |  | 108 | 112 | 0.026568 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
117 | LV_261-505_0_6_line_117 |  | 110 | 133 | 0.026541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
118 | LV_261-505_0_6_line_118 |  | 111 | 136 | 0.026352 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_261-505_0_6_line_119 |  | 112 | 113 | 0.015487 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
120 | LV_261-505_0_6_line_120 |  | 114 | 115 | 0.00057635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_261-505_0_6_line_121 |  | 115 | 116 | 0.019191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_261-505_0_6_line_122 |  | 116 | 118 | 0.024283 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_261-505_0_6_line_123 |  | 117 | 119 | 0.018327 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_261-505_0_6_line_124 |  | 118 | 120 | 0.0076347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_261-505_0_6_line_125 |  | 119 | 123 | 0.0066104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_261-505_0_6_line_126 |  | 120 | 131 | 0.0074365 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_261-505_0_6_line_127 |  | 121 | 140 | 0.014473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_261-505_0_6_line_128 |  | 122 | 137 | 0.026731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_261-505_0_6_line_129 |  | 123 | 138 | 0.02665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_261-505_0_6_line_130 |  | 124 | 125 | 0.0099843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_261-505_0_6_line_131 |  | 125 | 126 | 0.011393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_261-505_0_6_line_132 |  | 125 | 127 | 0.015688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_261-505_0_6_line_133 |  | 126 | 128 | 0.0087448 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_261-505_0_6_line_134 |  | 128 | 129 | 0.006132 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_261-505_0_6_line_135 |  | 128 | 130 | 0.010152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_261-505_0_6_line_136 |  | 131 | 132 | 0.0076661 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_261-505_0_6_line_137 |  | 132 | 133 | 0.0076464 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_261-505_0_6_line_138 |  | 134 | 135 | 0.015198 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
139 | LV_261-505_0_6_line_139 |  | 136 | 137 | 0.015211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_261-505_0_6_line_140 |  | 138 | 139 | 0.02192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_261-505_0_6_line_141 |  | 140 | 141 | 0.025849 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
142 | LV_261-505_0_6_line_142 |  | 142 | 143 | 0.016095 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
143 | LV_261-505_0_6_line_143 |  | 143 | 144 | 0.024548 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-505_0_6_trafo_86 | 0.63 MVA 20/0.4 kV | 145 | 133 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2682781.9065 | 1250351.9323 | 2682784.1643 | 1250349.6545 | 2682791.1934 | 1250351.6731
1 | 2682781.9065 | 1250351.9323 | 2682777.6092 | 1250356.2678 | 2682769.4459 | 1250357.3636
2 | 2682811.9371 | 1250321.2546 | 2682810.7503 | 1250321.9052 | 2682808.9358 | 1250324.782 | 2682801.8809 | 1250352.0259 | 2682798.572 | 1250353.7921 | 2682791.1934 | 1250351.6731
3 | 2682861.0172 | 1250334.3391 | 2682840.8586 | 1250327.8859 | 2682821.3289 | 1250321.2747 | 2682813.611 | 1250320.3329 | 2682811.9371 | 1250321.2546
4 | 2682811.9371 | 1250321.2546 | 2682797.3027 | 1250310.1086 | 2682781.8489 | 1250306.8014 | 2682777.9098 | 1250315.3082
5 | 2682861.0172 | 1250334.3391 | 2682864.7978 | 1250335.5484 | 2682863.755 | 1250337.2351
6 | 2682861.0172 | 1250334.3391 | 2682857.6754 | 1250340.0744 | 2682854.4441 | 1250345.4666 | 2682851.5989 | 1250348.9959
7 | 2682863.755 | 1250337.2351 | 2682864.7978 | 1250335.5484 | 2682867.5882 | 1250329.2938 | 2682871.3709 | 1250330.3586
8 | 2682863.755 | 1250337.2351 | 2682880.7248 | 1250350.3487 | 2682885.1593 | 1250353.3908 | 2682885.1593 | 1250353.3908
9 | 2682842.2933 | 1250360.5388 | 2682851.5989 | 1250348.9959
10 | 2682851.7285 | 1250305.3544 | 2682855.4375 | 1250293.8754
11 | 2682855.4375 | 1250293.8754 | 2682865.8839 | 1250295.6895 | 2682868.9778 | 1250297.4229 | 2682876.8324 | 1250299.3897 | 2682883.5811 | 1250301.0742
12 | 2682831.9048 | 1250265.7701 | 2682829.6795 | 1250261.8583 | 2682821.7888 | 1250259.2239 | 2682810.2521 | 1250292.7321 | 2682823.6398 | 1250293.1528 | 2682826.264 | 1250290.1428 | 2682831.3835 | 1250290.6369 | 2682855.4375 | 1250293.8754
13 | 2682883.5811 | 1250301.0742 | 2682881.8676 | 1250302.1288 | 2682880.4918 | 1250303.3327 | 2682878.9141 | 1250304.9341 | 2682877.8668 | 1250306.9431 | 2682876.2058 | 1250313.9585 | 2682874.3554 | 1250320.4819 | 2682871.3709 | 1250330.3586
14 | 2682883.5811 | 1250301.0742 | 2682886.6402 | 1250300.4388 | 2682890.571 | 1250300.6272 | 2682894.0432 | 1250301.5014
15 | 2682831.9048 | 1250265.7701 | 2682840.9093 | 1250268.3278
16 | 2683057.7475 | 1250344.8891 | 2683059.9353 | 1250347.6996 | 2683059.972 | 1250351.0026
17 | 2683057.7475 | 1250344.8891 | 2683055.8506 | 1250342.8721 | 2683050.5837 | 1250340.5077 | 2683038.1999 | 1250337.398
18 | 2683059.972 | 1250351.0026 | 2683059.4543 | 1250353.4638 | 2683052.4366 | 1250364.1941
19 | 2683038.1999 | 1250337.398 | 2683023.7101 | 1250333.7595 | 2683010.9348 | 1250330.6305
20 | 2683043.6455 | 1250377.636 | 2683052.4366 | 1250364.1941
21 | 2682912.8757 | 1250577.156 | 2682912.6753 | 1250577.4534 | 2682918.3224 | 1250581.2241 | 2682923.7826 | 1250584.8698 | 2682925.9026 | 1250583.3539 | 2682929.1419 | 1250582.2317 | 2682933.6429 | 1250576.7351 | 2682936.4926 | 1250573.2501
22 | 2682936.4926 | 1250573.2501 | 2682935.9713 | 1250572.1976 | 2682935.6259 | 1250569.9133 | 2682936.4688 | 1250567.401 | 2682941.0208 | 1250560.4261 | 2682942.1785 | 1250557.5402 | 2682956.2036 | 1250536.5067
23 | 2682932.4223 | 1250546.9069 | 2682931.9673 | 1250548.1348 | 2682931.0128 | 1250549.9783 | 2682912.8757 | 1250577.156
24 | 2682966.0523 | 1250521.7366 | 2682956.2036 | 1250536.5067
25 | 2683059.0347 | 1250524.9856 | 2683054.0055 | 1250532.6097
26 | 2683054.0055 | 1250532.6097 | 2683052.2622 | 1250535.2539 | 2683041.6105 | 1250550.979
27 | 2683054.0055 | 1250532.6097 | 2683046.6906 | 1250527.7146 | 2683044.4465 | 1250527.3051 | 2683040.481 | 1250524.6938
28 | 2683059.0347 | 1250524.9856 | 2683065.464 | 1250515.3201
29 | 2683020.1945 | 1250511.3348 | 2683040.481 | 1250524.6938
30 | 2682993.2485 | 1250290.5008 | 2682991.3521 | 1250293.2874 | 2682987.0327 | 1250299.2758
31 | 2682987.0327 | 1250299.2758 | 2682984.2914 | 1250300.405 | 2682982.3697 | 1250300.6894 | 2682980.447 | 1250300.5068 | 2682972.7732 | 1250298.8726
32 | 2682993.2485 | 1250290.5008 | 2683003.279 | 1250275.78
33 | 2682993.2485 | 1250290.5008 | 2682990.5556 | 1250288.7062 | 2682984.7369 | 1250285.0377
34 | 2682955.7516 | 1250295.2477 | 2682972.7732 | 1250298.8726
35 | 2682921.5942 | 1250199.1968 | 2682910.0481 | 1250207.4454
36 | 2682921.5942 | 1250199.1968 | 2682930.929 | 1250221.0992 | 2682935.053 | 1250226.0295
37 | 2682921.5942 | 1250199.1968 | 2682930.4806 | 1250192.9295
38 | 2682910.0481 | 1250207.4454 | 2682896.095 | 1250217.4136
39 | 2682943.1072 | 1250235.6582 | 2682935.053 | 1250226.0295
40 | 2682840.9093 | 1250268.3278 | 2682845.1628 | 1250269.536 | 2682857.5401 | 1250272.6523
41 | 2682852.5211 | 1250528.8205 | 2682846.7348 | 1250524.7366 | 2682864.0616 | 1250498.8039 | 2682864.8867 | 1250497.5701
42 | 2682852.5211 | 1250528.8205 | 2682863.77 | 1250537.5847
43 | 2682864.8867 | 1250497.5701 | 2682863.0971 | 1250495.9772
44 | 2682866.9609 | 1250494.4746 | 2682865.3261 | 1250496.9202 | 2682864.8867 | 1250497.5701
45 | 2682864.8867 | 1250497.5701 | 2682872.1726 | 1250503.4764 | 2682875.1489 | 1250505.5494
46 | 2682969.7174 | 1250320.5382 | 2682976.6997 | 1250322.2483
47 | 2682976.6997 | 1250322.2483 | 2682984.2238 | 1250324.0883 | 2682994.8258 | 1250326.685
48 | 2682969.7174 | 1250320.5382 | 2682966.9335 | 1250319.8542 | 2682957.9885 | 1250317.602
49 | 2682969.7174 | 1250320.5382 | 2682972.3893 | 1250329.2153 | 2682959.3314 | 1250353.875
50 | 2682994.8258 | 1250326.685 | 2683004.5605 | 1250329.0693
51 | 2682775.022 | 1250440.9169 | 2682770.9954 | 1250432.9992 | 2682762.3153 | 1250420.9579
52 | 2682775.022 | 1250440.9169 | 2682796.9421 | 1250436.364 | 2682796.8285 | 1250433.8755
53 | 2682811.751 | 1250422.0492 | 2682796.3757 | 1250423.958 | 2682796.8285 | 1250433.8755
54 | 2682885.3236 | 1250225.1088 | 2682884.884 | 1250226.8484
55 | 2682885.3236 | 1250225.1088 | 2682896.095 | 1250217.4136
56 | 2682884.884 | 1250226.8484 | 2682876.0841 | 1250232.8717
57 | 2682999.9132 | 1250220.5866 | 2683023.4801 | 1250236.5173 | 2683024.7043 | 1250237.513 | 2683025.4925 | 1250238.9139 | 2683025.8149 | 1250240.1527
58 | 2682999.9132 | 1250220.5866 | 2682976.5515 | 1250246.3066
59 | 2683025.8149 | 1250240.1527 | 2683025.8821 | 1250241.8216 | 2683025.0769 | 1250243.7895 | 2683011.8019 | 1250263.2718
60 | 2682976.5515 | 1250246.3066 | 2682963.5202 | 1250260.6535
61 | 2683003.279 | 1250275.78 | 2683011.8019 | 1250263.2718
62 | 2682936.4489 | 1250541.3257 | 2682939.3052 | 1250537.3739 | 2682947.4783 | 1250525.1706
63 | 2682936.4489 | 1250541.3257 | 2682932.4223 | 1250546.9069
64 | 2682947.4783 | 1250525.1706 | 2682961.7123 | 1250503.918
65 | 2682932.4223 | 1250546.9069 | 2682931.5818 | 1250544.927 | 2682929.9967 | 1250543.2925 | 2682919.2625 | 1250535.9771
66 | 2682871.3709 | 1250330.3586 | 2682883.3117 | 1250333.7263
67 | 2682910.4463 | 1250305.6315 | 2682894.0432 | 1250301.5014
68 | 2682885.1593 | 1250353.3908 | 2682883.7041 | 1250355.4164 | 2682878.7325 | 1250361.4537
69 | 2682885.3509 | 1250334.3015 | 2682883.3117 | 1250333.7263
70 | 2682863.0971 | 1250495.9772 | 2682856.3861 | 1250489.9901 | 2682853.0606 | 1250486.6783
71 | 2682866.9609 | 1250494.4746 | 2682881.442 | 1250505.5295
72 | 2682866.9609 | 1250494.4746 | 2682892.417 | 1250463.4045
73 | 2682866.9609 | 1250494.4746 | 2682865.4185 | 1250493.0186
74 | 2682889.8933 | 1250515.8193 | 2682875.1489 | 1250505.5494
75 | 2682966.0523 | 1250521.7366 | 2682971.2115 | 1250513.9994
76 | 2682987.3918 | 1250489.7337 | 2682971.2115 | 1250513.9994
77 | 2682987.3918 | 1250489.7337 | 2682994.1609 | 1250479.5812
78 | 2682987.3918 | 1250489.7337 | 2683019.4981 | 1250510.8762
79 | 2683009.8942 | 1250455.9987 | 2682996.8156 | 1250475.5995 | 2682994.1609 | 1250479.5812
80 | 2683019.4981 | 1250510.8762 | 2683020.1945 | 1250511.3348
81 | 2683013.7256 | 1250450.2567 | 2683009.8942 | 1250455.9987
82 | 2683013.7256 | 1250450.2567 | 2683034.8766 | 1250418.5579
83 | 2683004.5605 | 1250329.0693 | 2683010.9348 | 1250330.6305
84 | 2682928.7297 | 1250290.2341 | 2682945.6211 | 1250293.9034 | 2682950.3221 | 1250294.0915 | 2682955.7516 | 1250295.2477
85 | 2682943.1072 | 1250235.6582 | 2682920.8248 | 1250255.4087
86 | 2682943.1072 | 1250235.6582 | 2682953.5895 | 1250226.3663
87 | 2682857.5401 | 1250272.6523 | 2682867.7482 | 1250275.2226 | 2682872.1995 | 1250276.3482
88 | 2682918.6054 | 1250257.376 | 2682920.8248 | 1250255.4087
89 | 2682955.813 | 1250269.1387 | 2682937.2243 | 1250253.5559 | 2682930.9258 | 1250261.229 | 2682918.6054 | 1250257.376
90 | 2682955.813 | 1250269.1387 | 2682963.5202 | 1250260.6535
91 | 2682940.4644 | 1250313.1897 | 2682957.9885 | 1250317.602
92 | 2682950.0533 | 1250371.3966 | 2682959.3314 | 1250353.875
93 | 2682958.1218 | 1250359.5659 | 2682945.8585 | 1250382.7364
94 | 2682945.8585 | 1250382.7364 | 2682944.081 | 1250386.0948 | 2682938.5461 | 1250394.8892
95 | 2682886.4136 | 1250279.9426 | 2682872.1995 | 1250276.3482
96 | 2682886.4136 | 1250279.9426 | 2682893.3501 | 1250281.6964 | 2682899.2741 | 1250283.151
97 | 2682899.2741 | 1250283.151 | 2682913.9371 | 1250286.7512
98 | 2682876.0841 | 1250232.8717 | 2682864.6098 | 1250240.7256
99 | 2682811.751 | 1250422.0492 | 2682811.4838 | 1250417.9424 | 2682811.7739 | 1250412.8538 | 2682812.5929 | 1250407.1943 | 2682812.6681 | 1250406.9201
100 | 2682811.751 | 1250422.0492 | 2682812.7294 | 1250428.2119 | 2682813.7673 | 1250433.8972 | 2682815.3102 | 1250438.5556 | 2682817.8946 | 1250444.3293 | 2682818.2086 | 1250444.8459
101 | 2683035.9769 | 1250389.3616 | 2683035.9769 | 1250389.3616 | 2683043.6455 | 1250377.636
102 | 2682965.9789 | 1250497.5476 | 2682961.7123 | 1250503.918
103 | 2682896.1041 | 1250515.3206 | 2682884.3059 | 1250507.7158 | 2682881.442 | 1250505.5295
104 | 2682910.4463 | 1250305.6315 | 2682940.4644 | 1250313.1897
105 | 2682832.882 | 1250372.2097 | 2682832.9928 | 1250372.0755 | 2682842.2933 | 1250360.5388
106 | 2682869.3075 | 1250372.8991 | 2682878.7325 | 1250361.4537
107 | 2682853.0606 | 1250486.6783 | 2682847.7116 | 1250481.3513 | 2682843.2397 | 1250476.366
108 | 2682901.0456 | 1250451.9451 | 2682896.8011 | 1250458.0536 | 2682892.417 | 1250463.4045
109 | 2682865.4185 | 1250493.0186 | 2682854.0769 | 1250482.3633 | 2682852.3197 | 1250480.4048
110 | 2682978.4027 | 1250478.9978 | 2682986.4871 | 1250466.9271
111 | 2682978.4027 | 1250478.9978 | 2682974.1516 | 1250485.3451
112 | 2682986.4871 | 1250466.9271 | 2682993.2454 | 1250456.8364
113 | 2682965.9789 | 1250497.5476 | 2682974.1516 | 1250485.3451
114 | 2683001.6041 | 1250444.3561 | 2682993.2454 | 1250456.8364
115 | 2683014.5024 | 1250425.0978 | 2683001.6041 | 1250444.3561
116 | 2683029.2867 | 1250403.0235 | 2683014.5024 | 1250425.0978
117 | 2682950.0533 | 1250371.3966 | 2682942.4706 | 1250385.7164 | 2682937.0295 | 1250394.5055
118 | 2682938.5461 | 1250394.8892 | 2682924.5095 | 1250417.1916
119 | 2683029.2867 | 1250403.0235 | 2683034.9758 | 1250394.5292 | 2683035.9769 | 1250389.3616
120 | 2682895.718 | 1250455.6982 | 2682895.3835 | 1250456.1675
121 | 2682906.8576 | 1250440.0713 | 2682895.718 | 1250455.6982
122 | 2682920.6949 | 1250420.1228 | 2682916.7865 | 1250426.1427 | 2682906.8576 | 1250440.0713
123 | 2682852.3197 | 1250480.4048 | 2682840.0801 | 1250466.7638
124 | 2682920.6949 | 1250420.1228 | 2682924.8523 | 1250413.7193
125 | 2682840.0801 | 1250466.7638 | 2682837.2542 | 1250463.6142 | 2682835.7631 | 1250461.7606
126 | 2682928.9017 | 1250407.4821 | 2682924.8523 | 1250413.7193
127 | 2682843.2397 | 1250476.366 | 2682840.7015 | 1250473.5364 | 2682833.8404 | 1250465.3632
128 | 2682916.2989 | 1250429.9933 | 2682901.0456 | 1250451.9451
129 | 2682835.7631 | 1250461.7606 | 2682822.8876 | 1250445.7557 | 2682820.3016 | 1250440.2212
130 | 2682852.6065 | 1250393.1764 | 2682861.0528 | 1250398.5006
131 | 2682852.6065 | 1250393.1764 | 2682859.8498 | 1250384.3826
132 | 2682852.6065 | 1250393.1764 | 2682849.935 | 1250391.4822 | 2682845.499 | 1250397.18 | 2682841.0377 | 1250394.3125
133 | 2682865.4095 | 1250377.6327 | 2682859.8498 | 1250384.3826
134 | 2682865.4095 | 1250377.6327 | 2682869.3075 | 1250372.8991
135 | 2682874.5657 | 1250382.0751 | 2682865.4095 | 1250377.6327
136 | 2682933.0046 | 1250401.0069 | 2682930.9302 | 1250404.3577 | 2682928.9017 | 1250407.4821
137 | 2682937.0295 | 1250394.5055 | 2682933.0046 | 1250401.0069
138 | 2682913.9371 | 1250286.7512 | 2682923.4615 | 1250289.0897 | 2682928.7297 | 1250290.2341
139 | 2682916.2989 | 1250429.9933 | 2682917.9281 | 1250427.6487 | 2682924.5095 | 1250417.1916
140 | 2682820.3016 | 1250440.2212 | 2682818.5627 | 1250436.4995 | 2682816.5016 | 1250428.9429 | 2682815.5476 | 1250421.5796 | 2682815.4916 | 1250419.0256
141 | 2682833.8404 | 1250465.3632 | 2682827.1194 | 1250457.3568 | 2682822.4349 | 1250451.676 | 2682820.1307 | 1250448.0078 | 2682818.2086 | 1250444.8459
142 | 2682812.6681 | 1250406.9201 | 2682813.993 | 1250402.0879 | 2682815.8603 | 1250397.0547 | 2682818.1981 | 1250391.839 | 2682818.1981 | 1250391.839
143 | 2682818.1981 | 1250391.839 | 2682820.4158 | 1250388.2006 | 2682825.1823 | 1250381.54 | 2682832.882 | 1250372.2097

## bus_geodata
| x | y | coords
0 | 2682781.9065 | 1250351.9323
1 | 2682791.1934 | 1250351.6731
2 | 2682769.4459 | 1250357.3636
3 | 2682811.9371 | 1250321.2546
4 | 2682861.0172 | 1250334.3391
5 | 2682777.9098 | 1250315.3082
6 | 2682863.755 | 1250337.2351
7 | 2682851.5989 | 1250348.9959
8 | 2682855.4376 | 1250293.8754
9 | 2682851.7285 | 1250305.3544
10 | 2682883.5811 | 1250301.0742
11 | 2682831.9048 | 1250265.7701
12 | 2683057.7475 | 1250344.8891
13 | 2683059.972 | 1250351.0026
14 | 2683038.1999 | 1250337.398
15 | 2683052.4366 | 1250364.1941
16 | 2682936.4926 | 1250573.2501
17 | 2682912.8757 | 1250577.156
18 | 2682956.2036 | 1250536.5067
19 | 2683054.0055 | 1250532.6097
20 | 2683059.0347 | 1250524.9856
21 | 2683041.6105 | 1250550.979
22 | 2683040.481 | 1250524.6938
23 | 2683065.464 | 1250515.3201
24 | 2682987.0327 | 1250299.2758
25 | 2682993.2485 | 1250290.5008
26 | 2682972.7732 | 1250298.8726
27 | 2682921.5942 | 1250199.1968
28 | 2682910.0481 | 1250207.4454
29 | 2682935.053 | 1250226.0295
30 | 2682930.4806 | 1250192.9295
31 | 2682840.9093 | 1250268.3278
32 | 2682852.5211 | 1250528.8205
33 | 2682864.8867 | 1250497.5701
34 | 2682863.77 | 1250537.5847
35 | 2682976.6997 | 1250322.2483
36 | 2682969.7174 | 1250320.5382
37 | 2682994.8258 | 1250326.685
38 | 2682775.022 | 1250440.9169
39 | 2682762.3153 | 1250420.9579
40 | 2682796.8285 | 1250433.8755
41 | 2682885.3236 | 1250225.1088
42 | 2682884.884 | 1250226.8484
43 | 2682896.095 | 1250217.4136
44 | 2682999.9132 | 1250220.5866
45 | 2683025.8149 | 1250240.1527
46 | 2682976.5515 | 1250246.3066
47 | 2683011.8019 | 1250263.2718
48 | 2682936.4489 | 1250541.3257
49 | 2682947.4783 | 1250525.1706
50 | 2682932.4223 | 1250546.9069
51 | 2682871.3709 | 1250330.3586
52 | 2682894.0432 | 1250301.5014
53 | 2682885.1593 | 1250353.3908
54 | 2682883.3117 | 1250333.7263
55 | 2682863.0971 | 1250495.9772
56 | 2682866.9609 | 1250494.4746
57 | 2682875.1489 | 1250505.5494
58 | 2682966.0523 | 1250521.7366
59 | 2682971.2115 | 1250513.9994
60 | 2682987.3918 | 1250489.7337
61 | 2682994.1609 | 1250479.5812
62 | 2683019.4981 | 1250510.8762
63 | 2683009.8942 | 1250455.9987
64 | 2683020.1945 | 1250511.3348
65 | 2683013.7256 | 1250450.2567
66 | 2683010.9348 | 1250330.6305
67 | 2683003.279 | 1250275.78
68 | 2682984.7369 | 1250285.0377
69 | 2682955.7516 | 1250295.2477
70 | 2682943.1072 | 1250235.6582
71 | 2683034.8766 | 1250418.5579
72 | 2682857.5401 | 1250272.6523
73 | 2682918.6054 | 1250257.376
74 | 2682920.8248 | 1250255.4087
75 | 2682955.813 | 1250269.1387
76 | 2682963.5202 | 1250260.6535
77 | 2682953.5895 | 1250226.3663
78 | 2682957.9885 | 1250317.602
79 | 2682959.3314 | 1250353.875
80 | 2682958.1218 | 1250359.5659
81 | 2682945.8585 | 1250382.7364
82 | 2683004.5605 | 1250329.0693
83 | 2682886.4136 | 1250279.9426
84 | 2682872.1995 | 1250276.3482
85 | 2682899.2741 | 1250283.151
86 | 2682876.0841 | 1250232.8717
87 | 2682864.6098 | 1250240.7256
88 | 2682811.751 | 1250422.0492
89 | 2683043.6455 | 1250377.636
90 | 2682961.7123 | 1250503.918
91 | 2682919.2625 | 1250535.9771
92 | 2682896.1041 | 1250515.3206
93 | 2682881.442 | 1250505.5295
94 | 2682910.4463 | 1250305.6315
95 | 2682842.2933 | 1250360.5388
96 | 2682878.7325 | 1250361.4537
97 | 2682885.3509 | 1250334.3015
98 | 2682853.0606 | 1250486.6783
99 | 2682892.417 | 1250463.4045
100 | 2682865.4185 | 1250493.0186
101 | 2682889.8933 | 1250515.8193
102 | 2682978.4027 | 1250478.9978
103 | 2682986.4871 | 1250466.9271
104 | 2682974.1516 | 1250485.3451
105 | 2682993.2454 | 1250456.8364
106 | 2682965.9789 | 1250497.5476
107 | 2683001.6041 | 1250444.3561
108 | 2683014.5024 | 1250425.0978
109 | 2682940.4644 | 1250313.1897
110 | 2682950.0533 | 1250371.3966
111 | 2682938.5461 | 1250394.8892
112 | 2683029.2867 | 1250403.0235
113 | 2683035.9769 | 1250389.3616
114 | 2682895.3835 | 1250456.1675
115 | 2682895.718 | 1250455.6982
116 | 2682906.8576 | 1250440.0713
117 | 2682852.3197 | 1250480.4048
118 | 2682920.6949 | 1250420.1228
119 | 2682840.0801 | 1250466.7638
120 | 2682924.8523 | 1250413.7193
121 | 2682843.2397 | 1250476.366
122 | 2682901.0456 | 1250451.9451
123 | 2682835.7631 | 1250461.7606
124 | 2682861.0528 | 1250398.5006
125 | 2682852.6065 | 1250393.1764
126 | 2682859.8498 | 1250384.3826
127 | 2682841.0377 | 1250394.3125
128 | 2682865.4095 | 1250377.6327
129 | 2682869.3075 | 1250372.8991
130 | 2682874.5657 | 1250382.0751
131 | 2682928.9017 | 1250407.4821
132 | 2682933.0046 | 1250401.0069
133 | 2682937.0295 | 1250394.5055
134 | 2682913.9371 | 1250286.7512
135 | 2682928.7297 | 1250290.2341
136 | 2682924.5095 | 1250417.1916
137 | 2682916.2989 | 1250429.9933
138 | 2682820.3016 | 1250440.2212
139 | 2682815.4916 | 1250419.0256
140 | 2682833.8404 | 1250465.3632
141 | 2682818.2086 | 1250444.8459
142 | 2682812.6681 | 1250406.9201
143 | 2682818.1981 | 1250391.839
144 | 2682832.882 | 1250372.2097
145 | 2682969.7174 | 1250320.5382

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98295 | -0.32649 | 0.001939 | 0.00048595
1 | 0.983 | -0.32552 | 0.0013335 | 0.0003342
2 | 0.98291 | -0.32732 | 0.0031941 | 0.00080052
3 | 0.98326 | -0.32035 | 0 | 0
4 | 0.98371 | -0.31155 | 0 | 0
5 | 0.98314 | -0.32274 | 0.0030387 | 0.00076158
6 | 0.98388 | -0.30839 | 0 | 0
7 | 0.98327 | -0.32025 | 0.0067946 | 0.0017029
8 | 0.98513 | -0.28413 | 0 | 0
9 | 0.98488 | -0.28899 | 0.022446 | 0.0056256
10 | 0.98572 | -0.27261 | 0 | 0
11 | 0.98359 | -0.31403 | 0 | 0
12 | 0.98879 | -0.21339 | 0 | 0
13 | 0.98861 | -0.21697 | 0 | 0
14 | 0.98937 | -0.20227 | 0.0053065 | 0.0013299
15 | 0.98819 | -0.22498 | 0.0075799 | 0.0018997
16 | 0.9778 | -0.42614 | 0 | 0
17 | 0.97977 | -0.38779 | 0 | 0
18 | 0.97511 | -0.4788 | 0.005263 | 0.001319
19 | 0.97079 | -0.56396 | 0 | 0
20 | 0.97077 | -0.56438 | 0 | 0
21 | 0.97063 | -0.56718 | 0.0078601 | 0.0019699
22 | 0.97095 | -0.56092 | 0.003943 | 0.00098822
23 | 0.97075 | -0.56492 | 0.0025152 | 0.00063036
24 | 0.98052 | -0.37353 | 0 | 0
25 | 0.98001 | -0.38357 | 0 | 0
26 | 0.98123 | -0.35983 | 0.0047074 | 0.0011798
27 | 0.97079 | -0.56453 | 0 | 0
28 | 0.97057 | -0.56881 | 0.0044358 | 0.0011117
29 | 0.97132 | -0.55399 | 0.0041542 | 0.0010411
30 | 0.97076 | -0.56505 | 0.0025648 | 0.00064279
31 | 0.98343 | -0.31697 | 0.0063047 | 0.0015801
32 | 0.97596 | -0.46294 | 0 | 0
33 | 0.97614 | -0.45928 | 0 | 0
34 | 0.97589 | -0.46426 | 0.0050367 | 0.0012623
35 | 0.99126 | -0.16598 | 0 | 0
36 | 0.99149 | -0.16155 | 0 | 0
37 | 0.99066 | -0.17752 | 0.0083194 | 0.002085
38 | 0.98118 | -0.36079 | 0 | 0
39 | 0.98114 | -0.36168 | 0.0020744 | 0.00051989
40 | 0.98123 | -0.35985 | 0.0044325 | 0.0011109
41 | 0.97029 | -0.57434 | 0 | 0
42 | 0.97028 | -0.57458 | 0 | 0
43 | 0.97038 | -0.57257 | 0.0046434 | 0.0011637
44 | 0.97619 | -0.45808 | 0 | 0
45 | 0.97747 | -0.43297 | 0 | 0
46 | 0.97483 | -0.48471 | 0.0056891 | 0.0014258
47 | 0.97854 | -0.4121 | 0.0035568 | 0.00089143
48 | 0.98253 | -0.33415 | 0 | 0
49 | 0.98397 | -0.30645 | 0.012691 | 0.0031806
50 | 0.98203 | -0.3439 | 0 | 0
51 | 0.98436 | -0.29907 | 0 | 0
52 | 0.98638 | -0.25981 | 0.0051318 | 0.0012861
53 | 0.98251 | -0.33505 | 0.010586 | 0.0026531
54 | 0.9841 | -0.30415 | 0.0075134 | 0.001883
55 | 0.97633 | -0.45562 | 0 | 0
56 | 0.9759 | -0.46407 | 0 | 0
57 | 0.97604 | -0.46126 | 0.0041876 | 0.0010495
58 | 0.97409 | -0.49899 | 0.00598 | 0.0014987
59 | 0.9736 | -0.50856 | 0.002294 | 0.00057494
60 | 0.97214 | -0.53739 | 0 | 0
61 | 0.9718 | -0.54414 | 0.0061676 | 0.0015457
62 | 0.97129 | -0.55422 | 0.0057009 | 0.0014288
63 | 0.97117 | -0.55661 | 0.0083482 | 0.0020923
64 | 0.97127 | -0.55449 | 0.0036857 | 0.00092373
65 | 0.97107 | -0.55858 | 0.0095725 | 0.0023991
66 | 0.99016 | -0.18711 | 0.005767 | 0.0014454
67 | 0.97918 | -0.3996 | 0.0041578 | 0.0010421
68 | 0.97999 | -0.38393 | 0.0019475 | 0.0004881
69 | 0.98168 | -0.35098 | 0.0044767 | 0.001122
70 | 0.97159 | -0.54866 | 0 | 0
71 | 0.97086 | -0.56273 | 0.0058891 | 0.0014759
72 | 0.98317 | -0.322 | 0.0035677 | 0.00089415
73 | 0.97244 | -0.53176 | 0 | 0
74 | 0.97236 | -0.5335 | 0.0041501 | 0.0010401
75 | 0.97384 | -0.50425 | 0 | 0
76 | 0.97418 | -0.49757 | 0.004407 | 0.0011045
77 | 0.97153 | -0.54984 | 0.004576 | 0.0011469
78 | 0.99067 | -0.17732 | 0.0083315 | 0.0020881
79 | 0.9952 | -0.090733 | 0.0106 | 0.0026565
80 | 0.97175 | -0.54593 | 0.0083292 | 0.0020875
81 | 0.97195 | -0.5419 | 0.0083961 | 0.0021043
82 | 0.99035 | -0.18343 | 0.0084899 | 0.0021278
83 | 0.98276 | -0.33009 | 0 | 0
84 | 0.98296 | -0.32623 | 0.0045482 | 0.0011399
85 | 0.98258 | -0.33358 | 0.0043863 | 0.0010993
86 | 0.97021 | -0.576 | 0.0036054 | 0.00090359
87 | 0.97016 | -0.57693 | 0.003607 | 0.00090401
88 | 0.98138 | -0.35686 | 0 | 0
89 | 0.98778 | -0.23294 | 0.0069823 | 0.0017499
90 | 0.98469 | -0.29246 | 0.0017769 | 0.00044535
91 | 0.98185 | -0.34746 | 0.011299 | 0.0028317
92 | 0.97566 | -0.46883 | 0.004874 | 0.0012215
93 | 0.97574 | -0.46725 | 0.0046655 | 0.0011693
94 | 0.98745 | -0.23918 | 0.010373 | 0.0025998
95 | 0.9829 | -0.32728 | 0.0063712 | 0.0015968
96 | 0.98209 | -0.34334 | 0.0067953 | 0.0017031
97 | 0.98407 | -0.30473 | 0.015251 | 0.0038222
98 | 0.9774 | -0.43469 | 0.0039574 | 0.00099182
99 | 0.97435 | -0.49449 | 0.0048772 | 0.0012223
100 | 0.97586 | -0.46483 | 0 | 0
101 | 0.97598 | -0.46262 | 0.0041359 | 0.0010366
102 | 0.98522 | -0.28225 | 0.0016895 | 0.00042343
103 | 0.98548 | -0.27713 | 0.001667 | 0.00041778
104 | 0.98508 | -0.2849 | 0.0016912 | 0.00042385
105 | 0.98571 | -0.27278 | 0.0067421 | 0.0016897
106 | 0.98482 | -0.2899 | 0.0017758 | 0.00044506
107 | 0.98601 | -0.26704 | 0.0069056 | 0.0017307
108 | 0.9865 | -0.25761 | 0.0038901 | 0.00097495
109 | 0.98946 | -0.20042 | 0.0083308 | 0.0020879
110 | 0.99723 | -0.052251 | 0.010599 | 0.0026565
111 | 0.97217 | -0.53752 | 0.0048756 | 0.0012219
112 | 0.98708 | -0.24645 | 0.0072206 | 0.0018097
113 | 0.98743 | -0.23954 | 0.0072189 | 0.0018092
114 | 0.9991 | -0.017375 | 0.0056398 | 0.0014135
115 | 0.9991 | -0.017318 | 0.0017039 | 0.00042704
116 | 0.99923 | -0.014857 | 0.0055508 | 0.0013912
117 | 0.97553 | -0.47132 | 0.0043875 | 0.0010996
118 | 0.99951 | -0.0093928 | 0.0018231 | 0.00045691
119 | 0.97528 | -0.47639 | 0.0044293 | 0.0011101
120 | 0.99961 | -0.0074324 | 0.0018239 | 0.00045711
121 | 0.97856 | -0.41193 | 0.0037746 | 0.00094601
122 | 0.97387 | -0.5041 | 0.0049133 | 0.0012314
123 | 0.97521 | -0.47768 | 0.0027358 | 0.00068565
124 | 0.98108 | -0.36305 | 0.0068055 | 0.0017056
125 | 0.98114 | -0.36182 | 0 | 0
126 | 0.98125 | -0.35965 | 0.0066738 | 0.0016726
127 | 0.98109 | -0.36286 | 0.0036712 | 0.00092009
128 | 0.98139 | -0.35694 | 0 | 0
129 | 0.98157 | -0.35346 | 0.0063703 | 0.0015966
130 | 0.98126 | -0.35955 | 0.014214 | 0.0035624
131 | 0.99972 | -0.0052868 | 0.0016963 | 0.00042513
132 | 0.99985 | -0.0028486 | 0.0031311 | 0.00078473
133 | 1 | 0 | -0.59616 | -0.15286
134 | 0.98238 | -0.33732 | 0.0034299 | 0.00085962
135 | 0.9822 | -0.3409 | 0.0044753 | 0.0011216
136 | 0.9727 | -0.52703 | 0.0049277 | 0.001235
137 | 0.97308 | -0.5196 | 0.0049934 | 0.0012515
138 | 0.97501 | -0.48156 | 0.0035501 | 0.00088973
139 | 0.97492 | -0.48333 | 0.0043877 | 0.0010997
140 | 0.97979 | -0.38787 | 0.0040303 | 0.0010101
141 | 0.98094 | -0.36549 | 0.0044496 | 0.0011152
142 | 0.98168 | -0.351 | 0.0044503 | 0.0011154
143 | 0.98202 | -0.34454 | 0.0074708 | 0.0018724
144 | 0.98256 | -0.33405 | 0.0066753 | 0.001673
145 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0051332 | -0.0012864 | 0.0051334 | 0.0012864 | 2.3822e-07 | 1.9102e-08 | 0.0077707 | 0.0077707 | 0.0077707 | 0.98295 | -0.32649 | 0.983 | -0.32552 | 2.1348
1 | 0.0031942 | 0.00080041 | -0.0031941 | -0.00080052 | 1.2574e-07 | -1.013e-07 | 0.0048354 | 0.0048355 | 0.0048355 | 0.98295 | -0.32649 | 0.98291 | -0.32732 | 1.3284
2 | -0.0064669 | -0.0016206 | 0.0064685 | 0.001621 | 1.5928e-06 | 4.5734e-07 | 0.0097892 | 0.009789 | 0.0097892 | 0.983 | -0.32552 | 0.98326 | -0.32035 | 2.6893
3 | -0.0095076 | -0.0023823 | 0.0095116 | 0.0023842 | 3.9848e-06 | 1.8989e-06 | 0.014388 | 0.014388 | 0.014388 | 0.98326 | -0.32035 | 0.98371 | -0.31155 | 3.9528
4 | 0.0030391 | 0.00076125 | -0.0030387 | -0.00076158 | 3.4563e-07 | -3.3142e-07 | 0.004599 | 0.0045992 | 0.0045992 | 0.98326 | -0.32035 | 0.98314 | -0.32274 | 1.2635
5 | -0.14857 | -0.03756 | 0.14859 | 0.037574 | 2.257e-05 | 1.4067e-05 | 0.22485 | 0.22485 | 0.22485 | 0.98371 | -0.31155 | 0.98388 | -0.30839 | 12.3542
6 | 0.13906 | 0.035175 | -0.139 | -0.035139 | 5.7993e-05 | 3.6008e-05 | 0.21046 | 0.21046 | 0.21046 | 0.98371 | -0.31155 | 0.98327 | -0.32025 | 11.5637
7 | -0.20382 | -0.05146 | 0.20391 | 0.051518 | 9.1029e-05 | 5.7448e-05 | 0.3084 | 0.3084 | 0.3084 | 0.98388 | -0.30839 | 0.98436 | -0.29907 | 16.9449
8 | 0.055233 | 0.013887 | -0.055163 | -0.013842 | 7.0218e-05 | 4.4599e-05 | 0.08355 | 0.08355 | 0.08355 | 0.98388 | -0.30839 | 0.98251 | -0.33505 | 22.9533
9 | 0.1322 | 0.033437 | -0.13216 | -0.033409 | 4.4559e-05 | 2.7578e-05 | 0.20018 | 0.20018 | 0.20018 | 0.98327 | -0.32025 | 0.9829 | -0.32728 | 10.9988
10 | 0.022451 | 0.0056287 | -0.022446 | -0.0056256 | 5.2018e-06 | 3.1756e-06 | 0.033913 | 0.033913 | 0.033913 | 0.98513 | -0.28413 | 0.98488 | -0.28899 | 9.3168
11 | -0.11051 | -0.027939 | 0.11057 | 0.027977 | 6.1089e-05 | 3.7237e-05 | 0.16701 | 0.16701 | 0.16701 | 0.98513 | -0.28413 | 0.98572 | -0.27261 | 9.1764
12 | 0.088059 | 0.022311 | -0.087933 | -0.022236 | 0.0001263 | 7.4791e-05 | 0.1331 | 0.1331 | 0.1331 | 0.98513 | -0.28413 | 0.98359 | -0.31403 | 7.3132
13 | 0.22697 | 0.057409 | -0.22668 | -0.057227 | 0.00028778 | 0.0001821 | 0.34282 | 0.34282 | 0.34282 | 0.98572 | -0.27261 | 0.98436 | -0.29907 | 18.8362
14 | -0.33754 | -0.085386 | 0.33775 | 0.085518 | 0.00020742 | 0.00013207 | 0.50983 | 0.50983 | 0.50983 | 0.98572 | -0.27261 | 0.98638 | -0.25981 | 28.0125
15 | 0.087933 | 0.022236 | -0.08792 | -0.022229 | 1.2437e-05 | 7.3659e-06 | 0.1331 | 0.1331 | 0.1331 | 0.98359 | -0.31403 | 0.98343 | -0.31697 | 7.3132
16 | 0.14766 | 0.037502 | -0.14764 | -0.037486 | 2.5454e-05 | 1.5851e-05 | 0.22239 | 0.22239 | 0.22239 | 0.98879 | -0.21339 | 0.98861 | -0.21697 | 12.2194
17 | -0.14766 | -0.037502 | 0.14774 | 0.037551 | 7.9049e-05 | 4.9224e-05 | 0.22239 | 0.22239 | 0.22239 | 0.98879 | -0.21339 | 0.98937 | -0.20227 | 12.2194
18 | 0.14764 | 0.037486 | -0.14758 | -0.037451 | 5.689e-05 | 3.5427e-05 | 0.22239 | 0.22239 | 0.22239 | 0.98861 | -0.21697 | 0.98819 | -0.22498 | 12.2195
19 | -0.15305 | -0.038881 | 0.15316 | 0.038951 | 0.00011182 | 6.9759e-05 | 0.23037 | 0.23037 | 0.23037 | 0.98937 | -0.20227 | 0.99016 | -0.18711 | 12.6579
20 | 0.14 | 0.035551 | -0.13995 | -0.035518 | 5.362e-05 | 3.3289e-05 | 0.21098 | 0.21098 | 0.21098 | 0.98819 | -0.22498 | 0.98778 | -0.23294 | 11.5924
21 | -0.067602 | -0.017088 | 0.067727 | 0.017167 | 0.00012457 | 7.9331e-05 | 0.10293 | 0.10293 | 0.10293 | 0.9778 | -0.42614 | 0.97977 | -0.38779 | 28.2773
22 | 0.067602 | 0.017088 | -0.067432 | -0.01698 | 0.00017025 | 0.00010843 | 0.10293 | 0.10293 | 0.10293 | 0.9778 | -0.42614 | 0.97511 | -0.4788 | 28.2773
23 | -0.067727 | -0.017167 | 0.06787 | 0.017258 | 0.00014315 | 9.1162e-05 | 0.10293 | 0.10293 | 0.10293 | 0.97977 | -0.38779 | 0.98203 | -0.3439 | 28.2772
24 | 0.062169 | 0.01566 | -0.062109 | -0.015622 | 5.9953e-05 | 3.8148e-05 | 0.094898 | 0.094898 | 0.094898 | 0.97511 | -0.4788 | 0.97409 | -0.49899 | 26.0709
25 | 0.0025153 | 0.00063018 | -0.0025152 | -0.00063026 | 5.0867e-08 | -8.0278e-08 | 0.0038553 | 0.0038553 | 0.0038553 | 0.97079 | -0.56396 | 0.97077 | -0.56438 | 1.0592
26 | 0.0078613 | 0.0019704 | -0.0078601 | -0.0019699 | 1.2066e-06 | 4.9828e-07 | 0.01205 | 0.01205 | 0.01205 | 0.97079 | -0.56396 | 0.97063 | -0.56718 | 3.3104
27 | -0.010377 | -0.0026006 | 0.010378 | 0.0026014 | 1.5018e-06 | 7.6536e-07 | 0.015905 | 0.015905 | 0.015905 | 0.97079 | -0.56396 | 0.97095 | -0.56092 | 4.3695
28 | 0.0025152 | 0.00063026 | -0.0025152 | -0.00063036 | 6.4705e-08 | -1.0211e-07 | 0.0038553 | 0.0038554 | 0.0038554 | 0.97077 | -0.56438 | 0.97075 | -0.56492 | 1.0592
29 | -0.014321 | -0.0035896 | 0.014326 | 0.0035921 | 4.3877e-06 | 2.5076e-06 | 0.021948 | 0.021948 | 0.021948 | 0.97095 | -0.56092 | 0.97127 | -0.55449 | 6.0296
30 | 0.051851 | 0.013129 | -0.051826 | -0.013113 | 2.498e-05 | 1.5852e-05 | 0.078736 | 0.078736 | 0.078736 | 0.98052 | -0.37353 | 0.98001 | -0.38357 | 21.6309
31 | -0.051851 | -0.013129 | 0.051885 | 0.013151 | 3.4138e-05 | 2.1663e-05 | 0.078736 | 0.078736 | 0.078736 | 0.98052 | -0.37353 | 0.98123 | -0.35983 | 21.6308
32 | 0.049879 | 0.012625 | -0.04984 | -0.012601 | 3.836e-05 | 2.4326e-05 | 0.075779 | 0.075779 | 0.075779 | 0.98001 | -0.38357 | 0.97918 | -0.3996 | 20.8185
33 | 0.0019476 | 0.00048799 | -0.0019475 | -0.0004881 | 3.3168e-08 | -1.0621e-07 | 0.0029571 | 0.0029572 | 0.0029572 | 0.98001 | -0.38357 | 0.97999 | -0.38393 | 0.81241
34 | -0.056593 | -0.01433 | 0.056617 | 0.014345 | 2.4064e-05 | 1.4961e-05 | 0.085875 | 0.085875 | 0.085875 | 0.98123 | -0.35983 | 0.98168 | -0.35098 | 11.796
35 | 0.016298 | 0.0040865 | -0.016295 | -0.0040846 | 3.3212e-06 | 1.9501e-06 | 0.024983 | 0.024983 | 0.024983 | 0.97079 | -0.56453 | 0.97057 | -0.56881 | 6.8634
36 | -0.018863 | -0.0047292 | 0.018873 | 0.0047349 | 9.4793e-06 | 5.6927e-06 | 0.028914 | 0.028914 | 0.028914 | 0.97079 | -0.56453 | 0.97132 | -0.55399 | 7.9434
37 | 0.0025648 | 0.0006427 | -0.0025648 | -0.00064279 | 6.3025e-08 | -9.4108e-08 | 0.0039313 | 0.0039314 | 0.0039314 | 0.97079 | -0.56453 | 0.97076 | -0.56505 | 1.08
38 | 0.011859 | 0.0029729 | -0.011857 | -0.0029717 | 2.1259e-06 | 1.1487e-06 | 0.018182 | 0.018182 | 0.018182 | 0.97057 | -0.56881 | 0.97038 | -0.57257 | 4.9951
39 | -0.023027 | -0.0057761 | 0.023033 | 0.0057797 | 5.8586e-06 | 3.5941e-06 | 0.035278 | 0.035278 | 0.035278 | 0.97132 | -0.55399 | 0.97159 | -0.54866 | 9.6918
40 | 0.081616 | 0.020648 | -0.081596 | -0.020637 | 1.9678e-05 | 1.1504e-05 | 0.12356 | 0.12356 | 0.12356 | 0.98343 | -0.31697 | 0.98317 | -0.322 | 6.7891
41 | -0.005037 | -0.0012623 | 0.0050379 | 0.0012624 | 8.7924e-07 | 6.5837e-08 | 0.0076797 | 0.0076796 | 0.0076797 | 0.97596 | -0.46294 | 0.97614 | -0.45928 | 2.1098
42 | 0.005037 | 0.0012623 | -0.0050367 | -0.0012623 | 3.1539e-07 | 2.3668e-08 | 0.0076797 | 0.0076798 | 0.0076798 | 0.97596 | -0.46294 | 0.97589 | -0.46426 | 2.1098
43 | -0.083861 | -0.021075 | 0.083876 | 0.021084 | 1.4664e-05 | 9.3548e-06 | 0.12786 | 0.12786 | 0.12786 | 0.97614 | -0.45928 | 0.97633 | -0.45562 | 35.1255
44 | 0.070499 | 0.017726 | -0.070483 | -0.017716 | 1.613e-05 | 1.0277e-05 | 0.10749 | 0.10749 | 0.10749 | 0.97614 | -0.45928 | 0.9759 | -0.46407 | 29.5295
45 | 0.0083246 | 0.0020864 | -0.0083238 | -0.002086 | 7.8542e-07 | 3.4009e-07 | 0.01269 | 0.01269 | 0.01269 | 0.97614 | -0.45928 | 0.97604 | -0.46126 | 3.4863
46 | -0.17591 | -0.044718 | 0.17595 | 0.044741 | 3.7551e-05 | 2.3571e-05 | 0.26429 | 0.26429 | 0.26429 | 0.99126 | -0.16598 | 0.99149 | -0.16155 | 14.5215
47 | 0.17591 | 0.044718 | -0.17581 | -0.044656 | 9.7761e-05 | 6.1365e-05 | 0.26429 | 0.26429 | 0.26429 | 0.99126 | -0.16598 | 0.99066 | -0.17752 | 14.5215
48 | 0.3716 | 0.094654 | -0.37132 | -0.094474 | 0.00028259 | 0.00018008 | 0.55824 | 0.55824 | 0.55824 | 0.99149 | -0.16155 | 0.99067 | -0.17732 | 30.6726
49 | -0.54755 | -0.13939 | 0.54943 | 0.14059 | 0.0018766 | 0.0011986 | 0.82253 | 0.82253 | 0.82253 | 0.99149 | -0.16155 | 0.9952 | -0.090733 | 45.1941
50 | 0.16749 | 0.042571 | -0.16745 | -0.042542 | 4.7657e-05 | 2.9856e-05 | 0.2518 | 0.2518 | 0.2518 | 0.99066 | -0.17752 | 0.99035 | -0.18343 | 13.8349
51 | 0.0020745 | 0.00051964 | -0.0020744 | -0.00051989 | 8.806e-08 | -2.433e-07 | 0.0031459 | 0.003146 | 0.003146 | 0.98118 | -0.36079 | 0.98114 | -0.36168 | 0.8643
52 | -0.0020745 | -0.00051964 | 0.0020746 | 0.00051939 | 9.2331e-08 | -2.5515e-07 | 0.0031459 | 0.0031458 | 0.0031459 | 0.98118 | -0.36079 | 0.98123 | -0.35985 | 0.86427
53 | -0.0065071 | -0.0016303 | 0.006508 | 0.0016306 | 9.2822e-07 | 2.7291e-07 | 0.0098677 | 0.0098676 | 0.0098677 | 0.98123 | -0.35985 | 0.98138 | -0.35686 | 2.7109
54 | 0.0072131 | 0.0018077 | -0.0072131 | -0.0018077 | 8.2321e-08 | 3.0528e-08 | 0.011062 | 0.011062 | 0.011062 | 0.97029 | -0.57434 | 0.97028 | -0.57458 | 3.039
55 | -0.0072131 | -0.0018077 | 0.0072137 | 0.001808 | 6.0744e-07 | 2.2524e-07 | 0.011062 | 0.011062 | 0.011062 | 0.97029 | -0.57434 | 0.97038 | -0.57257 | 3.039
56 | 0.0072131 | 0.0018077 | -0.0072126 | -0.0018075 | 4.8934e-07 | 1.8148e-07 | 0.011062 | 0.011062 | 0.011062 | 0.97028 | -0.57458 | 0.97021 | -0.576 | 3.039
57 | -0.042006 | -0.010591 | 0.042056 | 0.010623 | 5.0539e-05 | 3.1934e-05 | 0.064052 | 0.064052 | 0.064052 | 0.97619 | -0.45808 | 0.97747 | -0.43297 | 17.5968
58 | 0.042006 | 0.010591 | -0.041952 | -0.010558 | 5.3458e-05 | 3.3779e-05 | 0.064052 | 0.064053 | 0.064053 | 0.97619 | -0.45808 | 0.97483 | -0.48471 | 17.5969
59 | -0.042056 | -0.010623 | 0.042098 | 0.01065 | 4.2112e-05 | 2.6608e-05 | 0.064052 | 0.064052 | 0.064052 | 0.97747 | -0.43297 | 0.97854 | -0.4121 | 17.5968
60 | 0.036263 | 0.0091317 | -0.036241 | -0.0091177 | 2.2282e-05 | 1.4019e-05 | 0.055369 | 0.055369 | 0.055369 | 0.97483 | -0.48471 | 0.97418 | -0.49757 | 15.2112
61 | -0.045655 | -0.011541 | 0.045682 | 0.011559 | 2.7385e-05 | 1.7336e-05 | 0.069461 | 0.069461 | 0.069461 | 0.97854 | -0.4121 | 0.97918 | -0.3996 | 19.0827
62 | -0.079208 | -0.020115 | 0.079314 | 0.020182 | 0.00010573 | 6.7422e-05 | 0.12005 | 0.12005 | 0.12005 | 0.98253 | -0.33415 | 0.98397 | -0.30645 | 32.9814
63 | 0.079208 | 0.020115 | -0.079171 | -0.020091 | 3.7163e-05 | 2.3697e-05 | 0.12005 | 0.12005 | 0.12005 | 0.98253 | -0.33415 | 0.98203 | -0.3439 | 32.9814
64 | -0.092004 | -0.023363 | 0.092066 | 0.023402 | 6.1993e-05 | 3.87e-05 | 0.13924 | 0.13924 | 0.13924 | 0.98397 | -0.30645 | 0.98469 | -0.29246 | 12.7513
65 | 0.011301 | 0.0028328 | -0.011299 | -0.0028317 | 1.9152e-06 | 1.0054e-06 | 0.017124 | 0.017124 | 0.017124 | 0.98203 | -0.3439 | 0.98185 | -0.34746 | 4.7043
66 | 0.02277 | 0.0057088 | -0.022764 | -0.0057055 | 5.5124e-06 | 3.3703e-06 | 0.034421 | 0.034421 | 0.034421 | 0.98436 | -0.29907 | 0.9841 | -0.30415 | 9.4564
67 | -0.34288 | -0.086804 | 0.34322 | 0.08702 | 0.00033984 | 0.00021642 | 0.51757 | 0.51757 | 0.51757 | 0.98638 | -0.25981 | 0.98745 | -0.23918 | 28.4378
68 | 0.044577 | 0.011189 | -0.044559 | -0.011178 | 1.7634e-05 | 1.1155e-05 | 0.067518 | 0.067518 | 0.067518 | 0.98251 | -0.33505 | 0.98209 | -0.34334 | 18.5489
69 | 0.015251 | 0.0038224 | -0.015251 | -0.0038222 | 4.2253e-07 | 2.435e-07 | 0.023061 | 0.023061 | 0.023061 | 0.9841 | -0.30415 | 0.98407 | -0.30473 | 6.3353
70 | -0.083876 | -0.021084 | 0.08396 | 0.021137 | 8.3904e-05 | 5.3527e-05 | 0.12786 | 0.12786 | 0.12786 | 0.97633 | -0.45562 | 0.9774 | -0.43469 | 35.1255
71 | 0.0095413 | 0.0023915 | -0.0095399 | -0.0023908 | 1.446e-06 | 6.9785e-07 | 0.014548 | 0.014548 | 0.014548 | 0.9759 | -0.46407 | 0.97574 | -0.46725 | 3.9968
72 | 0.041438 | 0.010432 | -0.041378 | -0.010394 | 6.0164e-05 | 3.8004e-05 | 0.0632 | 0.0632 | 0.0632 | 0.9759 | -0.46407 | 0.97435 | -0.49449 | 17.3627
73 | 0.019503 | 0.0048918 | -0.019503 | -0.0048914 | 7.0245e-07 | 4.2311e-07 | 0.029739 | 0.029739 | 0.029739 | 0.9759 | -0.46407 | 0.97586 | -0.46483 | 8.1701
74 | 0.0041362 | 0.0010365 | -0.0041359 | -0.0010366 | 2.6793e-07 | -5.3083e-08 | 0.0063058 | 0.0063058 | 0.0063058 | 0.97604 | -0.46126 | 0.97598 | -0.46262 | 1.7324
75 | 0.056129 | 0.014124 | -0.056103 | -0.014107 | 2.565e-05 | 1.6301e-05 | 0.085763 | 0.085763 | 0.085763 | 0.97409 | -0.49899 | 0.9736 | -0.50856 | 23.5613
76 | 0.053809 | 0.013532 | -0.053735 | -0.013485 | 7.4003e-05 | 4.7e-05 | 0.082257 | 0.082257 | 0.082257 | 0.9736 | -0.50856 | 0.97214 | -0.53739 | 22.5981
77 | 0.030004 | 0.0075289 | -0.029994 | -0.0075229 | 9.6526e-06 | 6.0264e-06 | 0.045929 | 0.045929 | 0.045929 | 0.97214 | -0.53739 | 0.9718 | -0.54414 | 12.6179
78 | 0.023731 | 0.0059565 | -0.023712 | -0.0059448 | 1.9025e-05 | 1.17e-05 | 0.036328 | 0.036328 | 0.036328 | 0.97214 | -0.53739 | 0.97129 | -0.55422 | 9.9803
79 | 0.023827 | 0.0059771 | -0.023812 | -0.0059684 | 1.4152e-05 | 8.7061e-06 | 0.036485 | 0.036485 | 0.036485 | 0.9718 | -0.54414 | 0.97117 | -0.55661 | 10.0235
80 | 0.018011 | 0.004516 | -0.018011 | -0.0045158 | 2.3812e-07 | 1.4207e-07 | 0.027594 | 0.027594 | 0.027594 | 0.97129 | -0.55422 | 0.97127 | -0.55449 | 7.5809
81 | 0.015464 | 0.0038762 | -0.015463 | -0.0038753 | 1.4533e-06 | 8.447e-07 | 0.023694 | 0.023694 | 0.023694 | 0.97117 | -0.55661 | 0.97107 | -0.55858 | 6.5094
82 | 0.0058902 | 0.0014762 | -0.0058891 | -0.0014759 | 1.1642e-06 | 2.7376e-07 | 0.0090259 | 0.0090261 | 0.0090261 | 0.97107 | -0.55858 | 0.97086 | -0.56273 | 2.4797
83 | -0.15893 | -0.040396 | 0.15896 | 0.040414 | 2.8125e-05 | 1.7578e-05 | 0.23904 | 0.23904 | 0.23904 | 0.99016 | -0.18711 | 0.99035 | -0.18343 | 13.1341
84 | -0.061094 | -0.015467 | 0.061123 | 0.015485 | 2.9558e-05 | 1.7872e-05 | 0.092661 | 0.09266 | 0.092661 | 0.98168 | -0.35098 | 0.9822 | -0.3409 | 8.4854
85 | -0.027609 | -0.0069265 | 0.027629 | 0.0069389 | 1.9966e-05 | 1.2409e-05 | 0.042287 | 0.042287 | 0.042287 | 0.97159 | -0.54866 | 0.97236 | -0.5335 | 11.6172
86 | 0.0045763 | 0.0011469 | -0.004576 | -0.0011469 | 2.5804e-07 | -8.3242e-09 | 0.0070087 | 0.0070088 | 0.0070088 | 0.97159 | -0.54866 | 0.97153 | -0.54984 | 1.9255
87 | 0.078028 | 0.019743 | -0.078012 | -0.019734 | 1.5831e-05 | 9.1735e-06 | 0.11816 | 0.11816 | 0.11816 | 0.98317 | -0.322 | 0.98296 | -0.32623 | 6.4924
88 | 0.031782 | 0.0079807 | -0.031779 | -0.007979 | 2.631e-06 | 1.647e-06 | 0.048637 | 0.048637 | 0.048637 | 0.97244 | -0.53176 | 0.97236 | -0.5335 | 13.3619
89 | -0.031782 | -0.0079807 | 0.031824 | 0.0080068 | 4.1775e-05 | 2.6151e-05 | 0.048637 | 0.048637 | 0.048637 | 0.97244 | -0.53176 | 0.97384 | -0.50425 | 13.3619
90 | -0.031824 | -0.0080068 | 0.031834 | 0.0080132 | 1.0169e-05 | 6.3653e-06 | 0.048637 | 0.048637 | 0.048637 | 0.97384 | -0.50425 | 0.97418 | -0.49757 | 13.3619
91 | 0.36299 | 0.092385 | -0.36259 | -0.092128 | 0.00040364 | 0.00025717 | 0.54573 | 0.54573 | 0.54573 | 0.99067 | -0.17732 | 0.98946 | -0.20042 | 29.985
92 | -0.56003 | -0.14325 | 0.56107 | 0.14392 | 0.0010452 | 0.00066762 | 0.83838 | 0.83838 | 0.83838 | 0.9952 | -0.090733 | 0.99723 | -0.052251 | 46.0648
93 | -0.0083292 | -0.0020875 | 0.0083308 | 0.0020882 | 1.5992e-06 | 6.9866e-07 | 0.012754 | 0.012754 | 0.012754 | 0.97175 | -0.54593 | 0.97195 | -0.5419 | 3.5039
94 | -0.016727 | -0.0041925 | 0.01673 | 0.0041945 | 3.4898e-06 | 2.0576e-06 | 0.025608 | 0.025608 | 0.025608 | 0.97195 | -0.5419 | 0.97217 | -0.53752 | 7.0352
95 | -0.073451 | -0.018586 | 0.073464 | 0.018594 | 1.3616e-05 | 7.7852e-06 | 0.11128 | 0.11128 | 0.11128 | 0.98276 | -0.33009 | 0.98296 | -0.32623 | 6.1141
96 | 0.073451 | 0.018586 | -0.073438 | -0.018579 | 1.231e-05 | 7.0386e-06 | 0.11128 | 0.11128 | 0.11128 | 0.98276 | -0.33009 | 0.98258 | -0.33358 | 6.1141
97 | 0.069052 | 0.01748 | -0.06904 | -0.017473 | 1.2398e-05 | 6.9787e-06 | 0.10463 | 0.10463 | 0.10463 | 0.98258 | -0.33358 | 0.98238 | -0.33732 | 5.7492
98 | 0.0036072 | 0.00090394 | -0.003607 | -0.00090401 | 1.5959e-07 | -6.9564e-08 | 0.0055323 | 0.0055324 | 0.0055324 | 0.97021 | -0.576 | 0.97016 | -0.57693 | 1.5199
99 | -0.10703 | -0.02705 | 0.10706 | 0.027068 | 3.0081e-05 | 1.829e-05 | 0.16236 | 0.16236 | 0.16236 | 0.98138 | -0.35686 | 0.98168 | -0.351 | 8.9208
100 | 0.10052 | 0.02542 | -0.10048 | -0.025394 | 4.1607e-05 | 2.5122e-05 | 0.15249 | 0.15249 | 0.15249 | 0.98138 | -0.35686 | 0.98094 | -0.36549 | 8.3787
101 | 0.13297 | 0.033768 | -0.13292 | -0.033742 | 4.2227e-05 | 2.6129e-05 | 0.20046 | 0.20046 | 0.20046 | 0.98778 | -0.23294 | 0.98743 | -0.23954 | 11.0144
102 | -0.093843 | -0.023847 | 0.093855 | 0.023854 | 1.1584e-05 | 6.9257e-06 | 0.14193 | 0.14193 | 0.14193 | 0.98469 | -0.29246 | 0.98482 | -0.2899 | 7.7983
103 | -0.004874 | -0.0012215 | 0.0048743 | 0.0012215 | 3.6551e-07 | 1.3617e-08 | 0.0074335 | 0.0074334 | 0.0074335 | 0.97566 | -0.46883 | 0.97574 | -0.46725 | 2.0422
104 | -0.3536 | -0.08962 | 0.35426 | 0.09004 | 0.00066004 | 0.00042044 | 0.5332 | 0.5332 | 0.5332 | 0.98745 | -0.23918 | 0.98946 | -0.20042 | 29.2967
105 | 0.12579 | 0.031812 | -0.12575 | -0.031787 | 4.0821e-05 | 2.5176e-05 | 0.19053 | 0.19053 | 0.19053 | 0.9829 | -0.32728 | 0.98256 | -0.33405 | 10.4688
106 | 0.037764 | 0.0094749 | -0.037746 | -0.0094634 | 1.8205e-05 | 1.1464e-05 | 0.057222 | 0.057222 | 0.057222 | 0.98209 | -0.34334 | 0.98157 | -0.35346 | 15.7204
107 | -0.087917 | -0.022129 | 0.088013 | 0.02219 | 9.5757e-05 | 6.1106e-05 | 0.13388 | 0.13388 | 0.13388 | 0.9774 | -0.43469 | 0.97856 | -0.41193 | 36.7807
108 | 0.036501 | 0.0091719 | -0.036484 | -0.0091613 | 1.6733e-05 | 1.0531e-05 | 0.055752 | 0.055752 | 0.055752 | 0.97435 | -0.49449 | 0.97387 | -0.5041 | 15.3165
109 | 0.019503 | 0.0048914 | -0.019497 | -0.0048878 | 6.0339e-06 | 3.6345e-06 | 0.029739 | 0.029739 | 0.029739 | 0.97586 | -0.46483 | 0.97553 | -0.47132 | 8.1701
110 | -0.099047 | -0.025167 | 0.099071 | 0.025182 | 2.4424e-05 | 1.4706e-05 | 0.14972 | 0.14972 | 0.14972 | 0.98522 | -0.28225 | 0.98548 | -0.27713 | 8.2262
111 | 0.097357 | 0.024744 | -0.097345 | -0.024737 | 1.2409e-05 | 7.4554e-06 | 0.14717 | 0.14717 | 0.14717 | 0.98522 | -0.28225 | 0.98508 | -0.2849 | 8.0861
112 | -0.10074 | -0.0256 | 0.10076 | 0.025613 | 2.1109e-05 | 1.2736e-05 | 0.15223 | 0.15223 | 0.15223 | 0.98548 | -0.27713 | 0.98571 | -0.27278 | 8.3645
113 | 0.095654 | 0.024313 | -0.095631 | -0.024299 | 2.3035e-05 | 1.3808e-05 | 0.14461 | 0.14461 | 0.14461 | 0.98508 | -0.2849 | 0.98482 | -0.2899 | 7.9457
114 | -0.1075 | -0.027302 | 0.10753 | 0.027321 | 2.9716e-05 | 1.8061e-05 | 0.16241 | 0.16241 | 0.16241 | 0.98571 | -0.27278 | 0.98601 | -0.26704 | 8.9237
115 | -0.11444 | -0.029051 | 0.11449 | 0.029083 | 5.1928e-05 | 3.1755e-05 | 0.17283 | 0.17283 | 0.17283 | 0.98601 | -0.26704 | 0.9865 | -0.25761 | 9.4963
116 | -0.11838 | -0.030058 | 0.11844 | 0.030097 | 6.363e-05 | 3.9026e-05 | 0.1787 | 0.1787 | 0.1787 | 0.9865 | -0.25761 | 0.98708 | -0.24645 | 9.8187
117 | -0.57167 | -0.14657 | 0.57313 | 0.1475 | 0.0014524 | 0.0009278 | 0.85419 | 0.85419 | 0.85419 | 0.99723 | -0.052251 | 1 | 0 | 46.9338
118 | -0.021606 | -0.0054164 | 0.021617 | 0.005423 | 1.0808e-05 | 6.59e-06 | 0.033071 | 0.033071 | 0.033071 | 0.97217 | -0.53752 | 0.9727 | -0.52703 | 9.0854
119 | -0.12566 | -0.031907 | 0.1257 | 0.031932 | 4.1748e-05 | 2.5729e-05 | 0.18958 | 0.18958 | 0.18958 | 0.98708 | -0.24645 | 0.98743 | -0.23954 | 10.4167
120 | -0.0056398 | -0.0014135 | 0.0056398 | 0.0014135 | 1.5249e-08 | 2.2117e-09 | 0.0083997 | 0.0083997 | 0.0083997 | 0.9991 | -0.017375 | 0.9991 | -0.017318 | 2.3076
121 | -0.0073437 | -0.0018405 | 0.0073446 | 0.0018408 | 8.609e-07 | 2.9962e-07 | 0.010937 | 0.010937 | 0.010937 | 0.9991 | -0.017318 | 0.99923 | -0.014857 | 3.0048
122 | -0.012895 | -0.003232 | 0.012899 | 0.0032338 | 3.358e-06 | 1.8309e-06 | 0.019203 | 0.019203 | 0.019203 | 0.99923 | -0.014857 | 0.99951 | -0.0093928 | 5.2757
123 | 0.015109 | 0.0037882 | -0.015105 | -0.0037861 | 3.6505e-06 | 2.1076e-06 | 0.023047 | 0.023047 | 0.023047 | 0.97553 | -0.47132 | 0.97528 | -0.47639 | 6.3316
124 | -0.014722 | -0.0036907 | 0.014723 | 0.0036915 | 1.3753e-06 | 7.8012e-07 | 0.021917 | 0.021917 | 0.021917 | 0.99951 | -0.0093928 | 0.99961 | -0.0074324 | 6.0213
125 | 0.010676 | 0.002676 | -0.010675 | -0.0026756 | 6.5773e-07 | 3.3847e-07 | 0.016289 | 0.016289 | 0.016289 | 0.97528 | -0.47639 | 0.97521 | -0.47768 | 4.475
126 | -0.016547 | -0.0041486 | 0.016549 | 0.0041496 | 1.692e-06 | 9.8541e-07 | 0.024632 | 0.024632 | 0.024632 | 0.99961 | -0.0074324 | 0.99972 | -0.0052868 | 6.7671
127 | -0.091788 | -0.023136 | 0.091893 | 0.023204 | 0.0001058 | 6.7529e-05 | 0.13962 | 0.13962 | 0.13962 | 0.97856 | -0.41193 | 0.97979 | -0.38787 | 38.3575
128 | 0.031571 | 0.0079299 | -0.031547 | -0.0079153 | 2.3332e-05 | 1.46e-05 | 0.048245 | 0.048245 | 0.048245 | 0.97387 | -0.5041 | 0.97308 | -0.5196 | 13.2541
129 | 0.0079396 | 0.00199 | -0.0079382 | -0.0019894 | 1.4667e-06 | 6.0628e-07 | 0.012115 | 0.012115 | 0.012115 | 0.97521 | -0.47768 | 0.97501 | -0.48156 | 3.3282
130 | -0.0068055 | -0.0017056 | 0.0068059 | 0.0017057 | 3.989e-07 | 1.2921e-07 | 0.010322 | 0.010322 | 0.010322 | 0.98108 | -0.36305 | 0.98114 | -0.36182 | 2.8357
131 | -0.010477 | -0.0026257 | 0.010478 | 0.0026263 | 1.0787e-06 | 5.4647e-07 | 0.01589 | 0.01589 | 0.01589 | 0.98114 | -0.36182 | 0.98125 | -0.35965 | 4.3654
132 | 0.0036714 | 0.00092001 | -0.0036712 | -0.00092009 | 1.8239e-07 | -8.1384e-08 | 0.005568 | 0.0055681 | 0.0055681 | 0.98114 | -0.36182 | 0.98109 | -0.36286 | 1.5297
133 | -0.017152 | -0.0042989 | 0.017154 | 0.0043002 | 2.2186e-06 | 1.3094e-06 | 0.02601 | 0.02601 | 0.02601 | 0.98125 | -0.35965 | 0.98139 | -0.35694 | 7.1457
134 | -0.03137 | -0.0078636 | 0.031376 | 0.0078669 | 5.2025e-06 | 3.2521e-06 | 0.047565 | 0.047565 | 0.047565 | 0.98139 | -0.35694 | 0.98157 | -0.35346 | 13.0673
135 | 0.014216 | 0.0035634 | -0.014214 | -0.0035624 | 1.7688e-06 | 1.0038e-06 | 0.021555 | 0.021555 | 0.021555 | 0.98139 | -0.35694 | 0.98126 | -0.35955 | 5.9217
136 | -0.018245 | -0.0045747 | 0.018247 | 0.004576 | 2.1202e-06 | 1.2564e-06 | 0.027157 | 0.027157 | 0.027157 | 0.99972 | -0.0052868 | 0.99985 | -0.0028486 | 7.4608
137 | -0.021378 | -0.0053607 | 0.021381 | 0.0053625 | 2.9027e-06 | 1.7574e-06 | 0.031817 | 0.031817 | 0.031817 | 0.99985 | -0.0028486 | 1 | 0 | 8.7409
138 | 0.06561 | 0.016613 | -0.065598 | -0.016607 | 1.1271e-05 | 6.2517e-06 | 0.09944 | 0.09944 | 0.09944 | 0.98238 | -0.33732 | 0.9822 | -0.3409 | 5.4637
139 | -0.026545 | -0.006658 | 0.026554 | 0.0066639 | 9.4065e-06 | 5.8313e-06 | 0.040609 | 0.040609 | 0.040609 | 0.9727 | -0.52703 | 0.97308 | -0.5196 | 11.1563
140 | 0.0043881 | 0.0010996 | -0.0043877 | -0.0010997 | 3.6866e-07 | -3.7419e-08 | 0.0066969 | 0.006697 | 0.006697 | 0.97501 | -0.48156 | 0.97492 | -0.48333 | 1.8398
141 | -0.095924 | -0.024214 | 0.096027 | 0.024279 | 0.00010295 | 6.5234e-05 | 0.14574 | 0.14574 | 0.14574 | 0.97979 | -0.38787 | 0.98094 | -0.36549 | 20.0195
142 | -0.11151 | -0.028184 | 0.11154 | 0.028205 | 3.4518e-05 | 2.1074e-05 | 0.1691 | 0.1691 | 0.1691 | 0.98168 | -0.351 | 0.98202 | -0.34454 | 9.2914
143 | -0.11901 | -0.030077 | 0.11907 | 0.030114 | 5.9934e-05 | 3.6804e-05 | 0.18042 | 0.18042 | 0.18042 | 0.98202 | -0.34454 | 0.98256 | -0.33405 | 9.9134

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.59926 | 0.15364

## res_load
| p_mw | q_mvar
0 | 0.001939 | 0.00048595
1 | 0.0013335 | 0.0003342
2 | 0.0031941 | 0.00080052
3 | 0.0030387 | 0.00076158
4 | 0.0067946 | 0.0017029
5 | 0.022446 | 0.0056256
6 | 0.0053065 | 0.0013299
7 | 0.0075799 | 0.0018997
8 | 0.005263 | 0.001319
9 | 0.0078601 | 0.0019699
10 | 0.003943 | 0.00098822
11 | 0.0025152 | 0.00063036
12 | 0.0047074 | 0.0011798
13 | 0.0044358 | 0.0011117
14 | 0.0041542 | 0.0010411
15 | 0.0025648 | 0.00064279
16 | 0.0063047 | 0.0015801
17 | 0.0050367 | 0.0012623
18 | 0.0083194 | 0.002085
19 | 0.0020744 | 0.00051989
20 | 0.0044325 | 0.0011109
21 | 0.0046434 | 0.0011637
22 | 0.0056891 | 0.0014258
23 | 0.0035568 | 0.00089143
24 | 0.012691 | 0.0031806
25 | 0.0051318 | 0.0012861
26 | 0.010586 | 0.0026531
27 | 0.0075134 | 0.001883
28 | 0.0041876 | 0.0010495
29 | 0.00598 | 0.0014987
30 | 0.002294 | 0.00057494
31 | 0.0061676 | 0.0015457
32 | 0.0057009 | 0.0014288
33 | 0.0083482 | 0.0020923
34 | 0.0036857 | 0.00092373
35 | 0.0095725 | 0.0023991
36 | 0.005767 | 0.0014454
37 | 0.0041578 | 0.0010421
38 | 0.0019475 | 0.0004881
39 | 0.0044767 | 0.001122
40 | 0.0058891 | 0.0014759
41 | 0.0035677 | 0.00089415
42 | 0.0041501 | 0.0010401
43 | 0.004407 | 0.0011045
44 | 0.004576 | 0.0011469
45 | 0.0083315 | 0.0020881
46 | 0.0106 | 0.0026565
47 | 0.0083292 | 0.0020875
48 | 0.0083961 | 0.0021043
49 | 0.0084899 | 0.0021278
50 | 0.0045482 | 0.0011399
51 | 0.0043863 | 0.0010993
52 | 0.0036054 | 0.00090359
53 | 0.003607 | 0.00090401
54 | 0.0069823 | 0.0017499
55 | 0.0017769 | 0.00044535
56 | 0.011299 | 0.0028317
57 | 0.004874 | 0.0012215
58 | 0.0046655 | 0.0011693
59 | 0.010373 | 0.0025998
60 | 0.0063712 | 0.0015968
61 | 0.0067953 | 0.0017031
62 | 0.015251 | 0.0038222
63 | 0.0039574 | 0.00099182
64 | 0.0048772 | 0.0012223
65 | 0.0041359 | 0.0010366
66 | 0.0016895 | 0.00042343
67 | 0.001667 | 0.00041778
68 | 0.0016912 | 0.00042385
69 | 0.0067421 | 0.0016897
70 | 0.0017758 | 0.00044506
71 | 0.0069056 | 0.0017307
72 | 0.0038901 | 0.00097495
73 | 0.0083308 | 0.0020879
74 | 0.010599 | 0.0026565
75 | 0.0048756 | 0.0012219
76 | 0.0072206 | 0.0018097
77 | 0.0072189 | 0.0018092
78 | 0.0056398 | 0.0014135
79 | 0.0017039 | 0.00042704
80 | 0.0055508 | 0.0013912
81 | 0.0043875 | 0.0010996
82 | 0.0018231 | 0.00045691
83 | 0.0044293 | 0.0011101
84 | 0.0018239 | 0.00045711
85 | 0.0037746 | 0.00094601
86 | 0.0049133 | 0.0012314
87 | 0.0027358 | 0.00068565
88 | 0.0068055 | 0.0017056
89 | 0.0066738 | 0.0016726
90 | 0.0036712 | 0.00092009
91 | 0.0063703 | 0.0015966
92 | 0.014214 | 0.0035624
93 | 0.0016963 | 0.00042513
94 | 0.0031311 | 0.00078473
95 | 0.0031019 | 0.0007774
96 | 0.0034299 | 0.00085962
97 | 0.0044753 | 0.0011216
98 | 0.0049277 | 0.001235
99 | 0.0049934 | 0.0012515
100 | 0.0035501 | 0.00088973
101 | 0.0043877 | 0.0010997
102 | 0.0040303 | 0.0010101
103 | 0.0044496 | 0.0011152
104 | 0.0044503 | 0.0011154
105 | 0.0074708 | 0.0018724
106 | 0.0066753 | 0.001673

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1