## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-509_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-509_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-509_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_261-509_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_261-509_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_261-509_0_4_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_261-509_0_4_node_61 | 0.4 | n |  | TRUE
7 | bus_LV_261-509_0_4_node_8 | 0.4 | n |  | TRUE
8 | bus_LV_261-509_0_4_node_132 | 0.4 | n |  | TRUE
9 | bus_LV_261-509_0_4_node_6 | 0.4 | n |  | TRUE
10 | bus_LV_261-509_0_4_node_82 | 0.4 | n |  | TRUE
11 | bus_LV_261-509_0_4_node_81 | 0.4 | n |  | TRUE
12 | bus_LV_261-509_0_4_node_7 | 0.4 | n |  | TRUE
13 | bus_LV_261-509_0_4_node_12 | 0.4 | n |  | TRUE
14 | bus_LV_261-509_0_4_node_86 | 0.4 | n |  | TRUE
15 | bus_LV_261-509_0_4_node_57 | 0.4 | n |  | TRUE
16 | bus_LV_261-509_0_4_node_9 | 0.4 | n |  | TRUE
17 | bus_LV_261-509_0_4_node_32 | 0.4 | n |  | TRUE
18 | bus_LV_261-509_0_4_node_24 | 0.4 | n |  | TRUE
19 | bus_LV_261-509_0_4_node_88 | 0.4 | n |  | TRUE
20 | bus_LV_261-509_0_4_node_20 | 0.4 | n |  | TRUE
21 | bus_LV_261-509_0_4_node_14 | 0.4 | n |  | TRUE
22 | bus_LV_261-509_0_4_node_125 | 0.4 | n |  | TRUE
23 | bus_LV_261-509_0_4_node_124 | 0.4 | n |  | TRUE
24 | bus_LV_261-509_0_4_node_15 | 0.4 | n |  | TRUE
25 | bus_LV_261-509_0_4_node_33 | 0.4 | n |  | TRUE
26 | bus_LV_261-509_0_4_node_118 | 0.4 | n |  | TRUE
27 | bus_LV_261-509_0_4_node_17 | 0.4 | n |  | TRUE
28 | bus_LV_261-509_0_4_node_26 | 0.4 | n |  | TRUE
29 | bus_LV_261-509_0_4_node_126 | 0.4 | n |  | TRUE
30 | bus_LV_261-509_0_4_node_18 | 0.4 | n |  | TRUE
31 | bus_LV_261-509_0_4_node_19 | 0.4 | n |  | TRUE
32 | bus_LV_261-509_0_4_node_72 | 0.4 | n |  | TRUE
33 | bus_LV_261-509_0_4_node_71 | 0.4 | n |  | TRUE
34 | bus_LV_261-509_0_4_node_74 | 0.4 | n |  | TRUE
35 | bus_LV_261-509_0_4_node_22 | 0.4 | n |  | TRUE
36 | bus_LV_261-509_0_4_node_98 | 0.4 | n |  | TRUE
37 | bus_LV_261-509_0_4_node_95 | 0.4 | n |  | TRUE
38 | bus_LV_261-509_0_4_node_23 | 0.4 | n |  | TRUE
39 | bus_LV_261-509_0_4_node_93 | 0.4 | n |  | TRUE
40 | bus_LV_261-509_0_4_node_99 | 0.4 | n |  | TRUE
41 | bus_LV_261-509_0_4_node_90 | 0.4 | n |  | TRUE
42 | bus_LV_261-509_0_4_node_52 | 0.4 | n |  | TRUE
43 | bus_LV_261-509_0_4_node_29 | 0.4 | n |  | TRUE
44 | bus_LV_261-509_0_4_node_107 | 0.4 | n |  | TRUE
45 | bus_LV_261-509_0_4_node_106 | 0.4 | n |  | TRUE
46 | bus_LV_261-509_0_4_node_30 | 0.4 | n |  | TRUE
47 | bus_LV_261-509_0_4_node_38 | 0.4 | n |  | TRUE
48 | bus_LV_261-509_0_4_node_112 | 0.4 | n |  | TRUE
49 | bus_LV_261-509_0_4_node_101 | 0.4 | n |  | TRUE
50 | bus_LV_261-509_0_4_node_117 | 0.4 | n |  | TRUE
51 | bus_LV_261-509_0_4_node_35 | 0.4 | n |  | TRUE
52 | bus_LV_261-509_0_4_node_36 | 0.4 | n |  | TRUE
53 | bus_LV_261-509_0_4_node_70 | 0.4 | n |  | TRUE
54 | bus_LV_261-509_0_4_node_79 | 0.4 | n |  | TRUE
55 | bus_LV_261-509_0_4_node_37 | 0.4 | n |  | TRUE
56 | bus_LV_261-509_0_4_node_133 | 0.4 | n |  | TRUE
57 | bus_LV_261-509_0_4_node_75 | 0.4 | n |  | TRUE
58 | bus_LV_261-509_0_4_node_47 | 0.4 | n |  | TRUE
59 | bus_LV_261-509_0_4_node_84 | 0.4 | n |  | TRUE
60 | bus_LV_261-509_0_4_node_60 | 0.4 | n |  | TRUE
61 | bus_LV_261-509_0_4_node_80 | 0.4 | n |  | TRUE
62 | bus_LV_261-509_0_4_node_87 | 0.4 | n |  | TRUE
63 | bus_LV_261-509_0_4_node_121 | 0.4 | n |  | TRUE
64 | bus_LV_261-509_0_4_node_55 | 0.4 | n |  | TRUE
65 | bus_LV_261-509_0_4_node_89 | 0.4 | n |  | TRUE
66 | bus_LV_261-509_0_4_node_123 | 0.4 | n |  | TRUE
67 | bus_LV_261-509_0_4_node_119 | 0.4 | n |  | TRUE
68 | bus_LV_261-509_0_4_node_120 | 0.4 | n |  | TRUE
69 | bus_LV_261-509_0_4_node_73 | 0.4 | n |  | TRUE
70 | bus_LV_261-509_0_4_node_83 | 0.4 | n |  | TRUE
71 | bus_LV_261-509_0_4_node_104 | 0.4 | n |  | TRUE
72 | bus_LV_261-509_0_4_node_96 | 0.4 | n |  | TRUE
73 | bus_LV_261-509_0_4_node_91 | 0.4 | n |  | TRUE
74 | bus_LV_261-509_0_4_node_100 | 0.4 | n |  | TRUE
75 | bus_LV_261-509_0_4_node_97 | 0.4 | n |  | TRUE
76 | bus_LV_261-509_0_4_node_66 | 0.4 | n |  | TRUE
77 | bus_LV_261-509_0_4_node_67 | 0.4 | n |  | TRUE
78 | bus_LV_261-509_0_4_node_68 | 0.4 | n |  | TRUE
79 | bus_LV_261-509_0_4_node_69 | 0.4 | n |  | TRUE
80 | bus_LV_261-509_0_4_node_128 | 0.4 | n |  | TRUE
81 | bus_LV_261-509_0_4_node_127 | 0.4 | n |  | TRUE
82 | bus_LV_261-509_0_4_node_64 | 0.4 | n |  | TRUE
83 | bus_LV_261-509_0_4_node_62 | 0.4 | n |  | TRUE
84 | bus_LV_261-509_0_4_node_65 | 0.4 | n |  | TRUE
85 | bus_LV_261-509_0_4_node_58 | 0.4 | n |  | TRUE
86 | bus_LV_261-509_0_4_node_110 | 0.4 | n |  | TRUE
87 | bus_LV_261-509_0_4_node_102 | 0.4 | n |  | TRUE
88 | bus_LV_261-509_0_4_node_115 | 0.4 | n |  | TRUE
89 | bus_LV_261-509_0_4_node_108 | 0.4 | n |  | TRUE
90 | bus_LV_261-509_0_4_node_105 | 0.4 | n |  | TRUE
91 | bus_LV_261-509_0_4_node_78 | 0.4 | n |  | TRUE
92 | bus_LV_261-509_0_4_node_76 | 0.4 | n |  | TRUE
93 | bus_LV_261-509_0_4_node_43 | 0.4 | n |  | TRUE
94 | bus_LV_261-509_0_4_node_113 | 0.4 | n |  | TRUE
95 | bus_LV_261-509_0_4_node_111 | 0.4 | n |  | TRUE
96 | bus_LV_261-509_0_4_node_41 | 0.4 | n |  | TRUE
97 | bus_LV_261-509_0_4_node_42 | 0.4 | n |  | TRUE
98 | bus_LV_261-509_0_4_node_44 | 0.4 | n |  | TRUE
99 | bus_LV_261-509_0_4_node_45 | 0.4 | n |  | TRUE
100 | bus_LV_261-509_0_4_node_46 | 0.4 | n |  | TRUE
101 | bus_LV_261-509_0_4_node_77 | 0.4 | n |  | TRUE
102 | bus_LV_261-509_0_4_node_48 | 0.4 | n |  | TRUE
103 | bus_LV_261-509_0_4_node_49 | 0.4 | n |  | TRUE
104 | bus_LV_261-509_0_4_node_50 | 0.4 | n |  | TRUE
105 | bus_LV_261-509_0_4_node_51 | 0.4 | n |  | TRUE
106 | bus_LV_261-509_0_4_node_53 | 0.4 | n |  | TRUE
107 | bus_LV_261-509_0_4_node_54 | 0.4 | n |  | TRUE
108 | bus_LV_261-509_0_4_node_56 | 0.4 | n |  | TRUE
109 | bus_LV_261-509_0_4_node_59 | 0.4 | n |  | TRUE
110 | bus_LV_261-509_0_4_node_63 | 0.4 | n |  | TRUE
111 | bus_LV_261-509_0_4_node_122 | 0.4 | n |  | TRUE
112 | bus_LV_261-509_0_4_node_129 | 0.4 | n |  | TRUE
113 | bus_LV_261-509_0_4_node_130 | 0.4 | n |  | TRUE
114 | bus_LV_261-509_0_4_node_94 | 0.4 | n |  | TRUE
115 | bus_LV_261-509_0_4_node_92 | 0.4 | n |  | TRUE
116 | bus_LV_261-509_0_4_node_103 | 0.4 | n |  | TRUE
117 | bus_LV_261-509_0_4_node_109 | 0.4 | n |  | TRUE
118 | bus_LV_261-509_0_4_node_114 | 0.4 | n |  | TRUE
119 | bus_LV_261-509_0_4_node_116 | 0.4 | n |  | TRUE
120 | bus_LV_261-509_0_4_node_131 | 0.4 | n |  | TRUE
121 | bus_MV_524_0_node_166 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-509_0_4_load_0 | 0 | 0.0049029 | 0.0012288 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-509_0_4_load_1 | 1 | 0.0013419 | 0.00033631 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-509_0_4_load_3 | 3 | 0.0016231 | 0.00040679 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-509_0_4_load_4 | 4 | 0.001517 | 0.0003802 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-509_0_4_load_61 | 6 | 0.0014961 | 0.00037497 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-509_0_4_load_132 | 8 | 0.026438 | 0.0066261 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-509_0_4_load_82 | 10 | 0.012289 | 0.0030799 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-509_0_4_load_81 | 11 | 0.011583 | 0.0029029 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-509_0_4_load_86 | 14 | 0.0068453 | 0.0017156 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-509_0_4_load_88 | 19 | 0.0074471 | 0.0018664 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-509_0_4_load_125 | 22 | 0.0032469 | 0.00081375 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-509_0_4_load_124 | 23 | 0.0023017 | 0.00057686 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-509_0_4_load_118 | 26 | 0.0051724 | 0.0012963 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-509_0_4_load_126 | 29 | 0.0030156 | 0.00075579 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-509_0_4_load_72 | 32 | 0.0033121 | 0.00083009 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-509_0_4_load_71 | 33 | 0.0046988 | 0.0011776 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-509_0_4_load_74 | 34 | 0.0059005 | 0.0014788 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_261-509_0_4_load_98 | 36 | 0.0044899 | 0.0011253 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_261-509_0_4_load_95 | 37 | 0.0034929 | 0.00087541 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_261-509_0_4_load_93 | 39 | 0.0034821 | 0.00087271 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_261-509_0_4_load_90 | 41 | 0.0075138 | 0.0018831 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_261-509_0_4_load_52 | 42 | 0.0036875 | 0.00092419 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_261-509_0_4_load_107 | 44 | 0.0022967 | 0.0005756 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_261-509_0_4_load_106 | 45 | 0.0047569 | 0.0011922 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_261-509_0_4_load_112 | 48 | 0.006411 | 0.0016067 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_261-509_0_4_load_101 | 49 | 0.0039185 | 0.00098207 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_261-509_0_4_load_117 | 50 | 0.0044515 | 0.0011157 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_261-509_0_4_load_70 | 53 | 0.011249 | 0.0028193 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_261-509_0_4_load_79 | 54 | 0.015031 | 0.0037671 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_261-509_0_4_load_133 | 56 | 0.0086315 | 0.0021633 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_261-509_0_4_load_47 | 58 | 0.0095299 | 0.0023884 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_261-509_0_4_load_84 | 59 | 0.0087701 | 0.002198 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_261-509_0_4_load_60 | 60 | 0.0051208 | 0.0012834 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_261-509_0_4_load_80 | 61 | 0.013135 | 0.003292 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_261-509_0_4_load_87 | 62 | 0.0075324 | 0.0018878 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_261-509_0_4_load_121 | 63 | 0.0039232 | 0.00098325 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_261-509_0_4_load_55 | 64 | 0.001551 | 0.00038871 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_261-509_0_4_load_89 | 65 | 0.0086467 | 0.0021671 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_261-509_0_4_load_123 | 66 | 0.0024204 | 0.00060661 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_261-509_0_4_load_119 | 67 | 0.0048782 | 0.0012226 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_261-509_0_4_load_120 | 68 | 0.0040669 | 0.0010193 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_261-509_0_4_load_73 | 69 | 0.014316 | 0.003588 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_261-509_0_4_load_83 | 70 | 0.0084736 | 0.0021237 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_261-509_0_4_load_96 | 72 | 0.0044355 | 0.0011116 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_261-509_0_4_load_91 | 73 | 0.0034118 | 0.00085507 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_261-509_0_4_load_100 | 74 | 0.00344 | 0.00086214 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_261-509_0_4_load_97 | 75 | 0.003419 | 0.00085688 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_261-509_0_4_load_68 | 78 | 0.0034896 | 0.00087456 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_261-509_0_4_load_69 | 79 | 0.0021999 | 0.00055134 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_261-509_0_4_load_128 | 80 | 0.00090399 | 0.00022656 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_261-509_0_4_load_127 | 81 | 0.0023819 | 0.00059695 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_261-509_0_4_load_64 | 82 | 0.0028558 | 0.00071574 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_261-509_0_4_load_62 | 83 | 0.0041337 | 0.001036 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_261-509_0_4_load_65 | 84 | 0.0061963 | 0.0015529 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_261-509_0_4_load_110 | 86 | 0.0069145 | 0.0017329 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_261-509_0_4_load_102 | 87 | 0.0049403 | 0.0012382 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_261-509_0_4_load_115 | 88 | 0.0045738 | 0.0011463 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_261-509_0_4_load_108 | 89 | 0.0026428 | 0.00066234 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_261-509_0_4_load_105 | 90 | 0.0047441 | 0.001189 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_261-509_0_4_load_78 | 91 | 0.013294 | 0.0033318 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_261-509_0_4_load_113 | 94 | 0.003926 | 0.00098395 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_261-509_0_4_load_111 | 95 | 0.0032701 | 0.00081957 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_261-509_0_4_load_41 | 96 | 0.02606 | 0.0065312 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_261-509_0_4_load_44 | 98 | 0.01372 | 0.0034386 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_261-509_0_4_load_46 | 100 | 0.0095091 | 0.0023832 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_261-509_0_4_load_77 | 101 | 0.0051662 | 0.0012948 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_261-509_0_4_load_48 | 102 | 0.0027471 | 0.00068849 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_261-509_0_4_load_49 | 103 | 0.0023815 | 0.00059686 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_261-509_0_4_load_51 | 105 | 0.00090359 | 0.00022646 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_261-509_0_4_load_53 | 106 | 0.0024091 | 0.00060378 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_261-509_0_4_load_54 | 107 | 0.0015629 | 0.00039171 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_261-509_0_4_load_59 | 109 | 0.0015666 | 0.00039264 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_261-509_0_4_load_63 | 110 | 0.0015629 | 0.0003917 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_261-509_0_4_load_122 | 111 | 0.0019232 | 0.000482 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_261-509_0_4_load_129 | 112 | 0.0043529 | 0.0010909 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_261-509_0_4_load_130 | 113 | 0.021077 | 0.0052825 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_261-509_0_4_load_94 | 114 | 0.006057 | 0.001518 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_261-509_0_4_load_92 | 115 | 0.0080389 | 0.0020147 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_261-509_0_4_load_103 | 116 | 0.0037983 | 0.00095196 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_261-509_0_4_load_109 | 117 | 0.0076498 | 0.0019172 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_261-509_0_4_load_114 | 118 | 0.005593 | 0.0014017 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_261-509_0_4_load_116 | 119 | 0.0048644 | 0.0012191 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_261-509_0_4_load_131 | 120 | 0.054885 | 0.013755 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 120 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-509_0_4_line_0 |  | 0 | 1 | 0.010568 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-509_0_4_line_1 |  | 0 | 2 | 0.021648 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-509_0_4_line_2 |  | 1 | 3 | 0.0031594 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-509_0_4_line_3 |  | 2 | 4 | 0.014427 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-509_0_4_line_4 |  | 2 | 5 | 0.02948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_261-509_0_4_line_5 |  | 3 | 6 | 0.0071745 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_261-509_0_4_line_6 |  | 4 | 7 | 0.016333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_261-509_0_4_line_7 |  | 5 | 8 | 0.061589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_261-509_0_4_line_8 |  | 6 | 60 | 0.013573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_261-509_0_4_line_9 |  | 7 | 15 | 0.003198 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_261-509_0_4_line_10 |  | 7 | 16 | 0.016567 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_261-509_0_4_line_11 |  | 9 | 10 | 0.01356 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_261-509_0_4_line_12 |  | 9 | 11 | 0.011693 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-509_0_4_line_13 |  | 10 | 13 | 0.023166 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_261-509_0_4_line_14 |  | 11 | 61 | 0.021572 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_261-509_0_4_line_15 |  | 12 | 13 | 0.033187 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
16 | LV_261-509_0_4_line_16 |  | 12 | 14 | 0.014308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
17 | LV_261-509_0_4_line_17 |  | 13 | 20 | 0.04225 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
18 | LV_261-509_0_4_line_18 |  | 14 | 62 | 0.021811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
19 | LV_261-509_0_4_line_19 |  | 15 | 63 | 0.021166 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_261-509_0_4_line_20 |  | 15 | 64 | 0.017133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_261-509_0_4_line_21 |  | 16 | 17 | 0.029402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
22 | LV_261-509_0_4_line_22 |  | 16 | 18 | 0.024403 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_261-509_0_4_line_23 |  | 16 | 19 | 0.020533 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
24 | LV_261-509_0_4_line_24 |  | 17 | 49 | 0.01085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
25 | LV_261-509_0_4_line_25 |  | 18 | 41 | 0.020376 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_261-509_0_4_line_26 |  | 19 | 62 | 0.024428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
27 | LV_261-509_0_4_line_27 |  | 20 | 34 | 0.011228 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
28 | LV_261-509_0_4_line_28 |  | 21 | 22 | 0.019994 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_261-509_0_4_line_29 |  | 21 | 23 | 0.029812 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_261-509_0_4_line_30 |  | 22 | 29 | 0.017742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_261-509_0_4_line_31 |  | 23 | 66 | 0.032169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_261-509_0_4_line_32 |  | 24 | 25 | 0.008282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_261-509_0_4_line_33 |  | 24 | 26 | 0.011482 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_261-509_0_4_line_34 |  | 25 | 50 | 0.019381 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_261-509_0_4_line_35 |  | 25 | 43 | 0.037312 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_261-509_0_4_line_36 |  | 26 | 67 | 0.018711 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_261-509_0_4_line_37 |  | 27 | 28 | 0.00966 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_261-509_0_4_line_38 |  | 27 | 29 | 0.011482 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_261-509_0_4_line_39 |  | 28 | 42 | 0.013771 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_261-509_0_4_line_40 |  | 30 | 31 | 0.085325 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_261-509_0_4_line_41 |  | 30 | 32 | 0.0078943 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_261-509_0_4_line_42 |  | 31 | 33 | 0.046384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_261-509_0_4_line_43 |  | 32 | 69 | 0.024335 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_261-509_0_4_line_44 |  | 33 | 51 | 0.049251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_261-509_0_4_line_45 |  | 34 | 57 | 0.03794 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
46 | LV_261-509_0_4_line_46 |  | 35 | 36 | 0.01896 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_261-509_0_4_line_47 |  | 35 | 37 | 0.0089614 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_261-509_0_4_line_48 |  | 36 | 71 | 0.0034325 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_261-509_0_4_line_49 |  | 37 | 72 | 0.014867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_261-509_0_4_line_50 |  | 38 | 39 | 0.015617 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_261-509_0_4_line_51 |  | 38 | 40 | 0.019004 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_261-509_0_4_line_52 |  | 39 | 73 | 0.02306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_261-509_0_4_line_53 |  | 40 | 74 | 0.013207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_261-509_0_4_line_54 |  | 40 | 75 | 0.012175 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_261-509_0_4_line_55 |  | 41 | 65 | 0.024301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_261-509_0_4_line_56 |  | 43 | 44 | 0.015083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_261-509_0_4_line_57 |  | 43 | 45 | 0.016991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_261-509_0_4_line_58 |  | 45 | 74 | 0.0030475 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_261-509_0_4_line_59 |  | 46 | 47 | 0.11106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_261-509_0_4_line_60 |  | 46 | 48 | 0.037936 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_261-509_0_4_line_61 |  | 47 | 58 | 0.013261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_261-509_0_4_line_62 |  | 47 | 59 | 0.027547 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_261-509_0_4_line_63 |  | 48 | 86 | 0.015966 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_261-509_0_4_line_64 |  | 49 | 87 | 0.016591 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_261-509_0_4_line_65 |  | 50 | 88 | 0.017587 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_261-509_0_4_line_66 |  | 51 | 52 | 0.061564 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_261-509_0_4_line_67 |  | 51 | 53 | 0.013998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_261-509_0_4_line_68 |  | 52 | 54 | 0.014043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_261-509_0_4_line_69 |  | 54 | 91 | 0.010194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_261-509_0_4_line_70 |  | 55 | 56 | 0.028867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_261-509_0_4_line_71 |  | 55 | 57 | 0.024734 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_261-509_0_4_line_72 |  | 57 | 92 | 0.0119 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
73 | LV_261-509_0_4_line_73 |  | 58 | 93 | 0.024244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_261-509_0_4_line_74 |  | 59 | 70 | 0.014622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_261-509_0_4_line_75 |  | 63 | 111 | 0.0073215 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_261-509_0_4_line_76 |  | 64 | 107 | 0.0050232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_261-509_0_4_line_77 |  | 66 | 111 | 0.01057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_261-509_0_4_line_78 |  | 67 | 68 | 0.016551 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_261-509_0_4_line_79 |  | 71 | 90 | 0.015397 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_261-509_0_4_line_80 |  | 71 | 116 | 0.013156 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_261-509_0_4_line_81 |  | 72 | 75 | 0.017968 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_261-509_0_4_line_82 |  | 73 | 115 | 0.016475 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_261-509_0_4_line_83 |  | 76 | 77 | 0.010478 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_261-509_0_4_line_84 |  | 76 | 78 | 0.034013 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_261-509_0_4_line_85 |  | 77 | 79 | 0.012623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_261-509_0_4_line_86 |  | 78 | 85 | 0.0042435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_261-509_0_4_line_87 |  | 79 | 105 | 0.016052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_261-509_0_4_line_88 |  | 80 | 81 | 0.013234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_261-509_0_4_line_89 |  | 81 | 106 | 0.016565 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_261-509_0_4_line_90 |  | 82 | 83 | 0.01355 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_261-509_0_4_line_91 |  | 83 | 110 | 0.02431 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_261-509_0_4_line_92 |  | 84 | 85 | 0.019435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_261-509_0_4_line_93 |  | 85 | 108 | 0.02405 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_261-509_0_4_line_94 |  | 86 | 117 | 0.017457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_261-509_0_4_line_95 |  | 87 | 116 | 0.016356 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_261-509_0_4_line_96 |  | 88 | 118 | 0.018501 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_261-509_0_4_line_97 |  | 89 | 90 | 0.0044402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_261-509_0_4_line_98 |  | 91 | 99 | 0.0049682 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_261-509_0_4_line_99 |  | 92 | 101 | 0.011652 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
100 | LV_261-509_0_4_line_100 |  | 92 | 98 | 0.034957 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
101 | LV_261-509_0_4_line_101 |  | 93 | 100 | 0.041421 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_261-509_0_4_line_102 |  | 93 | 96 | 0.042869 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_261-509_0_4_line_103 |  | 94 | 95 | 0.010249 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_261-509_0_4_line_104 |  | 95 | 117 | 0.030426 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_261-509_0_4_line_105 |  | 96 | 97 | 0.021215 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_261-509_0_4_line_106 |  | 97 | 98 | 0.00015076 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
107 | LV_261-509_0_4_line_107 |  | 97 | 99 | 0.009331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_261-509_0_4_line_108 |  | 101 | 112 | 0.00075554 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
109 | LV_261-509_0_4_line_109 |  | 102 | 103 | 0.0156 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_261-509_0_4_line_110 |  | 102 | 104 | 0.033359 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_261-509_0_4_line_111 |  | 103 | 105 | 0.013326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_261-509_0_4_line_112 |  | 104 | 106 | 0.014029 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_261-509_0_4_line_113 |  | 107 | 108 | 0.014662 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_261-509_0_4_line_114 |  | 108 | 109 | 0.0053655 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_261-509_0_4_line_115 |  | 109 | 110 | 1.5378e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_261-509_0_4_line_116 |  | 112 | 113 | 0.0098054 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
117 | LV_261-509_0_4_line_117 |  | 113 | 120 | 0.00061671 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
118 | LV_261-509_0_4_line_118 |  | 114 | 115 | 0.016517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_261-509_0_4_line_119 |  | 118 | 119 | 0.010068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-509_0_4_trafo_131 | 0.63 MVA 20/0.4 kV | 121 | 120 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2683003.9564 | 1253131.0294 | 2683004.0554 | 1253131.0094 | 2683014.3161 | 1253128.94
1 | 2682982.7371 | 1253135.314 | 2683003.9564 | 1253131.0294
2 | 2683017.4131 | 1253128.3154 | 2683014.3161 | 1253128.94
3 | 2682982.7371 | 1253135.314 | 2682980.6223 | 1253147.8272 | 2682980.1268 | 1253149.4916
4 | 2682982.7371 | 1253135.314 | 2682983.0413 | 1253133.5281 | 2682986.1735 | 1253106.0402
5 | 2683017.4131 | 1253128.3154 | 2683024.446 | 1253126.897
6 | 2682975.4669 | 1253165.1458 | 2682980.1268 | 1253149.4916
7 | 2683026.374 | 1253086.5887 | 2683030.2312 | 1253085.9756 | 2683032.815 | 1253087.9244 | 2683033.5517 | 1253091.8933 | 2683031.3447 | 1253095.365 | 2683027.8173 | 1253096.6721 | 2682986.1735 | 1253106.0402
8 | 2683024.446 | 1253126.897 | 2683037.751 | 1253124.2136
9 | 2682978.5723 | 1253165.9454 | 2682975.4669 | 1253165.1458
10 | 2682962.1366 | 1253165.4037 | 2682967.7659 | 1253167.5731 | 2682969.4289 | 1253163.6045 | 2682975.4669 | 1253165.1458
11 | 2682976.0283 | 1253024.4034 | 2682975.58 | 1253037.9557
12 | 2682976.0283 | 1253024.4034 | 2682974.9902 | 1253012.7562
13 | 2682970.2157 | 1253060.071 | 2682972.9607 | 1253055.3615 | 2682975.2949 | 1253046.5764 | 2682975.58 | 1253037.9557
14 | 2682973.3397 | 1252991.2761 | 2682973.1786 | 1252992.4283 | 2682974.9902 | 1253012.7562
15 | 2682970.2157 | 1253060.071 | 2682978.2593 | 1253060.673 | 2682977.0197 | 1253074.277 | 2682975.6528 | 1253085.6553
16 | 2682975.6528 | 1253085.6553 | 2682973.9445 | 1253099.8611
17 | 2682928.0236 | 1253056.3108 | 2682933.2939 | 1253056.6404 | 2682949.1579 | 1253057.6188 | 2682970.2157 | 1253060.071
18 | 2682973.9445 | 1253099.8611 | 2682971.3405 | 1253121.5156
19 | 2682978.5723 | 1253165.9454 | 2682986.1434 | 1253185.7107 | 2682986.1434 | 1253185.7107
20 | 2682978.5723 | 1253165.9454 | 2682995.5448 | 1253163.6065
21 | 2682948.8272 | 1253191.6371 | 2682962.1366 | 1253165.4037
22 | 2682938.7615 | 1253158.171 | 2682958.4783 | 1253164.2072 | 2682962.1366 | 1253165.4037
23 | 2682962.1366 | 1253165.4037 | 2682967.5533 | 1253145.5986
24 | 2682948.8272 | 1253191.6371 | 2682942.7543 | 1253189.3504 | 2682938.4162 | 1253189.7906
25 | 2682938.7615 | 1253158.171 | 2682942.0814 | 1253138.0668
26 | 2682971.3405 | 1253121.5156 | 2682969.1439 | 1253139.7826 | 2682967.5533 | 1253145.5986
27 | 2682928.0236 | 1253056.3108 | 2682920.6727 | 1253055.285 | 2682917.0318 | 1253054.1752
28 | 2682944.9702 | 1253218.0919 | 2682931.8259 | 1253233.1574
29 | 2682944.9702 | 1253218.0919 | 2682955.59 | 1253226.5469 | 2682967.0729 | 1253228.3313 | 2682971.6857 | 1253228.1498
30 | 2682920.1621 | 1253246.526 | 2682931.8259 | 1253233.1574
31 | 2682971.6857 | 1253228.1498 | 2682975.4085 | 1253228.0033 | 2682981.3529 | 1253223.839 | 2682981.781 | 1253202.6577
32 | 2682835.9963 | 1253241.2292 | 2682828.6242 | 1253237.4121
33 | 2682835.9963 | 1253241.2292 | 2682846.9575 | 1253244.6465
34 | 2682828.6242 | 1253237.4121 | 2682812.2301 | 1253227.0744
35 | 2682828.6242 | 1253237.4121 | 2682839.6076 | 1253215.0377 | 2682833.0013 | 1253212.0431 | 2682833.3672 | 1253206.9222
36 | 2682846.9575 | 1253244.6465 | 2682864.8201 | 1253250.2154
37 | 2682912.6134 | 1253255.178 | 2682912.2269 | 1253260.6878 | 2682915.3199 | 1253263.4443
38 | 2682912.6134 | 1253255.178 | 2682920.1621 | 1253246.526
39 | 2682915.3199 | 1253263.4443 | 2682925.5873 | 1253272.6221
40 | 2682883.2334 | 1252892.0496 | 2682897.5162 | 1252882.0197 | 2682904.4137 | 1252877.1792 | 2682908.2956 | 1252874.2758 | 2682918.9908 | 1252881.7088 | 2682938.2355 | 1252894.043 | 2682947.004 | 1252902.1718 | 2682952.2111 | 1252906.4813
41 | 2682883.2334 | 1252892.0496 | 2682888.1122 | 1252898.2559 | 2682888.1122 | 1252898.2559
42 | 2682952.2111 | 1252906.4813 | 2682913.795 | 1252932.4755
43 | 2682888.1122 | 1252898.2559 | 2682868.377 | 1252912.4932
44 | 2682877.1287 | 1252961.5609 | 2682886.2832 | 1252955.5956 | 2682888.9939 | 1252955.489 | 2682900.6855 | 1252947.2575 | 2682901.6392 | 1252943.8238 | 2682912.4221 | 1252936.3579 | 2682912.3801 | 1252933.4329 | 2682913.795 | 1252932.4755
45 | 2682880.0198 | 1253047.2212 | 2682886.6319 | 1253047.1248 | 2682896.3835 | 1253048.0841 | 2682906.4105 | 1253050.9377 | 2682917.0318 | 1253054.1752
46 | 2682889.5592 | 1253172.2264 | 2682890.4009 | 1253177.8646 | 2682892.105 | 1253191.0142
47 | 2682889.5592 | 1253172.2264 | 2682880.6097 | 1253171.7637
48 | 2682892.5462 | 1253194.4182 | 2682892.105 | 1253191.0142
49 | 2682880.6097 | 1253171.7637 | 2682874.2212 | 1253171.4335 | 2682865.8355 | 1253172.6257
50 | 2682836.1948 | 1253154.7669 | 2682830.3853 | 1253161.1572 | 2682823.4082 | 1253161.3788
51 | 2682835.763 | 1253173.7641 | 2682836.1948 | 1253154.7669
52 | 2682800.5006 | 1253163.6525 | 2682801.9837 | 1253163.6732 | 2682816.2902 | 1253161.6049 | 2682823.4082 | 1253161.3788
53 | 2682835.763 | 1253173.7641 | 2682834.8113 | 1253186.9362
54 | 2682835.763 | 1253173.7641 | 2682847.9382 | 1253173.6881
55 | 2682946.0408 | 1253114.0901 | 2682942.0814 | 1253138.0668
56 | 2682833.3672 | 1253206.9222 | 2682847.0979 | 1253213.1636
57 | 2682833.3672 | 1253206.9222 | 2682834.5917 | 1253189.9758
58 | 2682834.8113 | 1253186.9362 | 2682834.5917 | 1253189.9758
59 | 2682746.3373 | 1253108.0763 | 2682750.8045 | 1253108.0942 | 2682750.9275 | 1253083.6331 | 2682752.4606 | 1253051.1524 | 2682753.2876 | 1253043.814 | 2682754.8212 | 1253038.2979 | 2682768.8993 | 1253031.5339 | 2682771.5204 | 1253036.7522 | 2682764.3359 | 1253040.5547 | 2682759.304 | 1253045.2991
60 | 2682746.3373 | 1253108.0763 | 2682746.3709 | 1253112.6913 | 2682746.2431 | 1253146.0117
61 | 2682759.304 | 1253045.2991 | 2682772.5608 | 1253045.6193
62 | 2682759.304 | 1253045.2991 | 2682755.9356 | 1253052.513 | 2682755.1694 | 1253060.8975 | 2682755.2281 | 1253072.0637
63 | 2682746.1819 | 1253161.9774 | 2682746.2431 | 1253146.0117
64 | 2682938.4162 | 1253189.7906 | 2682921.9098 | 1253191.4655
65 | 2682797.3538 | 1253217.6937 | 2682812.2301 | 1253227.0744
66 | 2682841.5984 | 1252998.8698 | 2682838.1757 | 1252994.3074 | 2682860.6857 | 1252979.8335 | 2682875.2277 | 1252969.5959 | 2682880.0155 | 1252966.1269 | 2682877.1287 | 1252961.5609
67 | 2682877.1287 | 1252961.5609 | 2682875.1713 | 1252962.8456 | 2682864.7033 | 1252967.9746
68 | 2682841.5984 | 1252998.8698 | 2682843.0503 | 1253000.8138 | 2682845.7004 | 1253006.1104 | 2682847.9895 | 1253011.3241
69 | 2682848.1716 | 1253021.5163 | 2682847.9895 | 1253011.3241 | 2682847.9895 | 1253011.3241
70 | 2682881.2179 | 1253022.5528 | 2682903.4084 | 1253022.2741 | 2682903.5102 | 1253029.014
71 | 2682880.0198 | 1253047.2212 | 2682879.9772 | 1253034.6334 | 2682881.2179 | 1253022.5528
72 | 2682870.7164 | 1253054.6745 | 2682878.3034 | 1253048.5427 | 2682880.0198 | 1253047.2212
73 | 2682791.2215 | 1253059.0665 | 2682788.3076 | 1253055.9011 | 2682781.1296 | 1253047.3611 | 2682774.603 | 1253045.6687 | 2682772.5608 | 1253045.6193
74 | 2682755.3049 | 1253086.685 | 2682755.2281 | 1253072.0637
75 | 2682986.1434 | 1253185.7107 | 2682983.0137 | 1253192.3296
76 | 2683000.5209 | 1253162.9208 | 2682995.5448 | 1253163.6065
77 | 2682981.781 | 1253202.6577 | 2682981.944 | 1253194.5919 | 2682983.0137 | 1253192.3296
78 | 2682864.8201 | 1253250.2154 | 2682880.6208 | 1253255.1414
79 | 2682892.5462 | 1253194.4182 | 2682893.8223 | 1253209.7621
80 | 2682892.5462 | 1253194.4182 | 2682900.1934 | 1253193.6691 | 2682905.6372 | 1253193.1167
81 | 2682865.8355 | 1253172.6257 | 2682858.8415 | 1253173.62 | 2682847.9382 | 1253173.6881
82 | 2682800.5006 | 1253163.6525 | 2682784.0271 | 1253163.4221
83 | 2683046.6998 | 1253226.223 | 2683040.9747 | 1253217.4362
84 | 2683040.9747 | 1253217.4362 | 2683038.1898 | 1253213.1606 | 2683025.2605 | 1253187.3029
85 | 2683046.6998 | 1253226.223 | 2683036.6445 | 1253233.8545
86 | 2683023.5824 | 1253183.4113 | 2683024.4046 | 1253185.5911 | 2683025.2605 | 1253187.3029
87 | 2683036.6445 | 1253233.8545 | 2683032.3145 | 1253237.1407 | 2683023.9813 | 1253241.6051 | 2683022.8698 | 1253241.9457
88 | 2683026.8949 | 1253276.3452 | 2683039.8115 | 1253273.4651
89 | 2683010.727 | 1253279.9501 | 2683026.8949 | 1253276.3452
90 | 2683057.5305 | 1253152.8658 | 2683044.2171 | 1253155.3895
91 | 2683020.3328 | 1253159.917 | 2683044.2171 | 1253155.3895
92 | 2683023.5824 | 1253183.4113 | 2683042.6964 | 1253179.8952
93 | 2683015.046 | 1253160.9192 | 2683023.5824 | 1253183.4113
94 | 2682746.1635 | 1253179.4342 | 2682746.1569 | 1253168.4969 | 2682746.1819 | 1253161.9774
95 | 2682921.9098 | 1253191.4655 | 2682905.6372 | 1253193.1167
96 | 2682781.7044 | 1253207.8257 | 2682797.3538 | 1253217.6937
97 | 2682894.1903 | 1253214.1869 | 2682893.8223 | 1253209.7621
98 | 2682848.2604 | 1253026.4837 | 2682848.1716 | 1253021.5163
99 | 2682870.7164 | 1253054.6745 | 2682871.0757 | 1253058.6603 | 2682873.669 | 1253065.8575
100 | 2682870.7164 | 1253054.6745 | 2682867.0937 | 1253053.0893 | 2682859.6269 | 1253050.0937 | 2682849.8685 | 1253048.545 | 2682847.8855 | 1253044.6477 | 2682848.348 | 1253039.6393 | 2682848.3269 | 1253035.9646
101 | 2682791.2215 | 1253059.0665 | 2682785.6997 | 1253075.1013 | 2682782.2972 | 1253099.3276
102 | 2682791.2215 | 1253059.0665 | 2682799.4218 | 1253055.4784 | 2682811.9013 | 1253052.406 | 2682825.8497 | 1253051.6782 | 2682832.7692 | 1253050.096
103 | 2682746.2063 | 1253220.1095 | 2682746.1858 | 1253216.6446 | 2682746.1817 | 1253209.8605
104 | 2682746.1635 | 1253179.4342 | 2682746.1817 | 1253209.8605
105 | 2682848.326 | 1253035.8139 | 2682841.4802 | 1253040.7552 | 2682832.7692 | 1253050.096
106 | 2682848.326 | 1253035.8139 | 2682848.3269 | 1253035.9646
107 | 2682848.2604 | 1253026.4837 | 2682848.326 | 1253035.8139
108 | 2682873.669 | 1253065.8575 | 2682874.0877 | 1253066.4865
109 | 2682995.2124 | 1253250.4198 | 2683010.1281 | 1253245.8497
110 | 2682997.0346 | 1253283.0031 | 2682993.2987 | 1253269.5852 | 2682995.3502 | 1253261.5857 | 2682995.4534 | 1253255.3046 | 2682995.2124 | 1253250.4198
111 | 2683010.1281 | 1253245.8497 | 2683022.8698 | 1253241.9457
112 | 2682997.0346 | 1253283.0031 | 2683010.727 | 1253279.9501
113 | 2683015.046 | 1253160.9192 | 2683000.5209 | 1253162.9208
114 | 2683015.046 | 1253160.9192 | 2683020.3177 | 1253159.9199
115 | 2683020.3177 | 1253159.9199 | 2683020.3328 | 1253159.917
116 | 2682879.5209 | 1253074.6489 | 2682874.0877 | 1253066.4865
117 | 2682879.5209 | 1253074.6489 | 2682879.8626 | 1253075.1622
118 | 2682784.0271 | 1253163.4221 | 2682767.5121 | 1253163.1912
119 | 2682773.1883 | 1253202.4556 | 2682781.7044 | 1253207.8257

## bus_geodata
| x | y | coords
0 | 2683003.9564 | 1253131.0294
1 | 2683014.3161 | 1253128.94
2 | 2682982.7371 | 1253135.314
3 | 2683017.4131 | 1253128.3154
4 | 2682980.1268 | 1253149.4916
5 | 2682986.1735 | 1253106.0402
6 | 2683024.446 | 1253126.897
7 | 2682975.4669 | 1253165.1458
8 | 2683026.374 | 1253086.5887
9 | 2682976.0283 | 1253024.4034
10 | 2682975.58 | 1253037.9557
11 | 2682974.9902 | 1253012.7562
12 | 2682975.6528 | 1253085.6553
13 | 2682970.2157 | 1253060.071
14 | 2682973.9445 | 1253099.8611
15 | 2682978.5723 | 1253165.9454
16 | 2682962.1366 | 1253165.4037
17 | 2682948.8272 | 1253191.6371
18 | 2682938.7615 | 1253158.171
19 | 2682967.5533 | 1253145.5986
20 | 2682928.0236 | 1253056.3108
21 | 2682944.9702 | 1253218.0919
22 | 2682931.8259 | 1253233.1574
23 | 2682971.6857 | 1253228.1498
24 | 2682835.9963 | 1253241.2292
25 | 2682828.6242 | 1253237.4121
26 | 2682846.9575 | 1253244.6465
27 | 2682912.6134 | 1253255.178
28 | 2682915.3199 | 1253263.4443
29 | 2682920.1621 | 1253246.526
30 | 2682883.2334 | 1252892.0496
31 | 2682952.2111 | 1252906.4813
32 | 2682888.1122 | 1252898.2559
33 | 2682913.795 | 1252932.4755
34 | 2682917.0318 | 1253054.1752
35 | 2682889.5592 | 1253172.2264
36 | 2682892.105 | 1253191.0142
37 | 2682880.6097 | 1253171.7637
38 | 2682836.1948 | 1253154.7669
39 | 2682823.4082 | 1253161.3788
40 | 2682835.763 | 1253173.7641
41 | 2682942.0814 | 1253138.0668
42 | 2682925.5873 | 1253272.6221
43 | 2682833.3672 | 1253206.9222
44 | 2682847.0979 | 1253213.1636
45 | 2682834.5917 | 1253189.9758
46 | 2682746.3373 | 1253108.0763
47 | 2682759.304 | 1253045.2991
48 | 2682746.2431 | 1253146.0117
49 | 2682938.4162 | 1253189.7906
50 | 2682812.2301 | 1253227.0744
51 | 2682877.1287 | 1252961.5609
52 | 2682841.5984 | 1252998.8698
53 | 2682864.7033 | 1252967.9746
54 | 2682847.9895 | 1253011.3241
55 | 2682881.2179 | 1253022.5528
56 | 2682903.5102 | 1253029.014
57 | 2682880.0198 | 1253047.2212
58 | 2682772.5608 | 1253045.6193
59 | 2682755.2281 | 1253072.0637
60 | 2683037.751 | 1253124.2136
61 | 2682973.3397 | 1252991.2761
62 | 2682971.3405 | 1253121.5156
63 | 2682986.1434 | 1253185.7107
64 | 2682995.5448 | 1253163.6065
65 | 2682946.0408 | 1253114.0901
66 | 2682981.781 | 1253202.6577
67 | 2682864.8201 | 1253250.2154
68 | 2682880.6208 | 1253255.1414
69 | 2682868.377 | 1252912.4932
70 | 2682755.3049 | 1253086.685
71 | 2682892.5462 | 1253194.4182
72 | 2682865.8355 | 1253172.6257
73 | 2682800.5006 | 1253163.6525
74 | 2682834.8113 | 1253186.9362
75 | 2682847.9382 | 1253173.6881
76 | 2683040.9747 | 1253217.4362
77 | 2683046.6998 | 1253226.223
78 | 2683025.2605 | 1253187.3029
79 | 2683036.6445 | 1253233.8545
80 | 2683039.8115 | 1253273.4651
81 | 2683026.8949 | 1253276.3452
82 | 2683057.5305 | 1253152.8658
83 | 2683044.2171 | 1253155.3895
84 | 2683042.6964 | 1253179.8952
85 | 2683023.5824 | 1253183.4113
86 | 2682746.1819 | 1253161.9774
87 | 2682921.9098 | 1253191.4655
88 | 2682797.3538 | 1253217.6937
89 | 2682894.1903 | 1253214.1869
90 | 2682893.8223 | 1253209.7621
91 | 2682848.1716 | 1253021.5163
92 | 2682870.7164 | 1253054.6745
93 | 2682791.2215 | 1253059.0665
94 | 2682746.2063 | 1253220.1095
95 | 2682746.1817 | 1253209.8605
96 | 2682832.7692 | 1253050.096
97 | 2682848.326 | 1253035.8139
98 | 2682848.3269 | 1253035.9646
99 | 2682848.2604 | 1253026.4837
100 | 2682782.2972 | 1253099.3276
101 | 2682873.669 | 1253065.8575
102 | 2682995.2124 | 1253250.4198
103 | 2683010.1281 | 1253245.8497
104 | 2682997.0346 | 1253283.0031
105 | 2683022.8698 | 1253241.9457
106 | 2683010.727 | 1253279.9501
107 | 2683000.5209 | 1253162.9208
108 | 2683015.046 | 1253160.9192
109 | 2683020.3177 | 1253159.9199
110 | 2683020.3328 | 1253159.917
111 | 2682983.0137 | 1253192.3296
112 | 2682874.0877 | 1253066.4865
113 | 2682879.5209 | 1253074.6489
114 | 2682767.5121 | 1253163.1912
115 | 2682784.0271 | 1253163.4221
116 | 2682905.6372 | 1253193.1167
117 | 2682746.1635 | 1253179.4342
118 | 2682781.7044 | 1253207.8257
119 | 2682773.1883 | 1253202.4556
120 | 2682879.8626 | 1253075.1622
121 | 2682870.7164 | 1253054.6745

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98178 | -0.34963 | 0.0049029 | 0.0012288
1 | 0.98169 | -0.35146 | 0.0013419 | 0.00033631
2 | 0.98207 | -0.34396 | 0 | 0
3 | 0.98166 | -0.35193 | 0.0016231 | 0.00040679
4 | 0.98261 | -0.33329 | 0.001517 | 0.0003802
5 | 0.98135 | -0.35806 | 0 | 0
6 | 0.98162 | -0.35279 | 0.0014961 | 0.00037497
7 | 0.98326 | -0.32079 | 0 | 0
8 | 0.97984 | -0.38757 | 0.026438 | 0.0066261
9 | 0.98979 | -0.1946 | 0 | 0
10 | 0.9901 | -0.18864 | 0.012289 | 0.0030799
11 | 0.98953 | -0.19974 | 0.011583 | 0.0029029
12 | 0.98905 | -0.20864 | 0 | 0
13 | 0.99089 | -0.17341 | 0 | 0
14 | 0.98826 | -0.22387 | 0.0068453 | 0.0017156
15 | 0.98309 | -0.3241 | 0 | 0
16 | 0.98478 | -0.29102 | 0 | 0
17 | 0.98409 | -0.30437 | 0 | 0
18 | 0.98442 | -0.29811 | 0 | 0
19 | 0.98582 | -0.27102 | 0.0074471 | 0.0018664
20 | 0.99358 | -0.12183 | 0 | 0
21 | 0.98179 | -0.34941 | 0 | 0
22 | 0.98161 | -0.35301 | 0.0032469 | 0.00081375
23 | 0.98207 | -0.34405 | 0.0023017 | 0.00057686
24 | 0.97195 | -0.54188 | 0 | 0
25 | 0.97206 | -0.53972 | 0 | 0
26 | 0.9718 | -0.54487 | 0.0051724 | 0.0012963
27 | 0.98146 | -0.35593 | 0 | 0
28 | 0.98143 | -0.35658 | 0 | 0
29 | 0.9815 | -0.35516 | 0.0030156 | 0.00075579
30 | 0.98951 | -0.20152 | 0 | 0
31 | 0.99089 | -0.17478 | 0 | 0
32 | 0.98939 | -0.204 | 0.0033121 | 0.00083009
33 | 0.99164 | -0.16027 | 0.0046988 | 0.0011776
34 | 0.9943 | -0.10817 | 0.0059005 | 0.0014788
35 | 0.97799 | -0.42306 | 0 | 0
36 | 0.97934 | -0.39668 | 0.0044899 | 0.0011253
37 | 0.97735 | -0.43555 | 0.0034929 | 0.00087541
38 | 0.97408 | -0.49975 | 0 | 0
39 | 0.97378 | -0.50578 | 0.0034821 | 0.00087271
40 | 0.97445 | -0.49243 | 0 | 0
41 | 0.98412 | -0.30403 | 0.0075138 | 0.0018831
42 | 0.98138 | -0.35749 | 0.0036875 | 0.00092419
43 | 0.97323 | -0.51662 | 0 | 0
44 | 0.97319 | -0.51726 | 0.0022967 | 0.0005756
45 | 0.97379 | -0.5054 | 0.0047569 | 0.0011922
46 | 0.98729 | -0.24444 | 0 | 0
47 | 0.99016 | -0.18865 | 0 | 0
48 | 0.9863 | -0.26357 | 0.006411 | 0.0016067
49 | 0.98358 | -0.31423 | 0.0039185 | 0.00098207
50 | 0.9717 | -0.54669 | 0.0044515 | 0.0011157
51 | 0.99265 | -0.14079 | 0 | 0
52 | 0.99454 | -0.10429 | 0 | 0
53 | 0.9925 | -0.14358 | 0.011249 | 0.0028193
54 | 0.99497 | -0.095983 | 0.015031 | 0.0037671
55 | 0.99658 | -0.064921 | 0 | 0
56 | 0.99635 | -0.069295 | 0.0086315 | 0.0021633
57 | 0.99677 | -0.061174 | 0 | 0
58 | 0.99072 | -0.17795 | 0.0095299 | 0.0023884
59 | 0.98973 | -0.1971 | 0.0087701 | 0.002198
60 | 0.98155 | -0.35405 | 0.0051208 | 0.0012834
61 | 0.98927 | -0.20479 | 0.013135 | 0.003292
62 | 0.98709 | -0.24647 | 0.0075324 | 0.0018878
63 | 0.98269 | -0.33193 | 0.0039232 | 0.00098325
64 | 0.9825 | -0.33549 | 0.001551 | 0.00038871
65 | 0.98392 | -0.30782 | 0.0086467 | 0.0021671
66 | 0.98243 | -0.33693 | 0.0024204 | 0.00060661
67 | 0.97164 | -0.54796 | 0.0048782 | 0.0012226
68 | 0.97158 | -0.5492 | 0.0040669 | 0.0010193
69 | 0.98907 | -0.2102 | 0.014316 | 0.003588
70 | 0.98961 | -0.1993 | 0.0084736 | 0.0021237
71 | 0.9796 | -0.39163 | 0 | 0
72 | 0.97634 | -0.45536 | 0.0044355 | 0.0011116
73 | 0.9734 | -0.5132 | 0.0034118 | 0.00085507
74 | 0.97391 | -0.50312 | 0.00344 | 0.00086214
75 | 0.97519 | -0.47789 | 0.003419 | 0.00085688
76 | 0.98085 | -0.36783 | 0 | 0
77 | 0.98072 | -0.37047 | 0 | 0
78 | 0.98129 | -0.35925 | 0.0034896 | 0.00087456
79 | 0.98055 | -0.37366 | 0.0021999 | 0.00055134
80 | 0.97981 | -0.38818 | 0.00090399 | 0.00022656
81 | 0.97982 | -0.38797 | 0.0023819 | 0.00059695
82 | 0.98164 | -0.35239 | 0.0028558 | 0.00071574
83 | 0.98167 | -0.35169 | 0.0041337 | 0.001036
84 | 0.98125 | -0.36009 | 0.0061963 | 0.0015529
85 | 0.98136 | -0.35791 | 0 | 0
86 | 0.98598 | -0.2698 | 0.0069145 | 0.0017329
87 | 0.98208 | -0.34329 | 0.0049403 | 0.0012382
88 | 0.97146 | -0.55157 | 0.0045738 | 0.0011463
89 | 0.97948 | -0.39391 | 0.0026428 | 0.00066234
90 | 0.97949 | -0.3937 | 0.0047441 | 0.001189
91 | 0.99543 | -0.087261 | 0.013294 | 0.0033318
92 | 0.99757 | -0.046033 | 0 | 0
93 | 0.99194 | -0.15432 | 0 | 0
94 | 0.98551 | -0.2791 | 0.003926 | 0.00098395
95 | 0.98554 | -0.27838 | 0.0032701 | 0.00081957
96 | 0.99447 | -0.10549 | 0.02606 | 0.0065312
97 | 0.99623 | -0.071702 | 0 | 0
98 | 0.99624 | -0.0715 | 0.01372 | 0.0034386
99 | 0.99571 | -0.081852 | 0 | 0
100 | 0.99158 | -0.1613 | 0.0095091 | 0.0023832
101 | 0.9988 | -0.022769 | 0.0051662 | 0.0012948
102 | 0.98012 | -0.38208 | 0.0027471 | 0.00068849
103 | 0.98025 | -0.37969 | 0.0023815 | 0.00059686
104 | 0.97995 | -0.38553 | 0 | 0
105 | 0.98038 | -0.37707 | 0.00090359 | 0.00022646
106 | 0.97987 | -0.38698 | 0.0024091 | 0.00060378
107 | 0.98234 | -0.33869 | 0.0015629 | 0.00039171
108 | 0.98188 | -0.34763 | 0 | 0
109 | 0.98183 | -0.34861 | 0.0015666 | 0.00039264
110 | 0.98183 | -0.34862 | 0.0015629 | 0.0003917
111 | 0.98257 | -0.33413 | 0.0019232 | 0.000482
112 | 0.99888 | -0.021245 | 0.0043529 | 0.0010909
113 | 0.99993 | -0.0013091 | 0.021077 | 0.0052825
114 | 0.97309 | -0.51932 | 0.006057 | 0.001518
115 | 0.97318 | -0.51748 | 0.0080389 | 0.0020147
116 | 0.98068 | -0.37055 | 0.0037983 | 0.00095196
117 | 0.98574 | -0.27445 | 0.0076498 | 0.0019172
118 | 0.97128 | -0.55515 | 0.005593 | 0.0014017
119 | 0.97123 | -0.55605 | 0.0048644 | 0.0012191
120 | 1 | 0 | -0.49503 | -0.12609
121 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0095836 | 0.0024021 | -0.0095828 | -0.0024017 | 8.3616e-07 | 4.0151e-07 | 0.014525 | 0.014525 | 0.014525 | 0.98178 | -0.34963 | 0.98169 | -0.35146 | 3.9905
1 | -0.014486 | -0.0036308 | 0.01449 | 0.0036331 | 3.9134e-06 | 2.2308e-06 | 0.021956 | 0.021956 | 0.021956 | 0.98178 | -0.34963 | 0.98207 | -0.34396 | 6.0319
2 | 0.0082408 | 0.0020653 | -0.0082407 | -0.0020653 | 1.8486e-07 | 7.8368e-08 | 0.012491 | 0.012491 | 0.012491 | 0.98169 | -0.35146 | 0.98166 | -0.35193 | 3.4317
3 | -0.040984 | -0.010293 | 0.041005 | 0.010306 | 2.0868e-05 | 1.3173e-05 | 0.062106 | 0.062106 | 0.062106 | 0.98207 | -0.34396 | 0.98261 | -0.33329 | 17.0621
4 | 0.026494 | 0.0066602 | -0.026476 | -0.0066492 | 1.7821e-05 | 1.1033e-05 | 0.04015 | 0.04015 | 0.04015 | 0.98207 | -0.34396 | 0.98135 | -0.35806 | 11.0302
5 | 0.0066176 | 0.0016585 | -0.0066173 | -0.0016584 | 2.7071e-07 | 8.2556e-08 | 0.010031 | 0.010031 | 0.010031 | 0.98166 | -0.35193 | 0.98162 | -0.35279 | 2.7558
6 | -0.042522 | -0.010687 | 0.042547 | 0.010703 | 2.5405e-05 | 1.6052e-05 | 0.064403 | 0.064403 | 0.064403 | 0.98261 | -0.33329 | 0.98326 | -0.32079 | 17.6932
7 | 0.026476 | 0.0066492 | -0.026438 | -0.0066261 | 3.7231e-05 | 2.3051e-05 | 0.04015 | 0.04015 | 0.04015 | 0.98135 | -0.35806 | 0.97984 | -0.38757 | 11.0303
8 | 0.0051212 | 0.0012834 | -0.0051208 | -0.0012834 | 3.0674e-07 | 2.4745e-08 | 0.007763 | 0.0077631 | 0.0077631 | 0.98162 | -0.35279 | 0.98155 | -0.35405 | 2.1327
9 | 0.057465 | 0.014435 | -0.057456 | -0.014429 | 9.0721e-06 | 5.7656e-06 | 0.086976 | 0.086976 | 0.086976 | 0.98326 | -0.32079 | 0.98309 | -0.3241 | 23.8945
10 | -0.10001 | -0.025138 | 0.10015 | 0.025228 | 0.00014237 | 9.0906e-05 | 0.15138 | 0.15138 | 0.15138 | 0.98326 | -0.32079 | 0.98478 | -0.29102 | 41.5877
11 | -0.024727 | -0.0062004 | 0.024734 | 0.0062047 | 7.0271e-06 | 4.323e-06 | 0.037175 | 0.037175 | 0.037175 | 0.98979 | -0.1946 | 0.9901 | -0.18864 | 10.2129
12 | 0.024727 | 0.0062004 | -0.024721 | -0.0061966 | 6.0599e-06 | 3.7281e-06 | 0.037175 | 0.037175 | 0.037175 | 0.98979 | -0.1946 | 0.98953 | -0.19974 | 10.2129
13 | -0.037023 | -0.0092845 | 0.03705 | 0.0093015 | 2.6898e-05 | 1.6916e-05 | 0.055643 | 0.055643 | 0.055643 | 0.9901 | -0.18864 | 0.99089 | -0.17341 | 15.2867
14 | 0.013138 | 0.0032938 | -0.013135 | -0.003292 | 3.1578e-06 | 1.744e-06 | 0.019757 | 0.019758 | 0.019758 | 0.98953 | -0.19974 | 0.98927 | -0.20479 | 5.4279
15 | -0.24096 | -0.061228 | 0.24137 | 0.061488 | 0.00040956 | 0.00026041 | 0.36282 | 0.36282 | 0.36282 | 0.98905 | -0.20864 | 0.99089 | -0.17341 | 24.919
16 | 0.24096 | 0.061228 | -0.24078 | -0.061116 | 0.00017658 | 0.00011228 | 0.36282 | 0.36282 | 0.36282 | 0.98905 | -0.20864 | 0.98826 | -0.22387 | 24.919
17 | -0.27842 | -0.07079 | 0.27911 | 0.071231 | 0.0006936 | 0.00044172 | 0.41846 | 0.41846 | 0.41846 | 0.99089 | -0.17341 | 0.99358 | -0.12183 | 28.7406
18 | 0.23394 | 0.0594 | -0.23368 | -0.059238 | 0.00025409 | 0.0001615 | 0.35251 | 0.35251 | 0.35251 | 0.98826 | -0.22387 | 0.98709 | -0.24647 | 24.2111
19 | 0.020539 | 0.0051536 | -0.020532 | -0.005149 | 7.6725e-06 | 4.6421e-06 | 0.031091 | 0.031091 | 0.031091 | 0.98309 | -0.3241 | 0.98269 | -0.33193 | 8.5415
20 | 0.036916 | 0.0092754 | -0.036896 | -0.0092628 | 2.0066e-05 | 1.2625e-05 | 0.055885 | 0.055885 | 0.055885 | 0.98309 | -0.3241 | 0.9825 | -0.33549 | 15.3531
21 | 0.1019 | 0.025897 | -0.10184 | -0.025856 | 6.5459e-05 | 4.0399e-05 | 0.1541 | 0.1541 | 0.1541 | 0.98478 | -0.29102 | 0.98409 | -0.30437 | 10.584
22 | 0.016172 | 0.0040567 | -0.016167 | -0.0040536 | 5.465e-06 | 3.1872e-06 | 0.024437 | 0.024438 | 0.024438 | 0.98478 | -0.29102 | 0.98442 | -0.29811 | 6.7136
23 | -0.21823 | -0.055182 | 0.21844 | 0.055315 | 0.00020952 | 0.00013305 | 0.32992 | 0.32992 | 0.32992 | 0.98478 | -0.29102 | 0.98582 | -0.27102 | 22.6593
24 | 0.10184 | 0.025856 | -0.10179 | -0.025826 | 4.831e-05 | 3.0643e-05 | 0.1541 | 0.1541 | 0.1541 | 0.98409 | -0.30437 | 0.98358 | -0.31423 | 21.1681
25 | 0.016167 | 0.0040536 | -0.016162 | -0.0040509 | 4.5633e-06 | 2.6615e-06 | 0.024438 | 0.024438 | 0.024438 | 0.98442 | -0.29811 | 0.98412 | -0.30403 | 6.7136
26 | -0.22588 | -0.057181 | 0.22615 | 0.057351 | 0.00026655 | 0.00016934 | 0.34116 | 0.34116 | 0.34116 | 0.98582 | -0.27102 | 0.98709 | -0.24647 | 23.4313
27 | -0.27911 | -0.071231 | 0.2793 | 0.071349 | 0.00018433 | 0.00011739 | 0.41846 | 0.41846 | 0.41846 | 0.99358 | -0.12183 | 0.9943 | -0.10817 | 28.7405
28 | 0.0099529 | 0.0024946 | -0.0099512 | -0.0024938 | 1.7061e-06 | 8.3911e-07 | 0.015085 | 0.015085 | 0.015085 | 0.98179 | -0.34941 | 0.98161 | -0.35301 | 4.1442
29 | -0.0099529 | -0.0024946 | 0.0099554 | 0.0024958 | 2.5438e-06 | 1.251e-06 | 0.015085 | 0.015085 | 0.015085 | 0.98179 | -0.34941 | 0.98207 | -0.34405 | 4.1442
30 | 0.0067043 | 0.00168 | -0.0067036 | -0.0016798 | 6.8717e-07 | 2.1554e-07 | 0.010163 | 0.010163 | 0.010163 | 0.98161 | -0.35301 | 0.9815 | -0.35516 | 2.792
31 | -0.012257 | -0.0030727 | 0.012261 | 0.003075 | 4.161e-06 | 2.2558e-06 | 0.018572 | 0.018572 | 0.018572 | 0.98207 | -0.34405 | 0.98243 | -0.33693 | 5.1022
32 | -0.014121 | -0.0035399 | 0.014123 | 0.0035407 | 1.4516e-06 | 8.2637e-07 | 0.021619 | 0.021619 | 0.021619 | 0.97195 | -0.54188 | 0.97206 | -0.53972 | 5.9393
33 | 0.014121 | 0.0035399 | -0.014119 | -0.0035387 | 2.0124e-06 | 1.1457e-06 | 0.021619 | 0.021619 | 0.021619 | 0.97195 | -0.54188 | 0.9718 | -0.54487 | 5.9394
34 | 0.019495 | 0.0048897 | -0.019488 | -0.0048858 | 6.4732e-06 | 3.9027e-06 | 0.029844 | 0.029844 | 0.029844 | 0.97206 | -0.53972 | 0.9717 | -0.54669 | 8.1988
35 | -0.033617 | -0.0084304 | 0.033654 | 0.0084536 | 3.7057e-05 | 2.3253e-05 | 0.051463 | 0.051463 | 0.051463 | 0.97206 | -0.53972 | 0.97323 | -0.51662 | 14.1381
36 | 0.0089467 | 0.0022424 | -0.0089453 | -0.0022418 | 1.3168e-06 | 6.1096e-07 | 0.013699 | 0.013699 | 0.013699 | 0.9718 | -0.54487 | 0.97164 | -0.54796 | 3.7635
37 | 0.0036878 | 0.00092406 | -0.0036877 | -0.00092411 | 1.1324e-07 | -4.9597e-08 | 0.0055911 | 0.0055912 | 0.0055912 | 0.98146 | -0.35593 | 0.98143 | -0.35658 | 1.536
38 | -0.0036878 | -0.00092406 | 0.003688 | 0.00092401 | 1.346e-07 | -5.8965e-08 | 0.0055911 | 0.0055911 | 0.0055911 | 0.98146 | -0.35593 | 0.9815 | -0.35516 | 1.536
39 | 0.0036877 | 0.00092411 | -0.0036875 | -0.00092419 | 1.6144e-07 | -7.069e-08 | 0.0055912 | 0.0055912 | 0.0055912 | 0.98143 | -0.35658 | 0.98138 | -0.35749 | 1.5361
40 | -0.017635 | -0.0044218 | 0.017657 | 0.0044351 | 2.2503e-05 | 1.3304e-05 | 0.02652 | 0.026519 | 0.02652 | 0.98951 | -0.20152 | 0.99089 | -0.17478 | 7.2857
41 | 0.017635 | 0.0044218 | -0.017633 | -0.0044205 | 2.082e-06 | 1.2311e-06 | 0.02652 | 0.02652 | 0.02652 | 0.98951 | -0.20152 | 0.98939 | -0.204 | 7.2857
42 | -0.017657 | -0.0044351 | 0.01767 | 0.0044423 | 1.2233e-05 | 7.231e-06 | 0.026519 | 0.026519 | 0.026519 | 0.99089 | -0.17478 | 0.99164 | -0.16027 | 7.2856
43 | 0.014321 | 0.0035904 | -0.014316 | -0.003588 | 4.2334e-06 | 2.397e-06 | 0.021539 | 0.021539 | 0.021539 | 0.98939 | -0.204 | 0.98907 | -0.2102 | 5.9172
44 | -0.022368 | -0.0056199 | 0.022389 | 0.0056326 | 2.0813e-05 | 1.2685e-05 | 0.03357 | 0.03357 | 0.03357 | 0.99164 | -0.16027 | 0.99265 | -0.14079 | 9.2225
45 | -0.2852 | -0.072828 | 0.28585 | 0.073241 | 0.00064941 | 0.00041365 | 0.42729 | 0.42729 | 0.42729 | 0.9943 | -0.10817 | 0.99677 | -0.061174 | 29.347
46 | -0.076789 | -0.01938 | 0.076886 | 0.019442 | 9.7136e-05 | 6.1929e-05 | 0.11688 | 0.11688 | 0.11688 | 0.97799 | -0.42306 | 0.97934 | -0.39668 | 32.1108
47 | 0.076789 | 0.01938 | -0.076743 | -0.019351 | 4.5911e-05 | 2.927e-05 | 0.11688 | 0.11688 | 0.11688 | 0.97799 | -0.42306 | 0.97735 | -0.43555 | 32.1108
48 | -0.081376 | -0.020567 | 0.081396 | 0.02058 | 1.9698e-05 | 1.2563e-05 | 0.12371 | 0.12371 | 0.12371 | 0.97934 | -0.39668 | 0.9796 | -0.39163 | 33.9849
49 | 0.07325 | 0.018475 | -0.073181 | -0.018431 | 6.9393e-05 | 4.4226e-05 | 0.11157 | 0.11157 | 0.11157 | 0.97735 | -0.43555 | 0.97634 | -0.45536 | 30.6499
50 | 0.021005 | 0.0052696 | -0.020999 | -0.005266 | 6.0307e-06 | 3.6653e-06 | 0.03209 | 0.03209 | 0.03209 | 0.97408 | -0.49975 | 0.97378 | -0.50578 | 8.8159
51 | -0.021005 | -0.0052696 | 0.021013 | 0.0052741 | 7.3386e-06 | 4.46e-06 | 0.03209 | 0.03209 | 0.03209 | 0.97408 | -0.49975 | 0.97445 | -0.49243 | 8.8159
52 | 0.017517 | 0.0043933 | -0.017511 | -0.0043896 | 6.1966e-06 | 3.6791e-06 | 0.026769 | 0.026769 | 0.026769 | 0.97378 | -0.50578 | 0.9734 | -0.5132 | 7.3541
53 | 0.044194 | 0.011113 | -0.044172 | -0.011098 | 2.2564e-05 | 1.4276e-05 | 0.067499 | 0.067499 | 0.067499 | 0.97445 | -0.49243 | 0.97391 | -0.50312 | 18.5436
54 | -0.065207 | -0.016387 | 0.065252 | 0.016416 | 4.5283e-05 | 2.8829e-05 | 0.099589 | 0.099589 | 0.099589 | 0.97445 | -0.49243 | 0.97519 | -0.47789 | 27.3595
55 | 0.0086483 | 0.0021678 | -0.0086467 | -0.0021671 | 1.5583e-06 | 6.8861e-07 | 0.013077 | 0.013077 | 0.013077 | 0.98412 | -0.30403 | 0.98392 | -0.30782 | 3.5925
56 | 0.0022968 | 0.00057546 | -0.0022967 | -0.0005756 | 6.9746e-08 | -1.4278e-07 | 0.0035116 | 0.0035116 | 0.0035116 | 0.97323 | -0.51662 | 0.97319 | -0.51726 | 0.96474
57 | -0.035951 | -0.0090291 | 0.03597 | 0.0090412 | 1.9256e-05 | 1.2112e-05 | 0.054974 | 0.054974 | 0.054974 | 0.97323 | -0.51662 | 0.97379 | -0.5054 | 15.1028
58 | -0.040727 | -0.010233 | 0.040732 | 0.010236 | 4.4275e-06 | 2.7957e-06 | 0.062243 | 0.062243 | 0.062243 | 0.97379 | -0.5054 | 0.97391 | -0.50312 | 17.0997
59 | -0.028208 | -0.0070826 | 0.028284 | 0.0071294 | 7.5293e-05 | 4.6763e-05 | 0.04252 | 0.042519 | 0.04252 | 0.98729 | -0.24444 | 0.99016 | -0.18865 | 11.6812
60 | 0.028208 | 0.0070826 | -0.028183 | -0.0070667 | 2.5719e-05 | 1.5976e-05 | 0.04252 | 0.04252 | 0.04252 | 0.98729 | -0.24444 | 0.9863 | -0.26357 | 11.6813
61 | -0.045535 | -0.011456 | 0.045558 | 0.01147 | 2.3296e-05 | 1.4739e-05 | 0.068446 | 0.068446 | 0.068446 | 0.99016 | -0.18865 | 0.99072 | -0.17795 | 18.8037
62 | 0.017252 | 0.0043262 | -0.017245 | -0.0043221 | 6.9439e-06 | 4.0899e-06 | 0.025926 | 0.025927 | 0.025927 | 0.99016 | -0.18865 | 0.98973 | -0.1971 | 7.1227
63 | 0.021772 | 0.0054599 | -0.021765 | -0.005456 | 6.46e-06 | 3.9307e-06 | 0.032848 | 0.032848 | 0.032848 | 0.9863 | -0.26357 | 0.98598 | -0.2698 | 9.0241
64 | 0.09787 | 0.024844 | -0.097733 | -0.024756 | 0.0001366 | 8.7216e-05 | 0.14818 | 0.14818 | 0.14818 | 0.98358 | -0.31423 | 0.98208 | -0.34329 | 40.7076
65 | 0.015037 | 0.0037701 | -0.015033 | -0.0037681 | 3.497e-06 | 2.0203e-06 | 0.023027 | 0.023027 | 0.023027 | 0.9717 | -0.54669 | 0.97146 | -0.55157 | 6.3261
66 | -0.03364 | -0.0084527 | 0.033698 | 0.0084894 | 5.8724e-05 | 3.6786e-05 | 0.050435 | 0.050435 | 0.050435 | 0.99265 | -0.14079 | 0.99454 | -0.10429 | 13.8557
67 | 0.011251 | 0.0028201 | -0.011249 | -0.0028193 | 1.4931e-06 | 7.7466e-07 | 0.016865 | 0.016865 | 0.016865 | 0.99265 | -0.14079 | 0.9925 | -0.14358 | 4.6333
68 | -0.033698 | -0.0084894 | 0.033712 | 0.0084978 | 1.3395e-05 | 8.3906e-06 | 0.050435 | 0.050435 | 0.050435 | 0.99454 | -0.10429 | 0.99497 | -0.095983 | 13.8557
69 | -0.048743 | -0.012265 | 0.048763 | 0.012278 | 2.0323e-05 | 1.2874e-05 | 0.072914 | 0.072913 | 0.072914 | 0.99497 | -0.095983 | 0.99543 | -0.087261 | 20.0312
70 | 0.0086333 | 0.002164 | -0.0086315 | -0.0021633 | 1.7988e-06 | 7.7521e-07 | 0.012891 | 0.012891 | 0.012891 | 0.99658 | -0.064921 | 0.99635 | -0.069295 | 3.5414
71 | -0.0086333 | -0.002164 | 0.0086348 | 0.0021647 | 1.5413e-06 | 6.6406e-07 | 0.012891 | 0.012891 | 0.012891 | 0.99658 | -0.064921 | 0.99677 | -0.061174 | 3.5414
72 | -0.29448 | -0.075406 | 0.2947 | 0.075544 | 0.00021616 | 0.00013772 | 0.44018 | 0.44018 | 0.44018 | 0.99677 | -0.061174 | 0.99757 | -0.046033 | 30.2323
73 | -0.055088 | -0.013859 | 0.055151 | 0.013898 | 6.2267e-05 | 3.9538e-05 | 0.082759 | 0.082759 | 0.082759 | 0.99072 | -0.17795 | 0.99194 | -0.15432 | 22.736
74 | 0.0084745 | 0.0021241 | -0.0084736 | -0.0021237 | 8.9011e-07 | 3.8179e-07 | 0.012741 | 0.012741 | 0.012741 | 0.98973 | -0.1971 | 0.98961 | -0.1993 | 3.5003
75 | 0.016609 | 0.0041657 | -0.016607 | -0.0041647 | 1.7367e-06 | 1.0187e-06 | 0.02515 | 0.02515 | 0.02515 | 0.98269 | -0.33193 | 0.98257 | -0.33413 | 6.9095
76 | 0.035345 | 0.0088741 | -0.03534 | -0.0088707 | 5.3989e-06 | 3.3917e-06 | 0.053536 | 0.053536 | 0.053536 | 0.9825 | -0.33549 | 0.98234 | -0.33869 | 14.7077
77 | -0.014682 | -0.0036816 | 0.014684 | 0.0036827 | 1.9602e-06 | 1.1206e-06 | 0.022238 | 0.022238 | 0.022238 | 0.98243 | -0.33693 | 0.98257 | -0.33413 | 6.1093
78 | 0.0040671 | 0.0010192 | -0.0040669 | -0.0010193 | 2.4079e-07 | -5.0876e-08 | 0.0062286 | 0.0062287 | 0.0062287 | 0.97164 | -0.54796 | 0.97158 | -0.5492 | 1.7112
79 | 0.0073876 | 0.0018516 | -0.0073869 | -0.0018513 | 7.271e-07 | 2.7153e-07 | 0.011222 | 0.011222 | 0.011222 | 0.9796 | -0.39163 | 0.97949 | -0.3937 | 3.0829
80 | -0.088783 | -0.022431 | 0.088873 | 0.022489 | 8.9813e-05 | 5.7315e-05 | 0.13493 | 0.13493 | 0.13493 | 0.9796 | -0.39163 | 0.98068 | -0.37055 | 37.0679
81 | 0.068745 | 0.01732 | -0.068671 | -0.017272 | 7.4011e-05 | 4.7142e-05 | 0.10481 | 0.10481 | 0.10481 | 0.97634 | -0.45536 | 0.97519 | -0.47789 | 28.7927
82 | 0.014099 | 0.0035345 | -0.014096 | -0.0035329 | 2.8701e-06 | 1.6321e-06 | 0.021554 | 0.021554 | 0.021554 | 0.9734 | -0.5132 | 0.97318 | -0.51748 | 5.9213
83 | 0.013937 | 0.0034948 | -0.013935 | -0.0034938 | 1.7566e-06 | 9.9197e-07 | 0.021143 | 0.021144 | 0.021144 | 0.98085 | -0.36783 | 0.98072 | -0.37047 | 5.8087
84 | -0.013937 | -0.0034948 | 0.013942 | 0.003498 | 5.7019e-06 | 3.2197e-06 | 0.021143 | 0.021143 | 0.021143 | 0.98085 | -0.36783 | 0.98129 | -0.35925 | 5.8087
85 | 0.013935 | 0.0034938 | -0.013933 | -0.0034926 | 2.1162e-06 | 1.1951e-06 | 0.021144 | 0.021144 | 0.021144 | 0.98072 | -0.37047 | 0.98055 | -0.37366 | 5.8087
86 | -0.017432 | -0.0043725 | 0.017433 | 0.0043732 | 1.112e-06 | 6.5808e-07 | 0.026435 | 0.026435 | 0.026435 | 0.98129 | -0.35925 | 0.98136 | -0.35791 | 7.2623
87 | 0.011733 | 0.0029412 | -0.011731 | -0.0029402 | 1.9083e-06 | 1.0189e-06 | 0.017805 | 0.017805 | 0.017805 | 0.98055 | -0.37366 | 0.98038 | -0.37707 | 4.8916
88 | -0.00090399 | -0.00022656 | 0.000904 | 0.0002264 | 9.353e-09 | -1.6069e-07 | 0.0013729 | 0.0013728 | 0.0013729 | 0.97981 | -0.38818 | 0.97982 | -0.38797 | 0.37716
89 | -0.0032859 | -0.00082335 | 0.003286 | 0.00082324 | 1.5468e-07 | -1.0966e-07 | 0.00499 | 0.00499 | 0.00499 | 0.97982 | -0.38797 | 0.97987 | -0.38698 | 1.3709
90 | -0.0028558 | -0.00071574 | 0.0028559 | 0.00071563 | 9.5225e-08 | -1.1037e-07 | 0.004329 | 0.0043289 | 0.004329 | 0.98164 | -0.35239 | 0.98167 | -0.35169 | 1.1893
91 | -0.0069897 | -0.0017516 | 0.0069907 | 0.001752 | 1.0233e-06 | 3.475e-07 | 0.010595 | 0.010595 | 0.010595 | 0.98167 | -0.35169 | 0.98183 | -0.34862 | 2.9107
92 | -0.0061963 | -0.0015529 | 0.0061969 | 0.0015531 | 6.4347e-07 | 1.663e-07 | 0.0093964 | 0.0093963 | 0.0093964 | 0.98125 | -0.36009 | 0.98136 | -0.35791 | 2.5814
93 | -0.02363 | -0.0059263 | 0.023642 | 0.0059334 | 1.1579e-05 | 7.1065e-06 | 0.035831 | 0.035831 | 0.035831 | 0.98136 | -0.35791 | 0.98188 | -0.34763 | 9.8437
94 | 0.014851 | 0.003723 | -0.014847 | -0.0037212 | 3.2884e-06 | 1.882e-06 | 0.022413 | 0.022413 | 0.022413 | 0.98598 | -0.2698 | 0.98574 | -0.27445 | 6.1573
95 | 0.092793 | 0.023518 | -0.092671 | -0.023441 | 0.00012141 | 7.7493e-05 | 0.14069 | 0.14069 | 0.14069 | 0.98208 | -0.34329 | 0.98068 | -0.37055 | 38.6512
96 | 0.010459 | 0.0026218 | -0.010458 | -0.0026209 | 1.7808e-06 | 9.1069e-07 | 0.016021 | 0.016021 | 0.016021 | 0.97146 | -0.55157 | 0.97128 | -0.55515 | 4.4014
97 | -0.0026428 | -0.00066234 | 0.0026428 | 0.0006623 | 2.6839e-08 | -3.871e-08 | 0.0040149 | 0.0040148 | 0.0040149 | 0.97948 | -0.39391 | 0.97949 | -0.3937 | 1.103
98 | -0.062057 | -0.01561 | 0.062073 | 0.01562 | 1.604e-05 | 1.0201e-05 | 0.092786 | 0.092786 | 0.092786 | 0.99543 | -0.087261 | 0.99571 | -0.081852 | 25.4907
99 | -0.46175 | -0.11776 | 0.46227 | 0.11809 | 0.0005193 | 0.00033174 | 0.68948 | 0.68948 | 0.68948 | 0.99757 | -0.046033 | 0.9988 | -0.022769 | 47.3544
100 | 0.16705 | 0.042211 | -0.16685 | -0.042083 | 0.00020368 | 0.00012853 | 0.2493 | 0.2493 | 0.2493 | 0.99757 | -0.046033 | 0.99624 | -0.0715 | 17.1223
101 | 0.0095123 | 0.0023847 | -0.0095091 | -0.0023832 | 3.1629e-06 | 1.4898e-06 | 0.01427 | 0.01427 | 0.01427 | 0.99194 | -0.15432 | 0.99158 | -0.1613 | 3.9203
102 | -0.064663 | -0.016283 | 0.064814 | 0.016379 | 0.00015135 | 9.6306e-05 | 0.097029 | 0.097028 | 0.097029 | 0.99194 | -0.15432 | 0.99447 | -0.10549 | 26.6562
103 | -0.003926 | -0.00098395 | 0.0039261 | 0.0009839 | 1.3506e-07 | -4.4161e-08 | 0.0059279 | 0.0059278 | 0.0059279 | 0.98551 | -0.2791 | 0.98554 | -0.27838 | 1.6285
104 | -0.0071962 | -0.0018035 | 0.0071976 | 0.0018039 | 1.3469e-06 | 4.7425e-07 | 0.010865 | 0.010865 | 0.010865 | 0.98554 | -0.27838 | 0.98574 | -0.27445 | 2.9849
105 | -0.090874 | -0.02291 | 0.091021 | 0.023004 | 0.00014719 | 9.3929e-05 | 0.13602 | 0.13602 | 0.13602 | 0.99447 | -0.10549 | 0.99623 | -0.071702 | 37.3685
106 | -0.15312 | -0.038643 | 0.15313 | 0.038644 | 1.4799e-06 | 9.4319e-07 | 0.22881 | 0.22881 | 0.22881 | 0.99623 | -0.071702 | 0.99624 | -0.0715 | 31.4296
107 | 0.062103 | 0.015639 | -0.062073 | -0.01562 | 3.0125e-05 | 1.9159e-05 | 0.092786 | 0.092786 | 0.092786 | 0.99623 | -0.071702 | 0.99571 | -0.081852 | 25.4907
108 | -0.46743 | -0.11938 | 0.46747 | 0.1194 | 3.4428e-05 | 2.1995e-05 | 0.69718 | 0.69718 | 0.69718 | 0.9988 | -0.022769 | 0.99888 | -0.021245 | 47.883
109 | -0.0084436 | -0.0021158 | 0.0084445 | 0.0021162 | 9.6129e-07 | 4.1859e-07 | 0.012819 | 0.012819 | 0.012819 | 0.98012 | -0.38208 | 0.98025 | -0.37969 | 3.5217
110 | 0.0056965 | 0.0014273 | -0.0056955 | -0.0014271 | 9.3564e-07 | 1.7846e-07 | 0.0086482 | 0.0086483 | 0.0086483 | 0.98012 | -0.38208 | 0.97995 | -0.38553 | 2.3759
111 | -0.010826 | -0.002713 | 0.010827 | 0.0027137 | 1.3496e-06 | 6.9576e-07 | 0.016434 | 0.016434 | 0.016434 | 0.98025 | -0.37969 | 0.98038 | -0.37707 | 4.5148
112 | 0.0056955 | 0.0014271 | -0.0056951 | -0.001427 | 3.9347e-07 | 7.5098e-08 | 0.0086483 | 0.0086484 | 0.0086484 | 0.97995 | -0.38553 | 0.97987 | -0.38698 | 2.3759
113 | 0.033777 | 0.008479 | -0.033762 | -0.00847 | 1.4396e-05 | 9.028e-06 | 0.051169 | 0.051169 | 0.051169 | 0.98234 | -0.33869 | 0.98188 | -0.34763 | 14.0574
114 | 0.010121 | 0.0025366 | -0.01012 | -0.0025363 | 4.7333e-07 | 2.3507e-07 | 0.015338 | 0.015338 | 0.015338 | 0.98188 | -0.34763 | 0.98183 | -0.34861 | 4.2137
115 | 0.0085536 | 0.0021437 | -0.0085536 | -0.0021437 | 9.7506e-10 | 4.2729e-10 | 0.012963 | 0.012963 | 0.012963 | 0.98183 | -0.34861 | 0.98183 | -0.34862 | 3.5614
116 | -0.47182 | -0.12049 | 0.47228 | 0.12079 | 0.00045516 | 0.00029079 | 0.70366 | 0.70366 | 0.70366 | 0.99888 | -0.021245 | 0.99993 | -0.0013091 | 48.3284
117 | -0.49335 | -0.12607 | 0.49338 | 0.12609 | 3.1236e-05 | 1.9959e-05 | 0.73503 | 0.73503 | 0.73503 | 0.99993 | -0.0013091 | 1 | 0 | 50.4826
118 | -0.006057 | -0.001518 | 0.0060575 | 0.0015182 | 5.3134e-07 | 1.3486e-07 | 0.0092622 | 0.0092621 | 0.0092622 | 0.97309 | -0.51932 | 0.97318 | -0.51748 | 2.5445
119 | 0.0048646 | 0.0012191 | -0.0048644 | -0.0012191 | 2.097e-07 | 9.6079e-09 | 0.0074526 | 0.0074527 | 0.0074527 | 0.97128 | -0.55515 | 0.97123 | -0.55605 | 2.0474

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.54992 | 0.13984

## res_load
| p_mw | q_mvar
0 | 0.0049029 | 0.0012288
1 | 0.0013419 | 0.00033631
2 | 0.0016231 | 0.00040679
3 | 0.001517 | 0.0003802
4 | 0.0014961 | 0.00037497
5 | 0.026438 | 0.0066261
6 | 0.012289 | 0.0030799
7 | 0.011583 | 0.0029029
8 | 0.0068453 | 0.0017156
9 | 0.0074471 | 0.0018664
10 | 0.0032469 | 0.00081375
11 | 0.0023017 | 0.00057686
12 | 0.0051724 | 0.0012963
13 | 0.0030156 | 0.00075579
14 | 0.0033121 | 0.00083009
15 | 0.0046988 | 0.0011776
16 | 0.0059005 | 0.0014788
17 | 0.0044899 | 0.0011253
18 | 0.0034929 | 0.00087541
19 | 0.0034821 | 0.00087271
20 | 0.0075138 | 0.0018831
21 | 0.0036875 | 0.00092419
22 | 0.0022967 | 0.0005756
23 | 0.0047569 | 0.0011922
24 | 0.006411 | 0.0016067
25 | 0.0039185 | 0.00098207
26 | 0.0044515 | 0.0011157
27 | 0.011249 | 0.0028193
28 | 0.015031 | 0.0037671
29 | 0.0086315 | 0.0021633
30 | 0.0095299 | 0.0023884
31 | 0.0087701 | 0.002198
32 | 0.0051208 | 0.0012834
33 | 0.013135 | 0.003292
34 | 0.0075324 | 0.0018878
35 | 0.0039232 | 0.00098325
36 | 0.001551 | 0.00038871
37 | 0.0086467 | 0.0021671
38 | 0.0024204 | 0.00060661
39 | 0.0048782 | 0.0012226
40 | 0.0040669 | 0.0010193
41 | 0.014316 | 0.003588
42 | 0.0084736 | 0.0021237
43 | 0.0044355 | 0.0011116
44 | 0.0034118 | 0.00085507
45 | 0.00344 | 0.00086214
46 | 0.003419 | 0.00085688
47 | 0.0034896 | 0.00087456
48 | 0.0021999 | 0.00055134
49 | 0.00090399 | 0.00022656
50 | 0.0023819 | 0.00059695
51 | 0.0028558 | 0.00071574
52 | 0.0041337 | 0.001036
53 | 0.0061963 | 0.0015529
54 | 0.0069145 | 0.0017329
55 | 0.0049403 | 0.0012382
56 | 0.0045738 | 0.0011463
57 | 0.0026428 | 0.00066234
58 | 0.0047441 | 0.001189
59 | 0.013294 | 0.0033318
60 | 0.003926 | 0.00098395
61 | 0.0032701 | 0.00081957
62 | 0.02606 | 0.0065312
63 | 0.01372 | 0.0034386
64 | 0.0095091 | 0.0023832
65 | 0.0051662 | 0.0012948
66 | 0.0027471 | 0.00068849
67 | 0.0023815 | 0.00059686
68 | 0.00090359 | 0.00022646
69 | 0.0024091 | 0.00060378
70 | 0.0015629 | 0.00039171
71 | 0.0015666 | 0.00039264
72 | 0.0015629 | 0.0003917
73 | 0.0019232 | 0.000482
74 | 0.0043529 | 0.0010909
75 | 0.021077 | 0.0052825
76 | 0.006057 | 0.001518
77 | 0.0080389 | 0.0020147
78 | 0.0037983 | 0.00095196
79 | 0.0076498 | 0.0019172
80 | 0.005593 | 0.0014017
81 | 0.0048644 | 0.0012191
82 | 0.054885 | 0.013755

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1