## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-510_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-510_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-510_0_4_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_261-510_0_4_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_261-510_0_4_node_33 | 0.4 | n |  | TRUE
5 | bus_LV_261-510_0_4_node_7 | 0.4 | n |  | TRUE
6 | bus_LV_261-510_0_4_node_25 | 0.4 | n |  | TRUE
7 | bus_LV_261-510_0_4_node_6 | 0.4 | n |  | TRUE
8 | bus_LV_261-510_0_4_node_22 | 0.4 | n |  | TRUE
9 | bus_LV_261-510_0_4_node_31 | 0.4 | n |  | TRUE
10 | bus_LV_261-510_0_4_node_10 | 0.4 | n |  | TRUE
11 | bus_LV_261-510_0_4_node_13 | 0.4 | n |  | TRUE
12 | bus_LV_261-510_0_4_node_28 | 0.4 | n |  | TRUE
13 | bus_LV_261-510_0_4_node_11 | 0.4 | n |  | TRUE
14 | bus_LV_261-510_0_4_node_12 | 0.4 | n |  | TRUE
15 | bus_LV_261-510_0_4_node_15 | 0.4 | n |  | TRUE
16 | bus_LV_261-510_0_4_node_18 | 0.4 | n |  | TRUE
17 | bus_LV_261-510_0_4_node_27 | 0.4 | n |  | TRUE
18 | bus_LV_261-510_0_4_node_32 | 0.4 | n |  | TRUE
19 | bus_LV_261-510_0_4_node_34 | 0.4 | n |  | TRUE
20 | bus_LV_261-510_0_4_node_24 | 0.4 | n |  | TRUE
21 | bus_LV_261-510_0_4_node_36 | 0.4 | n |  | TRUE
22 | bus_LV_261-510_0_4_node_35 | 0.4 | n |  | TRUE
23 | bus_LV_261-510_0_4_node_29 | 0.4 | n |  | TRUE
24 | bus_LV_261-510_0_4_node_16 | 0.4 | n |  | TRUE
25 | bus_LV_261-510_0_4_node_19 | 0.4 | n |  | TRUE
26 | bus_LV_261-510_0_4_node_23 | 0.4 | n |  | TRUE
27 | bus_LV_261-510_0_4_node_17 | 0.4 | n |  | TRUE
28 | bus_LV_261-510_0_4_node_20 | 0.4 | n |  | TRUE
29 | bus_LV_261-510_0_4_node_21 | 0.4 | n |  | TRUE
30 | bus_LV_261-510_0_4_node_37 | 0.4 | n |  | TRUE
31 | bus_LV_261-510_0_4_node_26 | 0.4 | n |  | TRUE
32 | bus_LV_261-510_0_4_node_30 | 0.4 | n |  | TRUE
33 | bus_MV_524_0_node_61 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-510_0_4_load_0 | 0 | 0.014212 | 0.0035618 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-510_0_4_load_33 | 4 | 0.0043796 | 0.0010976 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-510_0_4_load_25 | 6 | 0.081236 | 0.02036 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-510_0_4_load_22 | 8 | 0.0067041 | 0.0016802 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-510_0_4_load_31 | 9 | 0.029168 | 0.0073102 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-510_0_4_load_28 | 12 | 0.0018408 | 0.00046135 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-510_0_4_load_15 | 15 | 0.006169 | 0.0015461 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-510_0_4_load_27 | 17 | 0.00097782 | 0.00024506 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-510_0_4_load_32 | 18 | 0.0089489 | 0.0022428 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-510_0_4_load_34 | 19 | 0.0043768 | 0.0010969 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-510_0_4_load_24 | 20 | 0.029991 | 0.0075164 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-510_0_4_load_36 | 21 | 0.0043796 | 0.0010976 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-510_0_4_load_35 | 22 | 0.0043768 | 0.0010969 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-510_0_4_load_23 | 26 | 0.0073017 | 0.00183 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-510_0_4_load_21 | 29 | 0.0030459 | 0.00076337 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-510_0_4_load_37 | 30 | 0.076547 | 0.019184 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-510_0_4_load_30 | 32 | 0.057526 | 0.014417 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 20 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-510_0_4_line_0 |  | 0 | 1 | 0.01099 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-510_0_4_line_1 |  | 1 | 2 | 0.093846 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-510_0_4_line_2 |  | 1 | 3 | 0.13582 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-510_0_4_line_3 |  | 2 | 4 | 0.035825 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-510_0_4_line_4 |  | 3 | 5 | 0.026234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
5 | LV_261-510_0_4_line_5 |  | 3 | 6 | 0.034578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
6 | LV_261-510_0_4_line_6 |  | 4 | 19 | 0.0063316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_261-510_0_4_line_7 |  | 5 | 9 | 0.037878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
8 | LV_261-510_0_4_line_8 |  | 5 | 7 | 0.088771 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_261-510_0_4_line_9 |  | 6 | 20 | 0.050018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
10 | LV_261-510_0_4_line_10 |  | 7 | 8 | 0.019346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_261-510_0_4_line_11 |  | 9 | 11 | 0.091715 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
12 | LV_261-510_0_4_line_12 |  | 10 | 11 | 0.097249 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-510_0_4_line_13 |  | 10 | 12 | 0.0086266 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_261-510_0_4_line_14 |  | 11 | 18 | 0.040803 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_261-510_0_4_line_15 |  | 12 | 23 | 0.093652 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_261-510_0_4_line_16 |  | 13 | 14 | 0.0088725 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_261-510_0_4_line_17 |  | 13 | 15 | 0.014558 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_261-510_0_4_line_18 |  | 14 | 16 | 0.013539 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
19 | LV_261-510_0_4_line_19 |  | 14 | 17 | 0.014108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
20 | LV_261-510_0_4_line_20 |  | 16 | 29 | 0.015925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
21 | LV_261-510_0_4_line_21 |  | 17 | 31 | 0.046875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
22 | LV_261-510_0_4_line_22 |  | 19 | 22 | 0.0063299 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_261-510_0_4_line_23 |  | 20 | 31 | 0.00062737 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
24 | LV_261-510_0_4_line_24 |  | 21 | 22 | 0.0063316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_261-510_0_4_line_25 |  | 23 | 32 | 0.059342 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_261-510_0_4_line_26 |  | 24 | 25 | 0.13166 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
27 | LV_261-510_0_4_line_27 |  | 24 | 26 | 0.0040843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
28 | LV_261-510_0_4_line_28 |  | 25 | 30 | 0.19827 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_261-510_0_4_line_29 |  | 26 | 27 | 0.017502 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
30 | LV_261-510_0_4_line_30 |  | 27 | 28 | 0.124 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
31 | LV_261-510_0_4_line_31 |  | 28 | 29 | 0.035071 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-510_0_4_trafo_24 | 0.63 MVA 20/0.4 kV | 33 | 20 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17
0 | 2682888.9369 | 1252409.6787 | 2682899.7301 | 1252411.7502
1 | 2682867.6117 | 1252383.5608 | 2682872.0859 | 1252361.0065 | 2682897.703 | 1252365.7461 | 2682892.3643 | 1252391.8243 | 2682889.9463 | 1252403.8884 | 2682888.9369 | 1252409.6787
2 | 2682888.9369 | 1252409.6787 | 2682889.9463 | 1252403.8884 | 2682892.3643 | 1252391.8243 | 2682897.703 | 1252365.7461 | 2682907.4645 | 1252367.6953 | 2682937.3803 | 1252373.7407 | 2682970.0664 | 1252382.9829 | 2682973.9113 | 1252384.36 | 2682976.1085 | 1252386.4479 | 2682976.6104 | 1252389.4127 | 2682983.0605 | 1252389.0694
3 | 2682867.6117 | 1252383.5608 | 2682859.4369 | 1252382.0231 | 2682844.8818 | 1252379.6067 | 2682832.3426 | 1252377.2842
4 | 2682983.0605 | 1252389.0694 | 2682987.9321 | 1252388.8153 | 2682987.828 | 1252383.8545 | 2682988.599 | 1252381.6192 | 2682990.5402 | 1252379.8895 | 2682992.1868 | 1252378.7228 | 2682992.4123 | 1252373.9446 | 2682992.628 | 1252369.322
5 | 2682983.0605 | 1252389.0694 | 2682983.914 | 1252399.2557 | 2682985.7402 | 1252423.5429
6 | 2682832.3426 | 1252377.2842 | 2682826.1169 | 1252376.1311
7 | 2682992.628 | 1252369.322 | 2683008.5508 | 1252371.0796 | 2683030.243 | 1252373.7726
8 | 2682992.628 | 1252369.322 | 2682989.3486 | 1252368.5199 | 2682986.9885 | 1252366.2073 | 2682986.1152 | 1252362.8259 | 2682985.6228 | 1252356.492 | 2682982.3479 | 1252313.3583 | 2683011.2091 | 1252310.6605
9 | 2682985.7402 | 1252423.5429 | 2682989.4905 | 1252473.4205
10 | 2683011.2091 | 1252310.6605 | 2683030.4232 | 1252308.4015
11 | 2683121.2793 | 1252384.9035 | 2683110.6915 | 1252383.7542 | 2683081.5568 | 1252380.1429 | 2683030.243 | 1252373.7726
12 | 2683119.2126 | 1252393.4143 | 2683132.1072 | 1252394.7517 | 2683163.8074 | 1252398.3881 | 2683164.3709 | 1252394.2707 | 2683164.9508 | 1252390.0646 | 2683121.2793 | 1252384.9035
13 | 2683119.2126 | 1252393.4143 | 2683119.3261 | 1252395.0059 | 2683121.8058 | 1252401.5851
14 | 2683121.2793 | 1252384.9035 | 2683112.6366 | 1252363.4662 | 2683106.33 | 1252346.94
15 | 2683158.4813 | 1252486.902 | 2683155.993 | 1252476.526 | 2683154.9705 | 1252469.2617 | 2683153.5299 | 1252462.7477 | 2683146.0746 | 1252449.2219 | 2683135.7032 | 1252428.9055 | 2683132.3753 | 1252421.8869 | 2683124.0702 | 1252407.593 | 2683121.8058 | 1252401.5851
16 | 2682988.1526 | 1252534.6277 | 2682982.9287 | 1252534.7213 | 2682982.9606 | 1252538.3689
17 | 2682982.9606 | 1252538.3689 | 2682980.4399 | 1252537.8332 | 2682968.4607 | 1252538.0457
18 | 2682988.1526 | 1252534.6277 | 2682989.6621 | 1252548.0811
19 | 2682988.1526 | 1252534.6277 | 2682987.0752 | 1252520.5613
20 | 2682989.6621 | 1252548.0811 | 2682994.3532 | 1252548.3137 | 2683005.5772 | 1252548.01
21 | 2682989.5375 | 1252474.0461 | 2682990.9328 | 1252487.042 | 2682987.3017 | 1252511.8765 | 2682986.883 | 1252518.053 | 2682987.0752 | 1252520.5613
22 | 2682826.1169 | 1252376.1311 | 2682819.8928 | 1252374.9783
23 | 2682989.5375 | 1252474.0461 | 2682989.4905 | 1252473.4205
24 | 2682819.8928 | 1252374.9783 | 2682813.6671 | 1252373.8252
25 | 2683112.9912 | 1252497.3605 | 2683156.5427 | 1252502.4087 | 2683158.4813 | 1252486.902
26 | 2683135.6979 | 1252574.9484 | 2683139.3433 | 1252573.8654 | 2683147.321 | 1252571.6757 | 2683177.2343 | 1252565.4575 | 2683178.0094 | 1252568.8376 | 2683199.0789 | 1252564.6747 | 2683221.5583 | 1252561.1433 | 2683246.6813 | 1252558.0049 | 2683262.6711 | 1252557.1067
27 | 2683135.6979 | 1252574.9484 | 2683131.7846 | 1252576.1177
28 | 2683066.3537 | 1252531.5211 | 2683109.3853 | 1252537.5735 | 2683122.8959 | 1252538.0189 | 2683135.3513 | 1252537.2819 | 2683150.3243 | 1252537.848 | 2683202.9137 | 1252544.7358 | 2683238.3134 | 1252549.8257 | 2683247.6604 | 1252551.1691 | 2683254.205 | 1252553.2293 | 2683262.6711 | 1252557.1067
29 | 2683115.7136 | 1252582.9963 | 2683121.0647 | 1252580.2916 | 2683131.1128 | 1252576.3184 | 2683131.7846 | 1252576.1177
30 | 2683028.5195 | 1252560.6349 | 2683057.239 | 1252558.2689 | 2683071.4432 | 1252554.9989 | 2683078.2247 | 1252554.6938 | 2683090.8566 | 1252556.4389 | 2683096.4345 | 1252559.0857 | 2683100.1936 | 1252565.4877 | 2683104.1827 | 1252572.7157 | 2683105.1595 | 1252575.7095 | 2683105.017 | 1252578.8765 | 2683103.6533 | 1252581.9375 | 2683101.6403 | 1252584.4778 | 2683098.0554 | 1252587.7077 | 2683100.7929 | 1252591.082 | 2683105.9537 | 1252587.4183 | 2683110.9493 | 1252584.7641 | 2683112.7569 | 1252584.4893 | 2683115.7136 | 1252582.9963
31 | 2683028.5195 | 1252560.6349 | 2683027.3765 | 1252547.4201 | 2683005.5772 | 1252548.01

## bus_geodata
| x | y | coords
0 | 2682899.7301 | 1252411.7502
1 | 2682888.9369 | 1252409.6787
2 | 2682867.6117 | 1252383.5608
3 | 2682983.0605 | 1252389.0694
4 | 2682832.3426 | 1252377.2842
5 | 2682992.628 | 1252369.322
6 | 2682985.7402 | 1252423.5429
7 | 2683011.2091 | 1252310.6605
8 | 2683030.4232 | 1252308.4015
9 | 2683030.243 | 1252373.7726
10 | 2683119.2126 | 1252393.4143
11 | 2683121.2793 | 1252384.9035
12 | 2683121.8058 | 1252401.5851
13 | 2682982.9606 | 1252538.3689
14 | 2682988.1526 | 1252534.6277
15 | 2682968.4607 | 1252538.0457
16 | 2682989.6621 | 1252548.0811
17 | 2682987.0752 | 1252520.5613
18 | 2683106.33 | 1252346.94
19 | 2682826.1169 | 1252376.1311
20 | 2682989.4905 | 1252473.4205
21 | 2682813.6671 | 1252373.8252
22 | 2682819.8928 | 1252374.9783
23 | 2683158.4813 | 1252486.902
24 | 2683135.6979 | 1252574.9484
25 | 2683262.6711 | 1252557.1067
26 | 2683131.7846 | 1252576.1177
27 | 2683115.7136 | 1252582.9963
28 | 2683028.5195 | 1252560.6349
29 | 2683005.5772 | 1252548.01
30 | 2683066.3537 | 1252531.5211
31 | 2682989.5375 | 1252474.0461
32 | 2683112.9912 | 1252497.3605
33 | 2682989.5375 | 1252474.0461

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98873 | -0.21591 | 0.014212 | 0.0035618
1 | 0.98888 | -0.21313 | 0 | 0
2 | 0.98737 | -0.24247 | 0 | 0
3 | 0.99283 | -0.13661 | 0 | 0
4 | 0.98679 | -0.2537 | 0.0043796 | 0.0010976
5 | 0.99157 | -0.16082 | 0 | 0
6 | 0.995 | -0.095146 | 0.081236 | 0.02036
7 | 0.99102 | -0.17137 | 0 | 0
8 | 0.9909 | -0.17368 | 0.0067041 | 0.0016802
9 | 0.98985 | -0.19361 | 0.029168 | 0.0073102
10 | 0.98155 | -0.3534 | 0 | 0
11 | 0.98694 | -0.24951 | 0 | 0
12 | 0.98107 | -0.36267 | 0.0018408 | 0.00046135
13 | 0.99725 | -0.051485 | 0 | 0
14 | 0.9973 | -0.050525 | 0 | 0
15 | 0.99717 | -0.053059 | 0.006169 | 0.0015461
16 | 0.99675 | -0.060843 | 0 | 0
17 | 0.99792 | -0.039025 | 0.00097782 | 0.00024506
18 | 0.9866 | -0.25605 | 0.0089489 | 0.0022428
19 | 0.98671 | -0.25518 | 0.0043768 | 0.0010969
20 | 1 | 0 | -0.31778 | -0.081122
21 | 0.98664 | -0.25667 | 0.0043796 | 0.0010976
22 | 0.98666 | -0.25618 | 0.0043768 | 0.0010969
23 | 0.97605 | -0.46073 | 0 | 0
24 | 0.98904 | -0.20675 | 0 | 0
25 | 0.98432 | -0.29698 | 0 | 0
26 | 0.98919 | -0.20397 | 0.0073017 | 0.00183
27 | 0.98987 | -0.1909 | 0 | 0
28 | 0.99473 | -0.098864 | 0 | 0
29 | 0.99611 | -0.072992 | 0.0030459 | 0.00076337
30 | 0.97013 | -0.57401 | 0.076547 | 0.019184
31 | 0.99997 | -0.00051435 | 0 | 0
32 | 0.97287 | -0.52339 | 0.057526 | 0.014417
33 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.014212 | -0.0035618 | 0.014214 | 0.0035629 | 1.8853e-06 | 1.0656e-06 | 0.021388 | 0.021388 | 0.021388 | 0.98873 | -0.21591 | 0.98888 | -0.21313 | 5.8759
1 | 0.017548 | 0.0044099 | -0.017524 | -0.0043953 | 2.4547e-05 | 1.4508e-05 | 0.02641 | 0.02641 | 0.02641 | 0.98888 | -0.21313 | 0.98737 | -0.24247 | 7.2556
2 | -0.031762 | -0.0079727 | 0.031878 | 0.0080454 | 0.00011637 | 7.2725e-05 | 0.047798 | 0.047798 | 0.047798 | 0.98888 | -0.21313 | 0.99283 | -0.13661 | 13.1314
3 | 0.017524 | 0.0043953 | -0.017514 | -0.0043898 | 9.3706e-06 | 5.5393e-06 | 0.02641 | 0.026411 | 0.026411 | 0.98737 | -0.24247 | 0.98679 | -0.2537 | 7.2556
4 | 0.10543 | 0.026899 | -0.10531 | -0.026821 | 0.00012309 | 7.8097e-05 | 0.15819 | 0.15819 | 0.15819 | 0.99283 | -0.13661 | 0.99157 | -0.16082 | 21.7291
5 | -0.13731 | -0.034945 | 0.13759 | 0.03512 | 0.00027509 | 0.00017516 | 0.20598 | 0.20598 | 0.20598 | 0.99283 | -0.13661 | 0.995 | -0.095146 | 28.2946
6 | 0.013135 | 0.0032922 | -0.013134 | -0.0032917 | 9.3144e-07 | 5.1524e-07 | 0.019806 | 0.019806 | 0.019806 | 0.98679 | -0.2537 | 0.98671 | -0.25518 | 5.4413
7 | 0.098601 | 0.02514 | -0.098446 | -0.025041 | 0.00015582 | 9.875e-05 | 0.14812 | 0.14812 | 0.14812 | 0.99157 | -0.16082 | 0.98985 | -0.19361 | 20.3463
8 | 0.0067082 | 0.0016814 | -0.0067048 | -0.0016804 | 3.3737e-06 | 1.0147e-06 | 0.010067 | 0.010067 | 0.010067 | 0.99157 | -0.16082 | 0.99102 | -0.17137 | 2.7657
9 | -0.21882 | -0.055479 | 0.21983 | 0.056122 | 0.0010057 | 0.00064235 | 0.32747 | 0.32747 | 0.32747 | 0.995 | -0.095146 | 1 | 0 | 44.9823
10 | 0.0067048 | 0.0016804 | -0.0067041 | -0.0016802 | 7.3529e-07 | 2.2134e-07 | 0.010067 | 0.010067 | 0.010067 | 0.99102 | -0.17137 | 0.9909 | -0.17368 | 2.7658
11 | 0.069277 | 0.017731 | -0.06909 | -0.017613 | 0.00018698 | 0.00011732 | 0.10427 | 0.10427 | 0.10427 | 0.98985 | -0.19361 | 0.98694 | -0.24951 | 14.3235
12 | -0.059838 | -0.015178 | 0.060139 | 0.015369 | 0.00030053 | 0.0001911 | 0.090779 | 0.090778 | 0.090779 | 0.98155 | -0.3534 | 0.98694 | -0.24951 | 24.9392
13 | 0.059838 | 0.015178 | -0.059811 | -0.015161 | 2.6659e-05 | 1.6953e-05 | 0.090779 | 0.090779 | 0.090779 | 0.98155 | -0.3534 | 0.98107 | -0.36267 | 24.9392
14 | 0.0089517 | 0.0022441 | -0.0089489 | -0.0022428 | 2.7873e-06 | 1.2627e-06 | 0.013497 | 0.013497 | 0.013497 | 0.98694 | -0.24951 | 0.9866 | -0.25605 | 3.708
15 | 0.057971 | 0.0147 | -0.057699 | -0.014527 | 0.00027188 | 0.00017283 | 0.087987 | 0.087987 | 0.087987 | 0.98107 | -0.36267 | 0.97605 | -0.46073 | 24.1723
16 | -0.0061695 | -0.0015462 | 0.0061698 | 0.0015463 | 2.8195e-07 | 6.4682e-08 | 0.0092056 | 0.0092055 | 0.0092056 | 0.99725 | -0.051485 | 0.9973 | -0.050525 | 2.529
17 | 0.0061695 | 0.0015462 | -0.006169 | -0.0015461 | 4.6264e-07 | 1.0616e-07 | 0.0092056 | 0.0092057 | 0.0092057 | 0.99725 | -0.051485 | 0.99717 | -0.053059 | 2.529
18 | 0.088914 | 0.023059 | -0.088869 | -0.02303 | 4.4864e-05 | 2.836e-05 | 0.13294 | 0.13294 | 0.13294 | 0.9973 | -0.050525 | 0.99675 | -0.060843 | 18.261
19 | -0.095084 | -0.024605 | 0.095137 | 0.024639 | 5.3446e-05 | 3.3837e-05 | 0.14215 | 0.14214 | 0.14215 | 0.9973 | -0.050525 | 0.99792 | -0.039025 | 19.5254
20 | 0.088869 | 0.02303 | -0.088816 | -0.022997 | 5.277e-05 | 3.3358e-05 | 0.13294 | 0.13294 | 0.13294 | 0.99675 | -0.060843 | 0.99611 | -0.072992 | 18.261
21 | -0.096115 | -0.024884 | 0.096296 | 0.024999 | 0.00018125 | 0.00011477 | 0.1436 | 0.1436 | 0.1436 | 0.99792 | -0.039025 | 0.99997 | -0.00051435 | 19.7257
22 | 0.0087569 | 0.0021947 | -0.0087565 | -0.0021945 | 4.1397e-07 | 1.8409e-07 | 0.013206 | 0.013206 | 0.013206 | 0.98671 | -0.25518 | 0.98666 | -0.25618 | 3.628
23 | 0.096298 | 0.025 | -0.096296 | -0.024999 | 2.4258e-06 | 1.536e-06 | 0.1436 | 0.1436 | 0.1436 | 1 | 0 | 0.99997 | -0.00051435 | 19.7256
24 | -0.0043796 | -0.0010976 | 0.0043797 | 0.0010976 | 1.0359e-07 | -1.4566e-08 | 0.0066052 | 0.0066051 | 0.0066052 | 0.98664 | -0.25667 | 0.98666 | -0.25618 | 1.8146
25 | 0.057699 | 0.014527 | -0.057526 | -0.014417 | 0.00017228 | 0.00010952 | 0.087987 | 0.087987 | 0.087987 | 0.97605 | -0.46073 | 0.97287 | -0.52339 | 24.1724
26 | 0.077912 | 0.020052 | -0.077572 | -0.019838 | 0.0003403 | 0.00021443 | 0.11741 | 0.11741 | 0.11741 | 0.98904 | -0.20675 | 0.98432 | -0.29698 | 16.1277
27 | -0.077912 | -0.020052 | 0.077923 | 0.020059 | 1.0556e-05 | 6.6512e-06 | 0.11741 | 0.11741 | 0.11741 | 0.98904 | -0.20675 | 0.98919 | -0.20397 | 16.1275
28 | 0.077572 | 0.019838 | -0.076547 | -0.019184 | 0.001025 | 0.00065349 | 0.11741 | 0.11741 | 0.11741 | 0.98432 | -0.29698 | 0.97013 | -0.57401 | 32.2556
29 | -0.085224 | -0.021889 | 0.085279 | 0.021923 | 5.4096e-05 | 3.4172e-05 | 0.12839 | 0.12839 | 0.12839 | 0.98919 | -0.20397 | 0.98987 | -0.1909 | 17.6363
30 | -0.085279 | -0.021923 | 0.085662 | 0.022165 | 0.00038324 | 0.00024207 | 0.12839 | 0.12839 | 0.12839 | 0.98987 | -0.1909 | 0.99473 | -0.098864 | 17.6362
31 | -0.085662 | -0.022165 | 0.08577 | 0.022234 | 0.0001084 | 6.8463e-05 | 0.12839 | 0.12839 | 0.12839 | 0.99473 | -0.098864 | 0.99611 | -0.072992 | 17.6361

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.34777 | 0.088639

## res_load
| p_mw | q_mvar
0 | 0.014212 | 0.0035618
1 | 0.0043796 | 0.0010976
2 | 0.081236 | 0.02036
3 | 0.0067041 | 0.0016802
4 | 0.029168 | 0.0073102
5 | 0.0018408 | 0.00046135
6 | 0.006169 | 0.0015461
7 | 0.00097782 | 0.00024506
8 | 0.0089489 | 0.0022428
9 | 0.0043768 | 0.0010969
10 | 0.029991 | 0.0075164
11 | 0.0043796 | 0.0010976
12 | 0.0043768 | 0.0010969
13 | 0.0073017 | 0.00183
14 | 0.0030459 | 0.00076337
15 | 0.076547 | 0.019184
16 | 0.057526 | 0.014417

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1