## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-511_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-511_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-511_0_4_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_261-511_0_4_node_2 | 0.4 | n |  | TRUE
4 | bus_LV_261-511_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_261-511_0_4_node_11 | 0.4 | n |  | TRUE
6 | bus_LV_261-511_0_4_node_27 | 0.4 | n |  | TRUE
7 | bus_LV_261-511_0_4_node_26 | 0.4 | n |  | TRUE
8 | bus_LV_261-511_0_4_node_5 | 0.4 | n |  | TRUE
9 | bus_LV_261-511_0_4_node_33 | 0.4 | n |  | TRUE
10 | bus_LV_261-511_0_4_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_261-511_0_4_node_6 | 0.4 | n |  | TRUE
12 | bus_LV_261-511_0_4_node_22 | 0.4 | n |  | TRUE
13 | bus_LV_261-511_0_4_node_13 | 0.4 | n |  | TRUE
14 | bus_LV_261-511_0_4_node_21 | 0.4 | n |  | TRUE
15 | bus_LV_261-511_0_4_node_7 | 0.4 | n |  | TRUE
16 | bus_LV_261-511_0_4_node_25 | 0.4 | n |  | TRUE
17 | bus_LV_261-511_0_4_node_24 | 0.4 | n |  | TRUE
18 | bus_LV_261-511_0_4_node_12 | 0.4 | n |  | TRUE
19 | bus_LV_261-511_0_4_node_15 | 0.4 | n |  | TRUE
20 | bus_LV_261-511_0_4_node_32 | 0.4 | n |  | TRUE
21 | bus_LV_261-511_0_4_node_14 | 0.4 | n |  | TRUE
22 | bus_LV_261-511_0_4_node_20 | 0.4 | n |  | TRUE
23 | bus_LV_261-511_0_4_node_23 | 0.4 | n |  | TRUE
24 | bus_LV_261-511_0_4_node_29 | 0.4 | n |  | TRUE
25 | bus_LV_261-511_0_4_node_28 | 0.4 | n |  | TRUE
26 | bus_LV_261-511_0_4_node_16 | 0.4 | n |  | TRUE
27 | bus_LV_261-511_0_4_node_17 | 0.4 | n |  | TRUE
28 | bus_LV_261-511_0_4_node_18 | 0.4 | n |  | TRUE
29 | bus_LV_261-511_0_4_node_31 | 0.4 | n |  | TRUE
30 | bus_LV_261-511_0_4_node_19 | 0.4 | n |  | TRUE
31 | bus_LV_261-511_0_4_node_30 | 0.4 | n |  | TRUE
32 | bus_MV_528_0_node_38 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-511_0_4_load_0 | 0 | 0.0078069 | 0.0019566 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-511_0_4_load_27 | 6 | 0.061475 | 0.015407 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-511_0_4_load_26 | 7 | 0.0024335 | 0.0006099 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-511_0_4_load_33 | 9 | 0.0096125 | 0.0024091 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-511_0_4_load_22 | 12 | 0.033059 | 0.0082854 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-511_0_4_load_21 | 14 | 0.013452 | 0.0033714 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-511_0_4_load_25 | 16 | 0.0030903 | 0.00077451 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-511_0_4_load_24 | 17 | 0.026441 | 0.0066267 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-511_0_4_load_32 | 20 | 0.023775 | 0.0059586 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-511_0_4_load_20 | 22 | 0.080174 | 0.020094 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-511_0_4_load_23 | 23 | 0.028648 | 0.00718 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-511_0_4_load_29 | 24 | 0.0043154 | 0.0010816 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-511_0_4_load_28 | 25 | 0.015793 | 0.0039582 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-511_0_4_load_31 | 29 | 0.0031973 | 0.00080132 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-511_0_4_load_19 | 30 | 0.01029 | 0.002579 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-511_0_4_load_30 | 31 | 0.020262 | 0.0050781 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 12 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-511_0_4_line_0 |  | 0 | 1 | 0.033667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-511_0_4_line_1 |  | 1 | 2 | 0.02182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-511_0_4_line_2 |  | 2 | 6 | 0.0069122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-511_0_4_line_3 |  | 3 | 4 | 0.004858 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-511_0_4_line_4 |  | 3 | 5 | 0.005015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_261-511_0_4_line_5 |  | 4 | 7 | 0.027253 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_261-511_0_4_line_6 |  | 5 | 18 | 0.011792 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_261-511_0_4_line_7 |  | 5 | 12 | 0.01679 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
8 | LV_261-511_0_4_line_8 |  | 6 | 27 | 0.017969 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_261-511_0_4_line_9 |  | 7 | 15 | 0.017185 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_261-511_0_4_line_10 |  | 8 | 9 | 0.005593 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_261-511_0_4_line_11 |  | 8 | 10 | 0.23034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_261-511_0_4_line_12 |  | 10 | 17 | 0.048227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-511_0_4_line_13 |  | 11 | 12 | 0.030055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
14 | LV_261-511_0_4_line_14 |  | 11 | 13 | 0.034287 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
15 | LV_261-511_0_4_line_15 |  | 11 | 14 | 0.056132 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_261-511_0_4_line_16 |  | 13 | 21 | 0.014897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_261-511_0_4_line_17 |  | 13 | 22 | 0.046247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_261-511_0_4_line_18 |  | 14 | 30 | 0.016126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_261-511_0_4_line_19 |  | 15 | 16 | 0.034946 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_261-511_0_4_line_20 |  | 16 | 26 | 0.014604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_261-511_0_4_line_21 |  | 17 | 23 | 0.014406 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_261-511_0_4_line_22 |  | 18 | 19 | 0.027599 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_261-511_0_4_line_23 |  | 18 | 20 | 0.0083592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_261-511_0_4_line_24 |  | 19 | 24 | 0.024505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_261-511_0_4_line_25 |  | 19 | 25 | 0.014965 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_261-511_0_4_line_26 |  | 20 | 28 | 0.015603 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_261-511_0_4_line_27 |  | 21 | 23 | 0.026477 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_261-511_0_4_line_28 |  | 26 | 27 | 0.035044 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_261-511_0_4_line_29 |  | 28 | 29 | 0.012531 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_261-511_0_4_line_30 |  | 29 | 31 | 0.019812 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-511_0_4_trafo_22 | 0.63 MVA 20/0.4 kV | 32 | 12 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24 | x25 | y25 | x26 | y26 | x27 | y27 | x28 | y28 | x29 | y29 | x30 | y30 | x31 | y31 | x32 | y32 | x33 | y33 | x34 | y34 | x35 | y35 | x36 | y36
0 | 2682815.7657 | 1251438.7961 | 2682847.2386 | 1251426.84
1 | 2682815.7657 | 1251438.7961 | 2682814.0776 | 1251434.2803 | 2682813.066 | 1251431.5864 | 2682811.9834 | 1251428.5801 | 2682808.2849 | 1251418.2985
2 | 2682808.2849 | 1251418.2985 | 2682805.9454 | 1251411.7943
3 | 2682890.8874 | 1251410.2583 | 2682889.2076 | 1251405.6981
4 | 2682890.8874 | 1251410.2583 | 2682892.6257 | 1251414.9639
5 | 2682889.2076 | 1251405.6981 | 2682886.5095 | 1251398.3771 | 2682879.4734 | 1251380.2435
6 | 2682892.6257 | 1251414.9639 | 2682898.9851 | 1251412.5511 | 2682903.5938 | 1251410.6363
7 | 2682892.6257 | 1251414.9639 | 2682898.5418 | 1251430.6775
8 | 2682799.8636 | 1251394.8856 | 2682805.9454 | 1251411.7943
9 | 2682873.2567 | 1251364.2219 | 2682879.4734 | 1251380.2435
10 | 2682857.1926 | 1251533.1456 | 2682861.7818 | 1251529.9296
11 | 2682857.1926 | 1251533.1456 | 2682856.4987 | 1251532.5688 | 2682849.2968 | 1251531.5451 | 2682845.2926 | 1251529.6433 | 2682843.3263 | 1251528.2926 | 2682843.6282 | 1251525.5948 | 2682844.1952 | 1251522.834 | 2682842.7849 | 1251519.5118 | 2682840.7744 | 1251516.4592 | 2682842.4998 | 1251516.1497 | 2682844.5858 | 1251513.7994 | 2682845.2161 | 1251511.373 | 2682851.2212 | 1251508.377 | 2682863.0293 | 1251503.8831 | 2682873.944 | 1251501.2115 | 2682881.1317 | 1251500.556 | 2682886.6088 | 1251505.6253 | 2682889.0926 | 1251514.7668 | 2682889.9083 | 1251526.0533 | 2682892.4179 | 1251533.3494 | 2682897.3 | 1251542.102 | 2682898.6067 | 1251549.5926 | 2682898.9519 | 1251559.9829 | 2682901.8758 | 1251559.2455 | 2682917.8934 | 1251554.933 | 2682930.1445 | 1251551.1461 | 2682932.1882 | 1251549.6624 | 2682934.8658 | 1251546.5754 | 2682935.8369 | 1251544.6097 | 2682937.2618 | 1251540.9603 | 2682945.7685 | 1251537.7436 | 2682953.4782 | 1251534.8493 | 2682956.4323 | 1251536.8144 | 2682959.5904 | 1251537.6815 | 2682964.4878 | 1251538.3283 | 2682966.6443 | 1251537.9582 | 2682982.423 | 1251531.8412
12 | 2682982.423 | 1251531.8412 | 2682962.5914 | 1251487.8805
13 | 2682909.1319 | 1251458.8053 | 2682898.5418 | 1251430.6775
14 | 2682921.4557 | 1251490.8128 | 2682909.1319 | 1251458.8053
15 | 2682909.1319 | 1251458.8053 | 2682861.6017 | 1251475.8978 | 2682856.1802 | 1251474.4098
16 | 2682921.4557 | 1251490.8128 | 2682927.068 | 1251488.9232 | 2682926.0925 | 1251486.3521 | 2682931.9131 | 1251484.143
17 | 2682921.4557 | 1251490.8128 | 2682895.3637 | 1251500.3215 | 2682886.7757 | 1251494.2413 | 2682879.5298 | 1251490.9598
18 | 2682841.0812 | 1251480.0719 | 2682856.1802 | 1251474.4098 | 2682856.1802 | 1251474.4098
19 | 2682873.2567 | 1251364.2219 | 2682872.5814 | 1251364.4681 | 2682848.9579 | 1251372.8552 | 2682842.9793 | 1251370.7034 | 2682840.3371 | 1251371.6444
20 | 2682826.5559 | 1251376.4782 | 2682835.4992 | 1251373.3675 | 2682840.3371 | 1251371.6444
21 | 2682956.6676 | 1251474.7491 | 2682962.5914 | 1251487.8805
22 | 2682903.5938 | 1251410.6363 | 2682893.772 | 1251384.8352
23 | 2682903.5938 | 1251410.6363 | 2682906.5998 | 1251418.4364
24 | 2682893.772 | 1251384.8352 | 2682885.0547 | 1251361.9329
25 | 2682893.772 | 1251384.8352 | 2682907.7862 | 1251379.5848
26 | 2682912.2107 | 1251432.9958 | 2682906.5998 | 1251418.4364
27 | 2682931.9131 | 1251484.143 | 2682956.6676 | 1251474.7491
28 | 2682826.5559 | 1251376.4782 | 2682811.5823 | 1251381.6839 | 2682809.4597 | 1251386.6469 | 2682807.7522 | 1251391.6156 | 2682799.8636 | 1251394.8856
29 | 2682912.2107 | 1251432.9958 | 2682923.9701 | 1251428.6679
30 | 2682942.5626 | 1251421.8252 | 2682923.9701 | 1251428.6679

## bus_geodata
| x | y | coords
0 | 2682847.2386 | 1251426.84
1 | 2682815.7657 | 1251438.7961
2 | 2682808.2849 | 1251418.2985
3 | 2682890.8874 | 1251410.2583
4 | 2682889.2076 | 1251405.6981
5 | 2682892.6257 | 1251414.9639
6 | 2682805.9454 | 1251411.7943
7 | 2682879.4734 | 1251380.2435
8 | 2682857.1926 | 1251533.1456
9 | 2682861.7817 | 1251529.9296
10 | 2682982.423 | 1251531.8412
11 | 2682909.1319 | 1251458.8053
12 | 2682898.5418 | 1251430.6775
13 | 2682921.4557 | 1251490.8128
14 | 2682856.1802 | 1251474.4098
15 | 2682873.2567 | 1251364.2219
16 | 2682840.3371 | 1251371.6444
17 | 2682962.5914 | 1251487.8805
18 | 2682903.5938 | 1251410.6363
19 | 2682893.772 | 1251384.8352
20 | 2682906.5998 | 1251418.4364
21 | 2682931.9131 | 1251484.143
22 | 2682879.5298 | 1251490.9598
23 | 2682956.6676 | 1251474.7491
24 | 2682885.0547 | 1251361.9329
25 | 2682907.7862 | 1251379.5848
26 | 2682826.5559 | 1251376.4782
27 | 2682799.8636 | 1251394.8856
28 | 2682912.2107 | 1251432.9958
29 | 2682923.9701 | 1251428.6679
30 | 2682841.0812 | 1251480.0719
31 | 2682942.5626 | 1251421.8252
32 | 2682892.6257 | 1251414.9639

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98816 | -0.22782 | 0.0078069 | 0.0019566
1 | 0.9884 | -0.22313 | 0 | 0
2 | 0.98855 | -0.22009 | 0 | 0
3 | 0.99857 | -0.02738 | 0 | 0
4 | 0.99823 | -0.033735 | 0 | 0
5 | 0.99891 | -0.020824 | 0 | 0
6 | 0.9886 | -0.21913 | 0.061475 | 0.015407
7 | 0.99636 | -0.069464 | 0.0024335 | 0.0006099
8 | 0.99004 | -0.19179 | 0 | 0
9 | 0.98999 | -0.19274 | 0.0096125 | 0.0024091
10 | 0.99207 | -0.15248 | 0 | 0
11 | 0.99768 | -0.044273 | 0 | 0
12 | 1 | 0 | -0.31447 | -0.079185
13 | 0.99541 | -0.087866 | 0 | 0
14 | 0.99647 | -0.067639 | 0.013452 | 0.0033714
15 | 0.99522 | -0.091327 | 0 | 0
16 | 0.9929 | -0.13594 | 0.0030903 | 0.00077451
17 | 0.99249 | -0.14427 | 0.026441 | 0.0066267
18 | 0.99819 | -0.034707 | 0 | 0
19 | 0.99768 | -0.04442 | 0 | 0
20 | 0.99783 | -0.041616 | 0.023775 | 0.0059586
21 | 0.99453 | -0.10484 | 0 | 0
22 | 0.99202 | -0.15331 | 0.080174 | 0.020094
23 | 0.99297 | -0.13508 | 0.028648 | 0.00718
24 | 0.99759 | -0.046273 | 0.0043154 | 0.0010816
25 | 0.99747 | -0.04856 | 0.015793 | 0.0039582
26 | 0.99197 | -0.15385 | 0 | 0
27 | 0.98974 | -0.19695 | 0 | 0
28 | 0.9975 | -0.048026 | 0 | 0
29 | 0.99723 | -0.053177 | 0.0031973 | 0.00080132
30 | 0.99632 | -0.070552 | 0.01029 | 0.002579
31 | 0.99686 | -0.060215 | 0.020262 | 0.0050781
32 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0078069 | -0.0019566 | 0.0078086 | 0.0019573 | 1.7448e-06 | 6.8529e-07 | 0.011756 | 0.011756 | 0.011756 | 0.98816 | -0.22782 | 0.9884 | -0.22313 | 3.2297
1 | -0.0078086 | -0.0019573 | 0.0078097 | 0.0019577 | 1.1308e-06 | 4.4402e-07 | 0.011756 | 0.011756 | 0.011756 | 0.9884 | -0.22313 | 0.98855 | -0.22009 | 3.2296
2 | -0.0078097 | -0.0019577 | 0.0078101 | 0.0019579 | 3.5821e-07 | 1.4063e-07 | 0.011756 | 0.011756 | 0.011756 | 0.98855 | -0.22009 | 0.9886 | -0.21913 | 3.2296
3 | 0.075469 | 0.01917 | -0.075446 | -0.019155 | 2.3077e-05 | 1.4706e-05 | 0.11255 | 0.11255 | 0.11255 | 0.99857 | -0.02738 | 0.99823 | -0.033735 | 30.9206
4 | -0.075469 | -0.01917 | 0.075493 | 0.019185 | 2.3823e-05 | 1.5181e-05 | 0.11255 | 0.11255 | 0.11255 | 0.99857 | -0.02738 | 0.99891 | -0.020824 | 30.9206
5 | 0.075446 | 0.019155 | -0.075317 | -0.019073 | 0.00012946 | 8.2501e-05 | 0.11255 | 0.11255 | 0.11255 | 0.99823 | -0.033735 | 0.99636 | -0.069464 | 30.9206
6 | 0.067436 | 0.016935 | -0.067391 | -0.016907 | 4.4636e-05 | 2.8413e-05 | 0.10047 | 0.10047 | 0.10047 | 0.99891 | -0.020824 | 0.99819 | -0.034707 | 27.6008
7 | -0.14293 | -0.03612 | 0.14307 | 0.036211 | 0.00014285 | 9.0986e-05 | 0.21302 | 0.21302 | 0.21302 | 0.99891 | -0.020824 | 1 | 0 | 29.2607
8 | -0.069285 | -0.017365 | 0.069358 | 0.017412 | 7.3284e-05 | 4.6671e-05 | 0.10429 | 0.10429 | 0.10429 | 0.9886 | -0.21913 | 0.98974 | -0.19695 | 28.65
9 | 0.072883 | 0.018463 | -0.072807 | -0.018414 | 7.6451e-05 | 4.8705e-05 | 0.10892 | 0.10892 | 0.10892 | 0.99636 | -0.069464 | 0.99522 | -0.091327 | 29.9222
10 | 0.0096129 | 0.0024093 | -0.0096125 | -0.0024091 | 4.3782e-07 | 2.0829e-07 | 0.014448 | 0.014448 | 0.014448 | 0.99004 | -0.19179 | 0.98999 | -0.19274 | 3.9693
11 | -0.0096129 | -0.0024093 | 0.0096309 | 0.0024179 | 1.8029e-05 | 8.5708e-06 | 0.014448 | 0.014447 | 0.014448 | 0.99004 | -0.19179 | 0.99207 | -0.15248 | 3.9693
12 | -0.0096309 | -0.0024179 | 0.0096347 | 0.0024197 | 3.7746e-06 | 1.7928e-06 | 0.014447 | 0.014447 | 0.014447 | 0.99207 | -0.15248 | 0.99249 | -0.14427 | 3.969
13 | -0.16938 | -0.042743 | 0.16974 | 0.042973 | 0.00035996 | 0.00022959 | 0.25274 | 0.25274 | 0.25274 | 0.99768 | -0.044273 | 1 | 0 | 34.7164
14 | 0.14561 | 0.036776 | -0.14531 | -0.036583 | 0.00030351 | 0.00019335 | 0.21728 | 0.21728 | 0.21728 | 0.99768 | -0.044273 | 0.99541 | -0.087866 | 29.8461
15 | 0.02377 | 0.0059674 | -0.023744 | -0.0059511 | 2.6463e-05 | 1.6204e-05 | 0.035456 | 0.035457 | 0.035457 | 0.99768 | -0.044273 | 0.99647 | -0.067639 | 9.7408
16 | 0.064886 | 0.016329 | -0.064833 | -0.016296 | 5.2585e-05 | 3.3461e-05 | 0.09702 | 0.09702 | 0.09702 | 0.99541 | -0.087866 | 0.99453 | -0.10484 | 26.6538
17 | 0.080425 | 0.020254 | -0.080174 | -0.020094 | 0.00025082 | 0.00015992 | 0.12026 | 0.12026 | 0.12026 | 0.99541 | -0.087866 | 0.99202 | -0.15331 | 33.0384
18 | 0.010292 | 0.0025797 | -0.01029 | -0.002579 | 1.4283e-06 | 7.0409e-07 | 0.015369 | 0.015369 | 0.015369 | 0.99647 | -0.067639 | 0.99632 | -0.070552 | 4.2222
19 | 0.072807 | 0.018414 | -0.072651 | -0.018315 | 0.00015546 | 9.9041e-05 | 0.10892 | 0.10892 | 0.10892 | 0.99522 | -0.091327 | 0.9929 | -0.13594 | 29.9222
20 | 0.069561 | 0.017541 | -0.069501 | -0.017503 | 5.9561e-05 | 3.7931e-05 | 0.10429 | 0.10429 | 0.10429 | 0.9929 | -0.13594 | 0.99197 | -0.15385 | 28.6499
21 | -0.036076 | -0.0090464 | 0.036091 | 0.0090563 | 1.5804e-05 | 9.9286e-06 | 0.054089 | 0.054089 | 0.054089 | 0.99249 | -0.14427 | 0.99297 | -0.13508 | 14.8595
22 | 0.020121 | 0.005047 | -0.020112 | -0.0050414 | 9.3128e-06 | 5.5996e-06 | 0.029997 | 0.029997 | 0.029997 | 0.99819 | -0.034707 | 0.99768 | -0.04442 | 8.2409
23 | 0.04727 | 0.01186 | -0.047254 | -0.01185 | 1.5567e-05 | 9.8537e-06 | 0.07047 | 0.07047 | 0.07047 | 0.99819 | -0.034707 | 0.99783 | -0.041616 | 19.3599
24 | 0.0043158 | 0.0010815 | -0.0043154 | -0.0010816 | 3.8076e-07 | -7.6289e-08 | 0.0064369 | 0.006437 | 0.006437 | 0.99768 | -0.04442 | 0.99759 | -0.046273 | 1.7684
25 | 0.015796 | 0.00396 | -0.015793 | -0.0039582 | 3.1151e-06 | 1.7983e-06 | 0.02356 | 0.02356 | 0.02356 | 0.99768 | -0.04442 | 0.99747 | -0.04856 | 6.4726
26 | 0.023479 | 0.0058914 | -0.023472 | -0.005887 | 7.174e-06 | 4.3876e-06 | 0.035015 | 0.035016 | 0.035016 | 0.99783 | -0.041616 | 0.9975 | -0.048026 | 9.6196
27 | 0.064833 | 0.016296 | -0.06474 | -0.016236 | 9.3459e-05 | 5.9471e-05 | 0.09702 | 0.09702 | 0.09702 | 0.99453 | -0.10484 | 0.99297 | -0.13508 | 26.6538
28 | 0.069501 | 0.017503 | -0.069358 | -0.017412 | 0.00014292 | 9.1018e-05 | 0.10429 | 0.10429 | 0.10429 | 0.99197 | -0.15385 | 0.98974 | -0.19695 | 28.6499
29 | 0.023472 | 0.005887 | -0.023466 | -0.0058835 | 5.7614e-06 | 3.5237e-06 | 0.035016 | 0.035016 | 0.035016 | 0.9975 | -0.048026 | 0.99723 | -0.053177 | 9.6197
30 | 0.020269 | 0.0050822 | -0.020262 | -0.0050781 | 6.796e-06 | 4.091e-06 | 0.030245 | 0.030245 | 0.030245 | 0.99723 | -0.053177 | 0.99686 | -0.060215 | 8.309

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.34753 | 0.08747

## res_load
| p_mw | q_mvar
0 | 0.0078069 | 0.0019566
1 | 0.061475 | 0.015407
2 | 0.0024335 | 0.0006099
3 | 0.0096125 | 0.0024091
4 | 0.033059 | 0.0082854
5 | 0.013452 | 0.0033714
6 | 0.0030903 | 0.00077451
7 | 0.026441 | 0.0066267
8 | 0.023775 | 0.0059586
9 | 0.080174 | 0.020094
10 | 0.028648 | 0.00718
11 | 0.0043154 | 0.0010816
12 | 0.015793 | 0.0039582
13 | 0.0031973 | 0.00080132
14 | 0.01029 | 0.002579
15 | 0.020262 | 0.0050781

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1