## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-512_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-512_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-512_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_261-512_0_3_node_11 | 0.4 | n |  | TRUE
4 | bus_LV_261-512_0_3_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_261-512_0_3_node_58 | 0.4 | n |  | TRUE
6 | bus_LV_261-512_0_3_node_9 | 0.4 | n |  | TRUE
7 | bus_LV_261-512_0_3_node_13 | 0.4 | n |  | TRUE
8 | bus_LV_261-512_0_3_node_12 | 0.4 | n |  | TRUE
9 | bus_LV_261-512_0_3_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_261-512_0_3_node_78 | 0.4 | n |  | TRUE
11 | bus_LV_261-512_0_3_node_6 | 0.4 | n |  | TRUE
12 | bus_LV_261-512_0_3_node_95 | 0.4 | n |  | TRUE
13 | bus_LV_261-512_0_3_node_3 | 0.4 | n |  | TRUE
14 | bus_LV_261-512_0_3_node_56 | 0.4 | n |  | TRUE
15 | bus_LV_261-512_0_3_node_14 | 0.4 | n |  | TRUE
16 | bus_LV_261-512_0_3_node_15 | 0.4 | n |  | TRUE
17 | bus_LV_261-512_0_3_node_16 | 0.4 | n |  | TRUE
18 | bus_LV_261-512_0_3_node_17 | 0.4 | n |  | TRUE
19 | bus_LV_261-512_0_3_node_18 | 0.4 | n |  | TRUE
20 | bus_LV_261-512_0_3_node_19 | 0.4 | n |  | TRUE
21 | bus_LV_261-512_0_3_node_63 | 0.4 | n |  | TRUE
22 | bus_LV_261-512_0_3_node_21 | 0.4 | n |  | TRUE
23 | bus_LV_261-512_0_3_node_20 | 0.4 | n |  | TRUE
24 | bus_LV_261-512_0_3_node_61 | 0.4 | n |  | TRUE
25 | bus_LV_261-512_0_3_node_89 | 0.4 | n |  | TRUE
26 | bus_LV_261-512_0_3_node_66 | 0.4 | n |  | TRUE
27 | bus_LV_261-512_0_3_node_22 | 0.4 | n |  | TRUE
28 | bus_LV_261-512_0_3_node_88 | 0.4 | n |  | TRUE
29 | bus_LV_261-512_0_3_node_23 | 0.4 | n |  | TRUE
30 | bus_LV_261-512_0_3_node_36 | 0.4 | n |  | TRUE
31 | bus_LV_261-512_0_3_node_71 | 0.4 | n |  | TRUE
32 | bus_LV_261-512_0_3_node_24 | 0.4 | n |  | TRUE
33 | bus_LV_261-512_0_3_node_77 | 0.4 | n |  | TRUE
34 | bus_LV_261-512_0_3_node_74 | 0.4 | n |  | TRUE
35 | bus_LV_261-512_0_3_node_26 | 0.4 | n |  | TRUE
36 | bus_LV_261-512_0_3_node_42 | 0.4 | n |  | TRUE
37 | bus_LV_261-512_0_3_node_41 | 0.4 | n |  | TRUE
38 | bus_LV_261-512_0_3_node_27 | 0.4 | n |  | TRUE
39 | bus_LV_261-512_0_3_node_43 | 0.4 | n |  | TRUE
40 | bus_LV_261-512_0_3_node_28 | 0.4 | n |  | TRUE
41 | bus_LV_261-512_0_3_node_60 | 0.4 | n |  | TRUE
42 | bus_LV_261-512_0_3_node_35 | 0.4 | n |  | TRUE
43 | bus_LV_261-512_0_3_node_59 | 0.4 | n |  | TRUE
44 | bus_LV_261-512_0_3_node_29 | 0.4 | n |  | TRUE
45 | bus_LV_261-512_0_3_node_52 | 0.4 | n |  | TRUE
46 | bus_LV_261-512_0_3_node_30 | 0.4 | n |  | TRUE
47 | bus_LV_261-512_0_3_node_55 | 0.4 | n |  | TRUE
48 | bus_LV_261-512_0_3_node_31 | 0.4 | n |  | TRUE
49 | bus_LV_261-512_0_3_node_53 | 0.4 | n |  | TRUE
50 | bus_LV_261-512_0_3_node_49 | 0.4 | n |  | TRUE
51 | bus_LV_261-512_0_3_node_32 | 0.4 | n |  | TRUE
52 | bus_LV_261-512_0_3_node_54 | 0.4 | n |  | TRUE
53 | bus_LV_261-512_0_3_node_65 | 0.4 | n |  | TRUE
54 | bus_LV_261-512_0_3_node_57 | 0.4 | n |  | TRUE
55 | bus_LV_261-512_0_3_node_40 | 0.4 | n |  | TRUE
56 | bus_LV_261-512_0_3_node_82 | 0.4 | n |  | TRUE
57 | bus_LV_261-512_0_3_node_47 | 0.4 | n |  | TRUE
58 | bus_LV_261-512_0_3_node_64 | 0.4 | n |  | TRUE
59 | bus_LV_261-512_0_3_node_69 | 0.4 | n |  | TRUE
60 | bus_LV_261-512_0_3_node_70 | 0.4 | n |  | TRUE
61 | bus_LV_261-512_0_3_node_68 | 0.4 | n |  | TRUE
62 | bus_LV_261-512_0_3_node_67 | 0.4 | n |  | TRUE
63 | bus_LV_261-512_0_3_node_72 | 0.4 | n |  | TRUE
64 | bus_LV_261-512_0_3_node_73 | 0.4 | n |  | TRUE
65 | bus_LV_261-512_0_3_node_75 | 0.4 | n |  | TRUE
66 | bus_LV_261-512_0_3_node_76 | 0.4 | n |  | TRUE
67 | bus_LV_261-512_0_3_node_48 | 0.4 | n |  | TRUE
68 | bus_LV_261-512_0_3_node_90 | 0.4 | n |  | TRUE
69 | bus_LV_261-512_0_3_node_87 | 0.4 | n |  | TRUE
70 | bus_LV_261-512_0_3_node_50 | 0.4 | n |  | TRUE
71 | bus_LV_261-512_0_3_node_84 | 0.4 | n |  | TRUE
72 | bus_LV_261-512_0_3_node_85 | 0.4 | n |  | TRUE
73 | bus_LV_261-512_0_3_node_44 | 0.4 | n |  | TRUE
74 | bus_LV_261-512_0_3_node_45 | 0.4 | n |  | TRUE
75 | bus_LV_261-512_0_3_node_83 | 0.4 | n |  | TRUE
76 | bus_LV_261-512_0_3_node_46 | 0.4 | n |  | TRUE
77 | bus_LV_261-512_0_3_node_91 | 0.4 | n |  | TRUE
78 | bus_LV_261-512_0_3_node_51 | 0.4 | n |  | TRUE
79 | bus_LV_261-512_0_3_node_81 | 0.4 | n |  | TRUE
80 | bus_LV_261-512_0_3_node_80 | 0.4 | n |  | TRUE
81 | bus_LV_261-512_0_3_node_86 | 0.4 | n |  | TRUE
82 | bus_LV_261-512_0_3_node_79 | 0.4 | n |  | TRUE
83 | bus_LV_261-512_0_3_node_92 | 0.4 | n |  | TRUE
84 | bus_LV_261-512_0_3_node_93 | 0.4 | n |  | TRUE
85 | bus_LV_261-512_0_3_node_94 | 0.4 | n |  | TRUE
86 | bus_MV_528_0_node_91 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-512_0_3_load_0 | 0 | 0.025867 | 0.0064829 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-512_0_3_load_1 | 1 | 0.017559 | 0.0044007 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-512_0_3_load_58 | 5 | 0.0051549 | 0.0012919 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-512_0_3_load_13 | 7 | 0.0057879 | 0.0014506 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-512_0_3_load_12 | 8 | 0.019789 | 0.0049597 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-512_0_3_load_78 | 10 | 0.0046751 | 0.0011717 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-512_0_3_load_95 | 12 | 0.0092448 | 0.002317 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-512_0_3_load_3 | 13 | 0.01543 | 0.0038672 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-512_0_3_load_56 | 14 | 0.0014503 | 0.00036348 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-512_0_3_load_14 | 15 | 0.0055654 | 0.0013948 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-512_0_3_load_15 | 16 | 0.0022759 | 0.0005704 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-512_0_3_load_17 | 18 | 0.0031172 | 0.00078125 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-512_0_3_load_18 | 19 | 0.0056687 | 0.0014207 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-512_0_3_load_63 | 21 | 0.0074353 | 0.0018635 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-512_0_3_load_89 | 25 | 0.0060483 | 0.0015158 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-512_0_3_load_66 | 26 | 0.010511 | 0.0026342 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-512_0_3_load_88 | 28 | 0.0027987 | 0.00070142 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_261-512_0_3_load_71 | 31 | 0.004437 | 0.001112 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_261-512_0_3_load_77 | 33 | 0.0050759 | 0.0012722 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_261-512_0_3_load_74 | 34 | 0.010204 | 0.0025573 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_261-512_0_3_load_42 | 36 | 0.00093143 | 0.00023344 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_261-512_0_3_load_41 | 37 | 0.0070834 | 0.0017753 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_261-512_0_3_load_60 | 41 | 0.0073097 | 0.001832 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_261-512_0_3_load_59 | 43 | 0.0034847 | 0.00087335 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_261-512_0_3_load_52 | 45 | 0.009813 | 0.0024594 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_261-512_0_3_load_55 | 47 | 0.0077665 | 0.0019465 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_261-512_0_3_load_53 | 49 | 0.0082662 | 0.0020717 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_261-512_0_3_load_49 | 50 | 0.011198 | 0.0028065 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_261-512_0_3_load_54 | 52 | 0.0076732 | 0.0019231 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_261-512_0_3_load_65 | 53 | 0.0073051 | 0.0018308 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_261-512_0_3_load_57 | 54 | 0.0014498 | 0.00036334 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_261-512_0_3_load_82 | 56 | 0.0023837 | 0.00059741 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_261-512_0_3_load_47 | 57 | 0.0056348 | 0.0014122 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_261-512_0_3_load_64 | 58 | 0.0058732 | 0.001472 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_261-512_0_3_load_69 | 59 | 0.0028151 | 0.00070553 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_261-512_0_3_load_70 | 60 | 0.0065539 | 0.0016426 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_261-512_0_3_load_68 | 61 | 0.0055941 | 0.001402 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_261-512_0_3_load_67 | 62 | 0.0049321 | 0.0012361 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_261-512_0_3_load_72 | 63 | 0.0044342 | 0.0011113 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_261-512_0_3_load_73 | 64 | 0.0050788 | 0.0012729 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_261-512_0_3_load_75 | 65 | 0.0086817 | 0.0021758 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_261-512_0_3_load_76 | 66 | 0.0086779 | 0.0021749 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_261-512_0_3_load_48 | 67 | 0.0010745 | 0.0002693 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_261-512_0_3_load_90 | 68 | 0.001617 | 0.00040526 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_261-512_0_3_load_87 | 69 | 0.0073677 | 0.0018465 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_261-512_0_3_load_50 | 70 | 0.0021956 | 0.00055026 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_261-512_0_3_load_84 | 71 | 0.0024698 | 0.00061898 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_261-512_0_3_load_85 | 72 | 0.0024768 | 0.00062075 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_261-512_0_3_load_44 | 73 | 0.0070956 | 0.0017783 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_261-512_0_3_load_83 | 75 | 0.0015194 | 0.00038079 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_261-512_0_3_load_46 | 76 | 0.0018842 | 0.00047223 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_261-512_0_3_load_91 | 77 | 0.0031513 | 0.0007898 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_261-512_0_3_load_51 | 78 | 0.0021962 | 0.00055042 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_261-512_0_3_load_81 | 79 | 0.0021949 | 0.0005501 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_261-512_0_3_load_80 | 80 | 0.002196 | 0.00055038 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_261-512_0_3_load_86 | 81 | 0.0024697 | 0.00061895 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_261-512_0_3_load_79 | 82 | 0.0021946 | 0.00055003 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_261-512_0_3_load_92 | 83 | 0.0016171 | 0.00040528 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_261-512_0_3_load_93 | 84 | 0.0016161 | 0.00040504 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_261-512_0_3_load_94 | 85 | 0.001617 | 0.00040525 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 44 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-512_0_3_line_0 |  | 0 | 1 | 0.05872 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-512_0_3_line_1 |  | 1 | 2 | 0.025291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-512_0_3_line_2 |  | 2 | 3 | 0.00511 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-512_0_3_line_3 |  | 2 | 4 | 0.014369 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-512_0_3_line_4 |  | 3 | 5 | 0.028705 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_261-512_0_3_line_5 |  | 3 | 6 | 0.027137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_261-512_0_3_line_6 |  | 4 | 13 | 0.03572 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_261-512_0_3_line_7 |  | 5 | 14 | 0.060532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_261-512_0_3_line_8 |  | 6 | 7 | 0.039724 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_261-512_0_3_line_9 |  | 6 | 8 | 0.020789 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_261-512_0_3_line_10 |  | 6 | 9 | 0.058463 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_261-512_0_3_line_11 |  | 9 | 10 | 0.022338 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_261-512_0_3_line_12 |  | 9 | 11 | 0.065106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-512_0_3_line_13 |  | 11 | 12 | 0.014255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_261-512_0_3_line_14 |  | 14 | 54 | 0.0063872 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_261-512_0_3_line_15 |  | 15 | 16 | 0.0040845 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_261-512_0_3_line_16 |  | 15 | 17 | 0.013114 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_261-512_0_3_line_17 |  | 16 | 18 | 0.02618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_261-512_0_3_line_18 |  | 17 | 19 | 0.017157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_261-512_0_3_line_19 |  | 18 | 20 | 0.012598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_261-512_0_3_line_20 |  | 19 | 21 | 0.0089371 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_261-512_0_3_line_21 |  | 20 | 22 | 0.003612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_261-512_0_3_line_22 |  | 21 | 58 | 0.020453 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_261-512_0_3_line_23 |  | 22 | 26 | 0.036613 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_261-512_0_3_line_24 |  | 23 | 24 | 0.014243 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_261-512_0_3_line_25 |  | 23 | 25 | 0.017447 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_261-512_0_3_line_26 |  | 24 | 59 | 0.002381 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_261-512_0_3_line_27 |  | 24 | 60 | 0.010382 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_261-512_0_3_line_28 |  | 24 | 61 | 0.042435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_261-512_0_3_line_29 |  | 25 | 27 | 0.005482 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_261-512_0_3_line_30 |  | 26 | 62 | 0.021058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_261-512_0_3_line_31 |  | 27 | 28 | 0.016569 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_261-512_0_3_line_32 |  | 29 | 30 | 0.030621 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_261-512_0_3_line_33 |  | 29 | 31 | 0.015244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_261-512_0_3_line_34 |  | 30 | 54 | 0.032853 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_261-512_0_3_line_35 |  | 30 | 42 | 0.025982 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_261-512_0_3_line_36 |  | 30 | 44 | 0.011917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
37 | LV_261-512_0_3_line_37 |  | 31 | 63 | 0.0098615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_261-512_0_3_line_38 |  | 32 | 33 | 0.014172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_261-512_0_3_line_39 |  | 32 | 34 | 0.048148 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_261-512_0_3_line_40 |  | 33 | 64 | 0.018623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_261-512_0_3_line_41 |  | 34 | 65 | 0.0034366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_261-512_0_3_line_42 |  | 35 | 36 | 0.0087939 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_261-512_0_3_line_43 |  | 35 | 37 | 0.024551 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_261-512_0_3_line_44 |  | 36 | 67 | 0.018261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_261-512_0_3_line_45 |  | 37 | 38 | 0.025132 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_261-512_0_3_line_46 |  | 38 | 39 | 0.002905 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_261-512_0_3_line_47 |  | 39 | 68 | 0.037234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_261-512_0_3_line_48 |  | 39 | 48 | 0.031935 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_261-512_0_3_line_49 |  | 40 | 41 | 0.038202 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_261-512_0_3_line_50 |  | 40 | 42 | 0.046118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_261-512_0_3_line_51 |  | 40 | 43 | 0.055486 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_261-512_0_3_line_52 |  | 42 | 53 | 0.008944 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_261-512_0_3_line_53 |  | 44 | 45 | 0.0084054 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_261-512_0_3_line_54 |  | 45 | 51 | 0.01626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_261-512_0_3_line_55 |  | 46 | 47 | 0.025709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_261-512_0_3_line_56 |  | 46 | 48 | 0.023419 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_261-512_0_3_line_57 |  | 46 | 49 | 0.0085178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_261-512_0_3_line_58 |  | 47 | 69 | 0.018795 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_261-512_0_3_line_59 |  | 48 | 50 | 0.015222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_261-512_0_3_line_60 |  | 49 | 51 | 0.0166 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_261-512_0_3_line_61 |  | 50 | 70 | 0.026457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_261-512_0_3_line_62 |  | 51 | 52 | 0.028473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_261-512_0_3_line_63 |  | 53 | 58 | 0.021111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_261-512_0_3_line_64 |  | 55 | 56 | 0.019055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_261-512_0_3_line_65 |  | 55 | 57 | 0.017259 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_261-512_0_3_line_66 |  | 56 | 75 | 0.0096397 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_261-512_0_3_line_67 |  | 57 | 74 | 0.093813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_261-512_0_3_line_68 |  | 61 | 62 | 0.023731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_261-512_0_3_line_69 |  | 63 | 64 | 0.014016 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_261-512_0_3_line_70 |  | 65 | 66 | 0.017004 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_261-512_0_3_line_71 |  | 67 | 76 | 0.0040008 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_261-512_0_3_line_72 |  | 68 | 77 | 0.0049037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_261-512_0_3_line_73 |  | 69 | 81 | 0.018705 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_261-512_0_3_line_74 |  | 70 | 78 | 0.023687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_261-512_0_3_line_75 |  | 71 | 72 | 0.019115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_261-512_0_3_line_76 |  | 72 | 81 | 0.031782 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_261-512_0_3_line_77 |  | 73 | 74 | 0.021533 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_261-512_0_3_line_78 |  | 74 | 76 | 0.011437 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_261-512_0_3_line_79 |  | 77 | 83 | 0.0052921 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_261-512_0_3_line_80 |  | 78 | 79 | 0.023435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_261-512_0_3_line_81 |  | 79 | 80 | 0.023474 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_261-512_0_3_line_82 |  | 80 | 82 | 0.023542 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_261-512_0_3_line_83 |  | 83 | 84 | 0.015257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_261-512_0_3_line_84 |  | 84 | 85 | 0.0099557 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-512_0_3_trafo_29 | 0.63 MVA 20/0.4 kV | 86 | 44 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2682809.1122 | 1251162.7858 | 2682830.071 | 1251217.6382
1 | 2682839.0982 | 1251241.2637 | 2682830.071 | 1251217.6382
2 | 2682839.0982 | 1251241.2637 | 2682840.9262 | 1251246.0372
3 | 2682826.2802 | 1251243.9866 | 2682827.6841 | 1251245.6185 | 2682833.6795 | 1251243.3339 | 2682839.0982 | 1251241.2637
4 | 2682840.9262 | 1251246.0372 | 2682868.3269 | 1251237.4812
5 | 2682850.596 | 1251271.4024 | 2682845.6012 | 1251258.2784 | 2682840.9262 | 1251246.0372
6 | 2682826.2802 | 1251243.9866 | 2682825.5741 | 1251244.2769 | 2682810.0806 | 1251250.465 | 2682807.8909 | 1251247.8102 | 2682802.7468 | 1251233.8997
7 | 2682926.1898 | 1251219.7055 | 2682916.938 | 1251222.5826 | 2682881.0417 | 1251233.5109 | 2682868.3269 | 1251237.4812
8 | 2682850.596 | 1251271.4024 | 2682853.2976 | 1251278.4788 | 2682864.7306 | 1251308.5267
9 | 2682850.596 | 1251271.4024 | 2682869.8824 | 1251263.643
10 | 2682855.3199 | 1251317.3806 | 2682852.3549 | 1251309.7112 | 2682859.7987 | 1251306.9576 | 2682853.693 | 1251292.3058 | 2682847.8335 | 1251280.5595 | 2682845.1835 | 1251273.5728 | 2682850.596 | 1251271.4024
11 | 2682855.3199 | 1251317.3806 | 2682863.3082 | 1251338.2417
12 | 2682817.5734 | 1251362.9648 | 2682819.3441 | 1251357.7968 | 2682829.8263 | 1251327.2316 | 2682855.3199 | 1251317.3806
13 | 2682806.9028 | 1251361.1254 | 2682808.7474 | 1251365.788 | 2682817.5734 | 1251362.9648
14 | 2682926.1898 | 1251219.7055 | 2682932.289 | 1251217.8088
15 | 2683017.4022 | 1251280.841 | 2683021.3076 | 1251279.6447
16 | 2683004.8636 | 1251284.682 | 2683017.4022 | 1251280.841
17 | 2683046.7197 | 1251281.342 | 2683042.6921 | 1251279.6859 | 2683034.3767 | 1251279.9919 | 2683030.6835 | 1251280.1291 | 2683028.6293 | 1251280.2004 | 2683024.5445 | 1251278.6531 | 2683021.3076 | 1251279.6447
18 | 2683004.8636 | 1251284.682 | 2682999.6674 | 1251268.3309
19 | 2683058.3709 | 1251286.1326 | 2683046.7197 | 1251281.342
20 | 2682996.9607 | 1251259.8136 | 2682999.6674 | 1251268.3309
21 | 2683061.7182 | 1251287.5139 | 2683058.3709 | 1251286.1326
22 | 2682996.9607 | 1251259.8136 | 2682990.7663 | 1251240.3216
23 | 2683061.7182 | 1251287.5139 | 2683063.1223 | 1251284.2867 | 2683076.4828 | 1251254.0104
24 | 2683117.6645 | 1251187.7905 | 2683122.8108 | 1251180.9353 | 2683118.1918 | 1251177.6458
25 | 2683117.6645 | 1251187.7905 | 2683131.3849 | 1251198.5676
26 | 2683116.2486 | 1251176.262 | 2683118.1918 | 1251177.6458
27 | 2683118.1918 | 1251177.6458 | 2683124.8821 | 1251169.7073
28 | 2683118.1918 | 1251177.6458 | 2683113.4982 | 1251184.5185 | 2683100.7382 | 1251204.599 | 2683095.6613 | 1251213.5844
29 | 2683135.696 | 1251201.9539 | 2683131.3849 | 1251198.5676
30 | 2683076.4828 | 1251254.0104 | 2683079.1519 | 1251247.9621 | 2683084.9833 | 1251234.7448
31 | 2683135.696 | 1251201.9539 | 2683147.029 | 1251189.8676
32 | 2682963.6932 | 1251208.1595 | 2682967.1585 | 1251216.214 | 2682974.3122 | 1251236.8629
33 | 2682974.3122 | 1251236.8629 | 2682959.7818 | 1251241.4734
34 | 2682963.6932 | 1251208.1595 | 2682940.8206 | 1251215.1557 | 2682932.289 | 1251217.8088
35 | 2682963.6932 | 1251208.1595 | 2682967.1585 | 1251216.214 | 2682972.6396 | 1251214.5451 | 2682974.2013 | 1251214.0666 | 2682975.2626 | 1251213.7479 | 2682983.6247 | 1251211.1964
36 | 2682963.6932 | 1251208.1595 | 2682961.3539 | 1251202.7116 | 2682959.1674 | 1251197.1324
37 | 2682959.7818 | 1251241.4734 | 2682950.3821 | 1251244.4558
38 | 2682964.4995 | 1251289.0867 | 2682960.2255 | 1251275.5747
39 | 2682964.4995 | 1251289.0867 | 2682947.8678 | 1251294.0799 | 2682955.1222 | 1251317.2432 | 2682961.3381 | 1251315.3085
40 | 2682954.609 | 1251257.8188 | 2682960.2255 | 1251275.5747
41 | 2682961.3381 | 1251315.3085 | 2682964.6194 | 1251314.2871
42 | 2683043.693 | 1251118.9355 | 2683042.1644 | 1251110.2755
43 | 2683043.693 | 1251118.9355 | 2683020.4964 | 1251126.978
44 | 2683042.1644 | 1251110.2755 | 2683041.8887 | 1251108.7137 | 2683038.7564 | 1251102.7543 | 2683046.731 | 1251096.8164
45 | 2682996.2621 | 1251133.5709 | 2683015.0568 | 1251128.864 | 2683020.4964 | 1251126.978
46 | 2682996.2621 | 1251133.5709 | 2682993.38 | 1251133.9976
47 | 2682993.38 | 1251133.9976 | 2682982.1988 | 1251098.4825
48 | 2682962.2927 | 1251141.0787 | 2682966.3678 | 1251141.1692 | 2682993.38 | 1251133.9976
49 | 2683012.9742 | 1251176.1923 | 2683016.0869 | 1251179.2382 | 2683028.8813 | 1251191.6823 | 2683033.7538 | 1251206.9208
50 | 2683012.9742 | 1251176.1923 | 2683001.3751 | 1251188.339 | 2682990.0098 | 1251200.5 | 2682986.3087 | 1251204.4289 | 2682983.6247 | 1251211.1964
51 | 2683012.9742 | 1251176.1923 | 2683036.9868 | 1251151.9773 | 2683051.6505 | 1251136.4132
52 | 2682983.6247 | 1251211.1964 | 2682985.1763 | 1251220.0048
53 | 2682959.1674 | 1251197.1324 | 2682957.7969 | 1251193.655 | 2682956.3928 | 1251189.2034
54 | 2682951.5015 | 1251173.6965 | 2682956.3928 | 1251189.2034
55 | 2682944.8277 | 1251149.485 | 2682943.2773 | 1251139.9896 | 2682940.667 | 1251127.477 | 2682939.708 | 1251124.3138
56 | 2682962.2927 | 1251141.0787 | 2682951.3183 | 1251140.4247 | 2682948.2873 | 1251148.7885 | 2682944.8277 | 1251149.485
57 | 2682944.8277 | 1251149.485 | 2682946.926 | 1251157.7403
58 | 2682934.255 | 1251106.3276 | 2682939.708 | 1251124.3138
59 | 2682962.2927 | 1251141.0787 | 2682958.3785 | 1251132.1951 | 2682956.5607 | 1251126.9895
60 | 2682951.5015 | 1251173.6965 | 2682947.3748 | 1251159.5059 | 2682946.926 | 1251157.7403
61 | 2682948.1313 | 1251101.9147 | 2682950.6562 | 1251110.0816 | 2682956.5607 | 1251126.9895
62 | 2682924.1147 | 1251181.7637 | 2682951.5015 | 1251173.6965
63 | 2682990.7663 | 1251240.3216 | 2682986.2539 | 1251226.1221 | 2682985.1763 | 1251220.0048
64 | 2682981.4733 | 1251006.458 | 2682976.8088 | 1251008.016 | 2682972.0431 | 1250994.7061
65 | 2682981.4733 | 1251006.458 | 2682980.2388 | 1251013.2124 | 2682982.8885 | 1251023.2616
66 | 2682972.0431 | 1250994.7061 | 2682969.8319 | 1250985.5016 | 2682969.8487 | 1250985.3291
67 | 2683050.5002 | 1251083.0041 | 2683050.447 | 1251080.3347 | 2683023.1504 | 1251060.9267 | 2682995.039 | 1251040.9292 | 2682986.1596 | 1251035.6676 | 2682982.8885 | 1251023.2616
68 | 2683095.6613 | 1251213.5844 | 2683089.537 | 1251224.4234 | 2683084.9833 | 1251234.7448
69 | 2682954.609 | 1251257.8188 | 2682950.3821 | 1251244.4558 | 2682950.3821 | 1251244.4558
70 | 2682980.8548 | 1251309.2338 | 2682964.6194 | 1251314.2871
71 | 2683046.731 | 1251096.8164 | 2683049.9399 | 1251094.427
72 | 2682982.1988 | 1251098.4825 | 2682980.7263 | 1251093.8052
73 | 2682928.8281 | 1251088.4275 | 2682934.255 | 1251106.3276
74 | 2682941.135 | 1251079.2849 | 2682948.1313 | 1251101.9147
75 | 2682914.061 | 1251039.7199 | 2682919.607 | 1251058.013
76 | 2682919.607 | 1251058.013 | 2682928.8281 | 1251088.4275
77 | 2683050.5002 | 1251083.0041 | 2683065.1374 | 1251067.2112
78 | 2683050.5002 | 1251083.0041 | 2683049.9399 | 1251094.427
79 | 2682979.137 | 1251088.7573 | 2682980.7263 | 1251093.8052
80 | 2682934.2131 | 1251056.8957 | 2682941.135 | 1251079.2849
81 | 2682927.243 | 1251034.4799 | 2682929.778 | 1251042.5502 | 2682934.2131 | 1251056.8957
82 | 2682920.1881 | 1251012.0204 | 2682927.243 | 1251034.4799
83 | 2682979.137 | 1251088.7573 | 2682974.5555 | 1251074.2048
84 | 2682974.5555 | 1251074.2048 | 2682971.5658 | 1251064.7086

## bus_geodata
| x | y | coords
0 | 2682809.1122 | 1251162.7858
1 | 2682830.071 | 1251217.6382
2 | 2682839.0982 | 1251241.2637
3 | 2682840.9262 | 1251246.0372
4 | 2682826.2802 | 1251243.9866
5 | 2682868.3269 | 1251237.4812
6 | 2682850.596 | 1251271.4024
7 | 2682864.7306 | 1251308.5267
8 | 2682869.8824 | 1251263.643
9 | 2682855.3199 | 1251317.3806
10 | 2682863.3082 | 1251338.2417
11 | 2682817.5734 | 1251362.9648
12 | 2682806.9028 | 1251361.1254
13 | 2682802.7468 | 1251233.8997
14 | 2682926.1898 | 1251219.7055
15 | 2683017.4022 | 1251280.841
16 | 2683021.3076 | 1251279.6447
17 | 2683004.8636 | 1251284.682
18 | 2683046.7197 | 1251281.342
19 | 2682999.6674 | 1251268.3309
20 | 2683058.3709 | 1251286.1326
21 | 2682996.9607 | 1251259.8136
22 | 2683061.7182 | 1251287.5139
23 | 2683117.6645 | 1251187.7905
24 | 2683118.1918 | 1251177.6458
25 | 2683131.3849 | 1251198.5676
26 | 2683076.4828 | 1251254.0104
27 | 2683135.696 | 1251201.9539
28 | 2683147.029 | 1251189.8676
29 | 2682974.3122 | 1251236.8629
30 | 2682963.6932 | 1251208.1595
31 | 2682959.7818 | 1251241.4734
32 | 2682964.4995 | 1251289.0867
33 | 2682960.2255 | 1251275.5747
34 | 2682961.3381 | 1251315.3085
35 | 2683043.693 | 1251118.9355
36 | 2683042.1644 | 1251110.2755
37 | 2683020.4964 | 1251126.978
38 | 2682996.2621 | 1251133.5709
39 | 2682993.38 | 1251133.9976
40 | 2683012.9742 | 1251176.1923
41 | 2683033.7538 | 1251206.9208
42 | 2682983.6247 | 1251211.1964
43 | 2683051.6505 | 1251136.4132
44 | 2682959.1674 | 1251197.1324
45 | 2682956.3928 | 1251189.2034
46 | 2682944.8277 | 1251149.485
47 | 2682939.708 | 1251124.3138
48 | 2682962.2927 | 1251141.0787
49 | 2682946.926 | 1251157.7403
50 | 2682956.5607 | 1251126.9895
51 | 2682951.5015 | 1251173.6965
52 | 2682924.1147 | 1251181.7637
53 | 2682985.1763 | 1251220.0048
54 | 2682932.289 | 1251217.8089
55 | 2682981.4733 | 1251006.458
56 | 2682972.0431 | 1250994.7061
57 | 2682982.8885 | 1251023.2616
58 | 2682990.7663 | 1251240.3216
59 | 2683116.2486 | 1251176.262
60 | 2683124.8821 | 1251169.7073
61 | 2683095.6613 | 1251213.5844
62 | 2683084.9833 | 1251234.7448
63 | 2682950.3821 | 1251244.4558
64 | 2682954.609 | 1251257.8188
65 | 2682964.6194 | 1251314.2871
66 | 2682980.8548 | 1251309.2338
67 | 2683046.731 | 1251096.8164
68 | 2682982.1988 | 1251098.4825
69 | 2682934.255 | 1251106.3276
70 | 2682948.1313 | 1251101.9147
71 | 2682914.061 | 1251039.7199
72 | 2682919.607 | 1251058.013
73 | 2683065.1374 | 1251067.2112
74 | 2683050.5002 | 1251083.0041
75 | 2682969.8487 | 1250985.3291
76 | 2683049.9399 | 1251094.427
77 | 2682980.7263 | 1251093.8052
78 | 2682941.135 | 1251079.2849
79 | 2682934.2131 | 1251056.8957
80 | 2682927.243 | 1251034.4799
81 | 2682928.8281 | 1251088.4275
82 | 2682920.1881 | 1251012.0204
83 | 2682979.137 | 1251088.7573
84 | 2682974.5555 | 1251074.2048
85 | 2682971.5658 | 1251064.7086
86 | 2682962.8373 | 1251196.5055

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98379 | -0.31194 | 0.025867 | 0.0064829
1 | 0.98519 | -0.28462 | 0.017559 | 0.0044007
2 | 0.9862 | -0.26492 | 0 | 0
3 | 0.98648 | -0.25953 | 0 | 0
4 | 0.986 | -0.26889 | 0 | 0
5 | 0.98908 | -0.20909 | 0.0051549 | 0.0012919
6 | 0.98549 | -0.27875 | 0 | 0
7 | 0.98528 | -0.28288 | 0.0057879 | 0.0014506
8 | 0.98511 | -0.28613 | 0.019789 | 0.0049597
9 | 0.98474 | -0.29337 | 0 | 0
10 | 0.98464 | -0.29525 | 0.0046751 | 0.0011717
11 | 0.98419 | -0.3042 | 0 | 0
12 | 0.98406 | -0.30657 | 0.0092448 | 0.002317
13 | 0.98549 | -0.27878 | 0.01543 | 0.0038672
14 | 0.99485 | -0.09809 | 0.0014503 | 0.00036348
15 | 0.9916 | -0.16101 | 0.0055654 | 0.0013948
16 | 0.99144 | -0.16424 | 0.0022759 | 0.0005704
17 | 0.99221 | -0.14934 | 0 | 0
18 | 0.99042 | -0.18394 | 0.0031172 | 0.00078125
19 | 0.993 | -0.1341 | 0.0056687 | 0.0014207
20 | 0.98996 | -0.19273 | 0 | 0
21 | 0.99346 | -0.12528 | 0.0074353 | 0.0018635
22 | 0.98983 | -0.19525 | 0 | 0
23 | 0.98661 | -0.25784 | 0 | 0
24 | 0.98673 | -0.25558 | 0 | 0
25 | 0.98647 | -0.2606 | 0.0060483 | 0.0015158
26 | 0.98851 | -0.22085 | 0.010511 | 0.0026342
27 | 0.98646 | -0.26088 | 0 | 0
28 | 0.98641 | -0.26171 | 0.0027987 | 0.00070142
29 | 0.99739 | -0.049957 | 0 | 0
30 | 0.99869 | -0.024991 | 0 | 0
31 | 0.99674 | -0.06241 | 0.004437 | 0.001112
32 | 0.99497 | -0.096558 | 0 | 0
33 | 0.99532 | -0.089682 | 0.0050759 | 0.0012722
34 | 0.99376 | -0.11995 | 0.010204 | 0.0025573
35 | 0.99219 | -0.15024 | 0 | 0
36 | 0.99203 | -0.15344 | 0.00093143 | 0.00023344
37 | 0.99265 | -0.14132 | 0.0070834 | 0.0017753
38 | 0.99329 | -0.12905 | 0 | 0
39 | 0.99336 | -0.12764 | 0 | 0
40 | 0.99616 | -0.073457 | 0 | 0
41 | 0.9959 | -0.078363 | 0.0073097 | 0.001832
42 | 0.99661 | -0.064714 | 0 | 0
43 | 0.99598 | -0.076854 | 0.0034847 | 0.00087335
44 | 1 | 0 | -0.35262 | -0.089096
45 | 0.99917 | -0.015795 | 0.009813 | 0.0024594
46 | 0.99572 | -0.082162 | 0 | 0
47 | 0.99519 | -0.092361 | 0.0077665 | 0.0019465
48 | 0.99445 | -0.10666 | 0 | 0
49 | 0.99635 | -0.069895 | 0.0082662 | 0.0020717
50 | 0.99414 | -0.11261 | 0.011198 | 0.0028065
51 | 0.99772 | -0.043631 | 0 | 0
52 | 0.99752 | -0.047457 | 0.0076732 | 0.0019231
53 | 0.99598 | -0.076729 | 0.0073051 | 0.0018308
54 | 0.99547 | -0.08629 | 0.0014498 | 0.00036334
55 | 0.99058 | -0.18155 | 0 | 0
56 | 0.99051 | -0.18287 | 0.0023837 | 0.00059741
57 | 0.99064 | -0.18035 | 0.0056348 | 0.0014122
58 | 0.99464 | -0.10243 | 0.0058732 | 0.001472
59 | 0.98672 | -0.2557 | 0.0028151 | 0.00070553
60 | 0.98667 | -0.2568 | 0.0065539 | 0.0016426
61 | 0.98744 | -0.24175 | 0.0055941 | 0.001402
62 | 0.98796 | -0.23166 | 0.0049321 | 0.0012361
63 | 0.99636 | -0.069706 | 0.0044342 | 0.0011113
64 | 0.99588 | -0.078993 | 0.0050788 | 0.0012729
65 | 0.9937 | -0.12101 | 0.0086817 | 0.0021758
66 | 0.99357 | -0.12361 | 0.0086779 | 0.0021749
67 | 0.9917 | -0.15978 | 0.0010745 | 0.0002693
68 | 0.99303 | -0.13397 | 0.001617 | 0.00040526
69 | 0.99494 | -0.097253 | 0.0073677 | 0.0018465
70 | 0.99387 | -0.11773 | 0.0021956 | 0.00055026
71 | 0.99462 | -0.1033 | 0.0024698 | 0.00061898
72 | 0.99467 | -0.10247 | 0.0024768 | 0.00062075
73 | 0.99132 | -0.16718 | 0.0070956 | 0.0017783
74 | 0.99146 | -0.16447 | 0 | 0
75 | 0.99049 | -0.18313 | 0.0015194 | 0.00038079
76 | 0.99163 | -0.16109 | 0.0018842 | 0.00047223
77 | 0.993 | -0.13466 | 0.0031513 | 0.0007898
78 | 0.99368 | -0.1214 | 0.0021962 | 0.00055042
79 | 0.99354 | -0.12413 | 0.0021949 | 0.0005501
80 | 0.99345 | -0.12595 | 0.002196 | 0.00055038
81 | 0.99481 | -0.099696 | 0.0024697 | 0.00061895
82 | 0.9934 | -0.12686 | 0.0021946 | 0.00055003
83 | 0.99297 | -0.13511 | 0.0016171 | 0.00040528
84 | 0.99293 | -0.13599 | 0.0016161 | 0.00040504
85 | 0.99291 | -0.13627 | 0.001617 | 0.00040525
86 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.025867 | -0.0064829 | 0.025901 | 0.0065037 | 3.3707e-05 | 2.0826e-05 | 0.039125 | 0.039125 | 0.039125 | 0.98379 | -0.31194 | 0.98519 | -0.28462 | 10.7486
1 | -0.04346 | -0.010904 | 0.043501 | 0.01093 | 4.0871e-05 | 2.5835e-05 | 0.065645 | 0.065645 | 0.065645 | 0.98519 | -0.28462 | 0.9862 | -0.26492 | 18.0345
2 | -0.058941 | -0.014803 | 0.058956 | 0.014813 | 1.5159e-05 | 9.6368e-06 | 0.088944 | 0.088944 | 0.088944 | 0.9862 | -0.26492 | 0.98648 | -0.25953 | 24.435
3 | 0.01544 | 0.0038731 | -0.015437 | -0.0038714 | 2.9249e-06 | 1.6887e-06 | 0.023298 | 0.023298 | 0.023298 | 0.9862 | -0.26492 | 0.986 | -0.26889 | 6.4006
4 | -0.098513 | -0.024747 | 0.098751 | 0.024899 | 0.00023776 | 0.0001518 | 0.14862 | 0.14862 | 0.14862 | 0.98648 | -0.25953 | 0.98908 | -0.20909 | 40.8296
5 | 0.039557 | 0.0099343 | -0.039521 | -0.0099115 | 3.6241e-05 | 2.2848e-05 | 0.059676 | 0.059676 | 0.059676 | 0.98648 | -0.25953 | 0.98549 | -0.27875 | 16.3946
6 | 0.015437 | 0.0038714 | -0.01543 | -0.0038672 | 7.2709e-06 | 4.198e-06 | 0.023298 | 0.023298 | 0.023298 | 0.986 | -0.26889 | 0.98549 | -0.27878 | 6.4007
7 | -0.10391 | -0.026191 | 0.10446 | 0.026545 | 0.00055507 | 0.00035447 | 0.15637 | 0.15637 | 0.15637 | 0.98908 | -0.20909 | 0.99485 | -0.09809 | 42.9601
8 | 0.005789 | 0.0014508 | -0.0057879 | -0.0014506 | 1.1382e-06 | 2.2241e-07 | 0.008741 | 0.0087411 | 0.0087411 | 0.98549 | -0.27875 | 0.98528 | -0.28288 | 2.4014
9 | 0.019796 | 0.0049638 | -0.019789 | -0.0049597 | 6.9657e-06 | 4.1932e-06 | 0.029892 | 0.029892 | 0.029892 | 0.98549 | -0.27875 | 0.98511 | -0.28613 | 8.212
10 | 0.013936 | 0.0034968 | -0.013926 | -0.0034914 | 9.7087e-06 | 5.4692e-06 | 0.021044 | 0.021044 | 0.021044 | 0.98549 | -0.27875 | 0.98474 | -0.29337 | 5.7813
11 | 0.0046755 | 0.0011717 | -0.0046751 | -0.0011717 | 4.1813e-07 | -1.6553e-08 | 0.007065 | 0.0070651 | 0.0070651 | 0.98474 | -0.29337 | 0.98464 | -0.29525 | 1.941
12 | 0.0092507 | 0.0023197 | -0.0092459 | -0.0023175 | 4.771e-06 | 2.2256e-06 | 0.013979 | 0.013979 | 0.013979 | 0.98474 | -0.29337 | 0.98419 | -0.3042 | 3.8404
13 | 0.0092459 | 0.0023175 | -0.0092448 | -0.002317 | 1.0446e-06 | 4.8744e-07 | 0.013979 | 0.013979 | 0.013979 | 0.98419 | -0.3042 | 0.98406 | -0.30657 | 3.8405
14 | -0.10591 | -0.026909 | 0.10597 | 0.026947 | 6.0206e-05 | 3.8449e-05 | 0.15854 | 0.15854 | 0.15854 | 0.99485 | -0.09809 | 0.99547 | -0.08629 | 43.556
15 | 0.044803 | 0.011287 | -0.044796 | -0.011283 | 6.9278e-06 | 4.3811e-06 | 0.067253 | 0.067253 | 0.067253 | 0.9916 | -0.16101 | 0.99144 | -0.16424 | 18.4761
16 | -0.050369 | -0.012682 | 0.050397 | 0.0127 | 2.811e-05 | 1.7821e-05 | 0.075605 | 0.075605 | 0.075605 | 0.9916 | -0.16101 | 0.99221 | -0.14934 | 20.7705
17 | 0.04252 | 0.010712 | -0.04248 | -0.010687 | 4.0009e-05 | 2.5268e-05 | 0.063837 | 0.063837 | 0.063837 | 0.99144 | -0.16424 | 0.99042 | -0.18394 | 17.5377
18 | -0.050397 | -0.0127 | 0.050434 | 0.012723 | 3.6776e-05 | 2.3315e-05 | 0.075605 | 0.075604 | 0.075605 | 0.99221 | -0.14934 | 0.993 | -0.1341 | 20.7705
19 | 0.039363 | 0.0099056 | -0.039347 | -0.0098952 | 1.6531e-05 | 1.0418e-05 | 0.059154 | 0.059154 | 0.059154 | 0.99042 | -0.18394 | 0.98996 | -0.19273 | 16.2511
20 | -0.056102 | -0.014144 | 0.056126 | 0.014159 | 2.3703e-05 | 1.5054e-05 | 0.084099 | 0.084099 | 0.084099 | 0.993 | -0.1341 | 0.99346 | -0.12528 | 23.1041
21 | 0.039347 | 0.0098952 | -0.039342 | -0.0098922 | 4.7397e-06 | 2.987e-06 | 0.059154 | 0.059154 | 0.059154 | 0.98996 | -0.19273 | 0.98983 | -0.19525 | 16.2511
22 | -0.063561 | -0.016022 | 0.063631 | 0.016066 | 6.9563e-05 | 4.4255e-05 | 0.095236 | 0.095236 | 0.095236 | 0.99346 | -0.12528 | 0.99464 | -0.10243 | 26.1637
23 | 0.039342 | 0.0098922 | -0.039294 | -0.009862 | 4.8043e-05 | 3.0278e-05 | 0.059154 | 0.059154 | 0.059154 | 0.98983 | -0.19525 | 0.98851 | -0.22085 | 16.2512
24 | -0.0088483 | -0.0022176 | 0.0088493 | 0.002218 | 9.5117e-07 | 4.2685e-07 | 0.013345 | 0.013345 | 0.013345 | 0.98661 | -0.25784 | 0.98673 | -0.25558 | 3.6662
25 | 0.0088483 | 0.0022176 | -0.0088472 | -0.0022171 | 1.1652e-06 | 5.2295e-07 | 0.013345 | 0.013345 | 0.013345 | 0.98661 | -0.25784 | 0.98647 | -0.2606 | 3.6663
26 | 0.0028151 | 0.00070551 | -0.0028151 | -0.00070553 | 1.6092e-08 | -2.0115e-08 | 0.0042453 | 0.0042453 | 0.0042453 | 0.98673 | -0.25558 | 0.98672 | -0.2557 | 1.1663
27 | 0.0065543 | 0.0016427 | -0.0065539 | -0.0016426 | 3.8034e-07 | 1.1081e-07 | 0.009884 | 0.0098841 | 0.0098841 | 0.98673 | -0.25558 | 0.98667 | -0.2568 | 2.7154
28 | -0.018219 | -0.0045662 | 0.018231 | 0.0045734 | 1.2012e-05 | 7.145e-06 | 0.027474 | 0.027474 | 0.027474 | 0.98673 | -0.25558 | 0.98744 | -0.24175 | 7.5479
29 | 0.0027988 | 0.00070123 | -0.0027988 | -0.00070128 | 3.6641e-08 | -4.6536e-08 | 0.0042218 | 0.0042218 | 0.0042218 | 0.98647 | -0.2606 | 0.98646 | -0.26088 | 1.1598
30 | 0.028783 | 0.0072277 | -0.028768 | -0.0072185 | 1.4827e-05 | 9.2197e-06 | 0.043332 | 0.043332 | 0.043332 | 0.98851 | -0.22085 | 0.98796 | -0.23166 | 11.9045
31 | 0.0027988 | 0.00070128 | -0.0027987 | -0.00070142 | 1.1074e-07 | -1.4064e-07 | 0.0042218 | 0.0042219 | 0.0042219 | 0.98646 | -0.26088 | 0.98641 | -0.26171 | 1.1599
32 | -0.046707 | -0.01175 | 0.046763 | 0.011785 | 5.5782e-05 | 3.5301e-05 | 0.069698 | 0.069698 | 0.069698 | 0.99739 | -0.049957 | 0.99869 | -0.024991 | 19.1479
33 | 0.046707 | 0.01175 | -0.046679 | -0.011732 | 2.777e-05 | 1.7574e-05 | 0.069698 | 0.069698 | 0.069698 | 0.99739 | -0.049957 | 0.99674 | -0.06241 | 19.1479
34 | 0.10774 | 0.027514 | -0.10742 | -0.027311 | 0.0003182 | 0.00020322 | 0.16071 | 0.16071 | 0.16071 | 0.99869 | -0.024991 | 0.99547 | -0.08629 | 44.1513
35 | 0.087908 | 0.022267 | -0.08774 | -0.02216 | 0.00016737 | 0.00010677 | 0.13106 | 0.13106 | 0.13106 | 0.99869 | -0.024991 | 0.99661 | -0.064714 | 36.0063
36 | -0.24241 | -0.061566 | 0.2427 | 0.061752 | 0.00029196 | 0.00018654 | 0.36147 | 0.36147 | 0.36147 | 0.99869 | -0.024991 | 1 | 0 | 49.6527
37 | 0.042242 | 0.01062 | -0.042227 | -0.010611 | 1.4712e-05 | 9.2874e-06 | 0.063074 | 0.063074 | 0.063074 | 0.99674 | -0.06241 | 0.99636 | -0.069706 | 17.3281
38 | -0.027596 | -0.006928 | 0.027605 | 0.0069336 | 9.0539e-06 | 5.6103e-06 | 0.041275 | 0.041275 | 0.041275 | 0.99497 | -0.096558 | 0.99532 | -0.089682 | 11.3393
39 | 0.027596 | 0.006928 | -0.027565 | -0.006909 | 3.076e-05 | 1.9062e-05 | 0.041275 | 0.041275 | 0.041275 | 0.99497 | -0.096558 | 0.99376 | -0.11995 | 11.3394
40 | -0.032681 | -0.0082058 | 0.032698 | 0.0082162 | 1.6675e-05 | 1.043e-05 | 0.048864 | 0.048864 | 0.048864 | 0.99532 | -0.089682 | 0.99588 | -0.078993 | 13.4241
41 | 0.017362 | 0.0043517 | -0.017361 | -0.0043512 | 8.7097e-07 | 5.129e-07 | 0.025997 | 0.025997 | 0.025997 | 0.99376 | -0.11995 | 0.9937 | -0.12101 | 7.142
42 | 0.020545 | 0.0051548 | -0.020542 | -0.005153 | 3.1312e-06 | 1.8904e-06 | 0.030814 | 0.030814 | 0.030814 | 0.99219 | -0.15024 | 0.99203 | -0.15344 | 8.4654
43 | -0.020545 | -0.0051548 | 0.020554 | 0.0051601 | 8.7418e-06 | 5.2776e-06 | 0.030814 | 0.030814 | 0.030814 | 0.99219 | -0.15024 | 0.99265 | -0.14132 | 8.4654
44 | 0.019611 | 0.0049195 | -0.019605 | -0.004916 | 5.9259e-06 | 3.5569e-06 | 0.029417 | 0.029417 | 0.029417 | 0.99203 | -0.15344 | 0.9917 | -0.15978 | 8.0816
45 | -0.027637 | -0.0069354 | 0.027653 | 0.0069454 | 1.6179e-05 | 1.0029e-05 | 0.041432 | 0.041432 | 0.041432 | 0.99265 | -0.14132 | 0.99329 | -0.12905 | 11.3825
46 | -0.027653 | -0.0069454 | 0.027655 | 0.0069466 | 1.87e-06 | 1.1592e-06 | 0.041432 | 0.041432 | 0.041432 | 0.99329 | -0.12905 | 0.99336 | -0.12764 | 11.3825
47 | 0.009622 | 0.0024119 | -0.0096191 | -0.0024105 | 2.9007e-06 | 1.3746e-06 | 0.014413 | 0.014414 | 0.014414 | 0.99336 | -0.12764 | 0.99303 | -0.13397 | 3.9598
48 | -0.037277 | -0.0093585 | 0.037315 | 0.009382 | 3.7349e-05 | 2.3489e-05 | 0.055846 | 0.055846 | 0.055846 | 0.99336 | -0.12764 | 0.99445 | -0.10666 | 15.3422
49 | 0.0073114 | 0.0018326 | -0.0073097 | -0.001832 | 1.7088e-06 | 5.9642e-07 | 0.010922 | 0.010922 | 0.010922 | 0.99616 | -0.073457 | 0.9959 | -0.078363 | 3.0005
50 | -0.010797 | -0.0027056 | 0.010801 | 0.0027078 | 4.4981e-06 | 2.2781e-06 | 0.016128 | 0.016127 | 0.016128 | 0.99616 | -0.073457 | 0.99661 | -0.064714 | 4.4306
51 | 0.0034853 | 0.00087299 | -0.0034847 | -0.00087335 | 5.6395e-07 | -3.613e-07 | 0.005206 | 0.0052062 | 0.0052062 | 0.99616 | -0.073457 | 0.99598 | -0.076854 | 1.4303
52 | 0.076939 | 0.019452 | -0.076895 | -0.019424 | 4.4307e-05 | 2.824e-05 | 0.11494 | 0.11494 | 0.11494 | 0.99661 | -0.064714 | 0.99598 | -0.076729 | 31.5758
53 | 0.10827 | 0.027344 | -0.10818 | -0.027292 | 8.1883e-05 | 5.2295e-05 | 0.16118 | 0.16118 | 0.16118 | 1 | 0 | 0.99917 | -0.015795 | 44.2793
54 | 0.098372 | 0.024832 | -0.098241 | -0.024749 | 0.00013098 | 8.3614e-05 | 0.14656 | 0.14656 | 0.14656 | 0.99917 | -0.015795 | 0.99772 | -0.043631 | 40.2645
55 | 0.022566 | 0.0056605 | -0.022556 | -0.0056538 | 1.0965e-05 | 6.6836e-06 | 0.033725 | 0.033726 | 0.033726 | 0.99572 | -0.082162 | 0.99519 | -0.092361 | 9.2653
56 | 0.059572 | 0.01499 | -0.059502 | -0.014946 | 6.9635e-05 | 4.4262e-05 | 0.089046 | 0.089046 | 0.089046 | 0.99572 | -0.082162 | 0.99445 | -0.10666 | 24.4632
57 | -0.082138 | -0.02065 | 0.082186 | 0.020681 | 4.8145e-05 | 3.0702e-05 | 0.12277 | 0.12277 | 0.12277 | 0.99572 | -0.082162 | 0.99635 | -0.069895 | 33.7284
58 | 0.014789 | 0.0037073 | -0.014786 | -0.0037053 | 3.4464e-06 | 1.9615e-06 | 0.022113 | 0.022113 | 0.022113 | 0.99519 | -0.092361 | 0.99494 | -0.097253 | 6.075
59 | 0.022187 | 0.0055635 | -0.022181 | -0.0055597 | 6.2919e-06 | 3.8294e-06 | 0.033201 | 0.033201 | 0.033201 | 0.99445 | -0.10666 | 0.99414 | -0.11261 | 9.1211
60 | -0.090453 | -0.022753 | 0.090566 | 0.022825 | 0.00011365 | 7.2518e-05 | 0.13512 | 0.13512 | 0.13512 | 0.99635 | -0.069895 | 0.99772 | -0.043631 | 37.12
61 | 0.010983 | 0.0027532 | -0.01098 | -0.0027518 | 2.6813e-06 | 1.3731e-06 | 0.016439 | 0.016439 | 0.016439 | 0.99414 | -0.11261 | 0.99387 | -0.11773 | 4.5163
62 | 0.0076746 | 0.0019236 | -0.0076732 | -0.0019231 | 1.3989e-06 | 5.2352e-07 | 0.011446 | 0.011446 | 0.011446 | 0.99772 | -0.043631 | 0.99752 | -0.047457 | 3.1446
63 | 0.06959 | 0.017593 | -0.069504 | -0.017538 | 8.5661e-05 | 5.4549e-05 | 0.10402 | 0.10402 | 0.10402 | 0.99598 | -0.076729 | 0.99464 | -0.10243 | 28.5775
64 | 0.0039033 | 0.000978 | -0.0039031 | -0.00097809 | 2.4567e-07 | -8.8057e-08 | 0.0058634 | 0.0058635 | 0.0058635 | 0.99058 | -0.18155 | 0.99051 | -0.18287 | 1.6108
65 | -0.0039033 | -0.000978 | 0.0039036 | 0.00097792 | 2.2251e-07 | -7.9789e-08 | 0.0058634 | 0.0058633 | 0.0058634 | 0.99058 | -0.18155 | 0.99064 | -0.18035 | 1.6108
66 | 0.0015194 | 0.00038068 | -0.0015194 | -0.00038079 | 1.8833e-08 | -1.1202e-07 | 0.0022825 | 0.0022825 | 0.0022825 | 0.99051 | -0.18287 | 0.99049 | -0.18313 | 0.62707
67 | -0.0095383 | -0.0023901 | 0.0095456 | 0.0023935 | 7.2211e-06 | 3.4127e-06 | 0.014327 | 0.014327 | 0.014327 | 0.99064 | -0.18035 | 0.99146 | -0.16447 | 3.936
68 | -0.023825 | -0.0059754 | 0.023836 | 0.0059824 | 1.1472e-05 | 7.0382e-06 | 0.035904 | 0.035904 | 0.035904 | 0.98744 | -0.24175 | 0.98796 | -0.23166 | 9.8638
69 | 0.037793 | 0.0094996 | -0.037776 | -0.0094891 | 1.6749e-05 | 1.0537e-05 | 0.056452 | 0.056452 | 0.056452 | 0.99636 | -0.069706 | 0.99588 | -0.078993 | 15.5088
70 | 0.008679 | 0.0021754 | -0.0086779 | -0.0021749 | 1.077e-06 | 4.6905e-07 | 0.012996 | 0.012996 | 0.012996 | 0.9937 | -0.12101 | 0.99357 | -0.12361 | 3.5705
71 | 0.01853 | 0.0046467 | -0.018529 | -0.004646 | 1.1599e-06 | 6.9071e-07 | 0.027805 | 0.027805 | 0.027805 | 0.9917 | -0.15978 | 0.99163 | -0.16109 | 7.6387
72 | 0.0080021 | 0.0020053 | -0.0080018 | -0.0020051 | 2.6439e-07 | 1.0577e-07 | 0.011991 | 0.011991 | 0.011991 | 0.99303 | -0.13397 | 0.993 | -0.13466 | 3.2941
73 | 0.0074179 | 0.0018588 | -0.007417 | -0.0018585 | 8.633e-07 | 3.0963e-07 | 0.011094 | 0.011094 | 0.011094 | 0.99494 | -0.097253 | 0.99481 | -0.099696 | 3.0478
74 | 0.0087847 | 0.0022015 | -0.0087831 | -0.0022009 | 1.5365e-06 | 6.7648e-07 | 0.013152 | 0.013152 | 0.013152 | 0.99387 | -0.11773 | 0.99368 | -0.1214 | 3.6133
75 | -0.0024698 | -0.00061898 | 0.0024699 | 0.0006188 | 9.7862e-08 | -1.8547e-07 | 0.0036949 | 0.0036949 | 0.0036949 | 0.99462 | -0.1033 | 0.99467 | -0.10247 | 1.0151
76 | -0.0049467 | -0.0012396 | 0.0049474 | 0.0012396 | 6.5265e-07 | 5.1221e-09 | 0.0074002 | 0.0074 | 0.0074002 | 0.99467 | -0.10247 | 0.99481 | -0.099696 | 2.033
77 | -0.0070956 | -0.0017783 | 0.0070965 | 0.0017786 | 9.16e-07 | 3.0859e-07 | 0.010651 | 0.010651 | 0.010651 | 0.99132 | -0.16718 | 0.99146 | -0.16447 | 2.9261
78 | -0.016642 | -0.0041722 | 0.016645 | 0.0041737 | 2.6756e-06 | 1.5649e-06 | 0.024977 | 0.024977 | 0.024977 | 0.99146 | -0.16447 | 0.99163 | -0.16109 | 6.8619
79 | 0.0048505 | 0.0012154 | -0.0048504 | -0.0012154 | 1.0484e-07 | -1.3587e-09 | 0.0072684 | 0.0072684 | 0.0072684 | 0.993 | -0.13466 | 0.99297 | -0.13511 | 1.9968
80 | 0.0065869 | 0.0016504 | -0.0065861 | -0.0016502 | 8.5501e-07 | 2.4367e-07 | 0.0098636 | 0.0098637 | 0.0098637 | 0.99368 | -0.1214 | 0.99354 | -0.12413 | 2.7098
81 | 0.0043911 | 0.0011001 | -0.0043908 | -0.0011002 | 3.8072e-07 | -6.0312e-08 | 0.0065764 | 0.0065765 | 0.0065765 | 0.99354 | -0.12413 | 0.99345 | -0.12595 | 1.8067
82 | 0.0021947 | 0.00054978 | -0.0021946 | -0.00055003 | 9.5399e-08 | -2.4375e-07 | 0.0032872 | 0.0032873 | 0.0032873 | 0.99345 | -0.12595 | 0.9934 | -0.12686 | 0.90312
83 | 0.0032333 | 0.00081007 | -0.0032331 | -0.00081018 | 1.3431e-07 | -1.1139e-07 | 0.0048451 | 0.0048452 | 0.0048452 | 0.99297 | -0.13511 | 0.99293 | -0.13599 | 1.3311
84 | 0.001617 | 0.00040514 | -0.001617 | -0.00040525 | 2.1923e-08 | -1.1474e-07 | 0.0024232 | 0.0024233 | 0.0024233 | 0.99293 | -0.13599 | 0.99291 | -0.13627 | 0.66573

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.35262 | 0.089096

## res_load
| p_mw | q_mvar
0 | 0.025867 | 0.0064829
1 | 0.017559 | 0.0044007
2 | 0.0051549 | 0.0012919
3 | 0.0057879 | 0.0014506
4 | 0.019789 | 0.0049597
5 | 0.0046751 | 0.0011717
6 | 0.0092448 | 0.002317
7 | 0.01543 | 0.0038672
8 | 0.0014503 | 0.00036348
9 | 0.0055654 | 0.0013948
10 | 0.0022759 | 0.0005704
11 | 0.0031172 | 0.00078125
12 | 0.0056687 | 0.0014207
13 | 0.0074353 | 0.0018635
14 | 0.0060483 | 0.0015158
15 | 0.010511 | 0.0026342
16 | 0.0027987 | 0.00070142
17 | 0.004437 | 0.001112
18 | 0.0050759 | 0.0012722
19 | 0.010204 | 0.0025573
20 | 0.00093143 | 0.00023344
21 | 0.0070834 | 0.0017753
22 | 0.0073097 | 0.001832
23 | 0.0034847 | 0.00087335
24 | 0.009813 | 0.0024594
25 | 0.0077665 | 0.0019465
26 | 0.0082662 | 0.0020717
27 | 0.011198 | 0.0028065
28 | 0.0076732 | 0.0019231
29 | 0.0073051 | 0.0018308
30 | 0.0014498 | 0.00036334
31 | 0.0023837 | 0.00059741
32 | 0.0056348 | 0.0014122
33 | 0.0058732 | 0.001472
34 | 0.0028151 | 0.00070553
35 | 0.0065539 | 0.0016426
36 | 0.0055941 | 0.001402
37 | 0.0049321 | 0.0012361
38 | 0.0044342 | 0.0011113
39 | 0.0050788 | 0.0012729
40 | 0.0086817 | 0.0021758
41 | 0.0086779 | 0.0021749
42 | 0.0010745 | 0.0002693
43 | 0.001617 | 0.00040526
44 | 0.0073677 | 0.0018465
45 | 0.0021956 | 0.00055026
46 | 0.0024698 | 0.00061898
47 | 0.0024768 | 0.00062075
48 | 0.0070956 | 0.0017783
49 | 0.0015194 | 0.00038079
50 | 0.0018842 | 0.00047223
51 | 0.0031513 | 0.0007898
52 | 0.0021962 | 0.00055042
53 | 0.0021949 | 0.0005501
54 | 0.002196 | 0.00055038
55 | 0.0024697 | 0.00061895
56 | 0.0021946 | 0.00055003
57 | 0.0016171 | 0.00040528
58 | 0.0016161 | 0.00040504
59 | 0.001617 | 0.00040525

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1