## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-51_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-51_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-51_0_6_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_261-51_0_6_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_261-51_0_6_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_261-51_0_6_node_35 | 0.4 | n |  | TRUE
6 | bus_LV_261-51_0_6_node_76 | 0.4 | n |  | TRUE
7 | bus_LV_261-51_0_6_node_78 | 0.4 | n |  | TRUE
8 | bus_LV_261-51_0_6_node_79 | 0.4 | n |  | TRUE
9 | bus_LV_261-51_0_6_node_32 | 0.4 | n |  | TRUE
10 | bus_LV_261-51_0_6_node_75 | 0.4 | n |  | TRUE
11 | bus_LV_261-51_0_6_node_5 | 0.4 | n |  | TRUE
12 | bus_LV_261-51_0_6_node_6 | 0.4 | n |  | TRUE
13 | bus_LV_261-51_0_6_node_7 | 0.4 | n |  | TRUE
14 | bus_LV_261-51_0_6_node_8 | 0.4 | n |  | TRUE
15 | bus_LV_261-51_0_6_node_9 | 0.4 | n |  | TRUE
16 | bus_LV_261-51_0_6_node_77 | 0.4 | n |  | TRUE
17 | bus_LV_261-51_0_6_node_10 | 0.4 | n |  | TRUE
18 | bus_LV_261-51_0_6_node_41 | 0.4 | n |  | TRUE
19 | bus_LV_261-51_0_6_node_11 | 0.4 | n |  | TRUE
20 | bus_LV_261-51_0_6_node_12 | 0.4 | n |  | TRUE
21 | bus_LV_261-51_0_6_node_13 | 0.4 | n |  | TRUE
22 | bus_LV_261-51_0_6_node_14 | 0.4 | n |  | TRUE
23 | bus_LV_261-51_0_6_node_15 | 0.4 | n |  | TRUE
24 | bus_LV_261-51_0_6_node_16 | 0.4 | n |  | TRUE
25 | bus_LV_261-51_0_6_node_69 | 0.4 | n |  | TRUE
26 | bus_LV_261-51_0_6_node_143 | 0.4 | n |  | TRUE
27 | bus_LV_261-51_0_6_node_61 | 0.4 | n |  | TRUE
28 | bus_LV_261-51_0_6_node_82 | 0.4 | n |  | TRUE
29 | bus_LV_261-51_0_6_node_18 | 0.4 | n |  | TRUE
30 | bus_LV_261-51_0_6_node_60 | 0.4 | n |  | TRUE
31 | bus_LV_261-51_0_6_node_148 | 0.4 | n |  | TRUE
32 | bus_LV_261-51_0_6_node_50 | 0.4 | n |  | TRUE
33 | bus_LV_261-51_0_6_node_104 | 0.4 | n |  | TRUE
34 | bus_LV_261-51_0_6_node_102 | 0.4 | n |  | TRUE
35 | bus_LV_261-51_0_6_node_19 | 0.4 | n |  | TRUE
36 | bus_LV_261-51_0_6_node_28 | 0.4 | n |  | TRUE
37 | bus_LV_261-51_0_6_node_118 | 0.4 | n |  | TRUE
38 | bus_LV_261-51_0_6_node_22 | 0.4 | n |  | TRUE
39 | bus_LV_261-51_0_6_node_25 | 0.4 | n |  | TRUE
40 | bus_LV_261-51_0_6_node_38 | 0.4 | n |  | TRUE
41 | bus_LV_261-51_0_6_node_130 | 0.4 | n |  | TRUE
42 | bus_LV_261-51_0_6_node_24 | 0.4 | n |  | TRUE
43 | bus_LV_261-51_0_6_node_86 | 0.4 | n |  | TRUE
44 | bus_LV_261-51_0_6_node_84 | 0.4 | n |  | TRUE
45 | bus_LV_261-51_0_6_node_27 | 0.4 | n |  | TRUE
46 | bus_LV_261-51_0_6_node_133 | 0.4 | n |  | TRUE
47 | bus_LV_261-51_0_6_node_37 | 0.4 | n |  | TRUE
48 | bus_LV_261-51_0_6_node_131 | 0.4 | n |  | TRUE
49 | bus_LV_261-51_0_6_node_34 | 0.4 | n |  | TRUE
50 | bus_LV_261-51_0_6_node_29 | 0.4 | n |  | TRUE
51 | bus_LV_261-51_0_6_node_113 | 0.4 | n |  | TRUE
52 | bus_LV_261-51_0_6_node_33 | 0.4 | n |  | TRUE
53 | bus_LV_261-51_0_6_node_43 | 0.4 | n |  | TRUE
54 | bus_LV_261-51_0_6_node_42 | 0.4 | n |  | TRUE
55 | bus_LV_261-51_0_6_node_103 | 0.4 | n |  | TRUE
56 | bus_LV_261-51_0_6_node_117 | 0.4 | n |  | TRUE
57 | bus_LV_261-51_0_6_node_128 | 0.4 | n |  | TRUE
58 | bus_LV_261-51_0_6_node_116 | 0.4 | n |  | TRUE
59 | bus_LV_261-51_0_6_node_115 | 0.4 | n |  | TRUE
60 | bus_LV_261-51_0_6_node_44 | 0.4 | n |  | TRUE
61 | bus_LV_261-51_0_6_node_55 | 0.4 | n |  | TRUE
62 | bus_LV_261-51_0_6_node_126 | 0.4 | n |  | TRUE
63 | bus_LV_261-51_0_6_node_45 | 0.4 | n |  | TRUE
64 | bus_LV_261-51_0_6_node_70 | 0.4 | n |  | TRUE
65 | bus_LV_261-51_0_6_node_68 | 0.4 | n |  | TRUE
66 | bus_LV_261-51_0_6_node_49 | 0.4 | n |  | TRUE
67 | bus_LV_261-51_0_6_node_53 | 0.4 | n |  | TRUE
68 | bus_LV_261-51_0_6_node_112 | 0.4 | n |  | TRUE
69 | bus_LV_261-51_0_6_node_140 | 0.4 | n |  | TRUE
70 | bus_LV_261-51_0_6_node_51 | 0.4 | n |  | TRUE
71 | bus_LV_261-51_0_6_node_54 | 0.4 | n |  | TRUE
72 | bus_LV_261-51_0_6_node_139 | 0.4 | n |  | TRUE
73 | bus_LV_261-51_0_6_node_127 | 0.4 | n |  | TRUE
74 | bus_LV_261-51_0_6_node_122 | 0.4 | n |  | TRUE
75 | bus_LV_261-51_0_6_node_74 | 0.4 | n |  | TRUE
76 | bus_LV_261-51_0_6_node_62 | 0.4 | n |  | TRUE
77 | bus_LV_261-51_0_6_node_141 | 0.4 | n |  | TRUE
78 | bus_LV_261-51_0_6_node_119 | 0.4 | n |  | TRUE
79 | bus_LV_261-51_0_6_node_83 | 0.4 | n |  | TRUE
80 | bus_LV_261-51_0_6_node_81 | 0.4 | n |  | TRUE
81 | bus_LV_261-51_0_6_node_88 | 0.4 | n |  | TRUE
82 | bus_LV_261-51_0_6_node_89 | 0.4 | n |  | TRUE
83 | bus_LV_261-51_0_6_node_129 | 0.4 | n |  | TRUE
84 | bus_LV_261-51_0_6_node_87 | 0.4 | n |  | TRUE
85 | bus_LV_261-51_0_6_node_85 | 0.4 | n |  | TRUE
86 | bus_LV_261-51_0_6_node_134 | 0.4 | n |  | TRUE
87 | bus_LV_261-51_0_6_node_132 | 0.4 | n |  | TRUE
88 | bus_LV_261-51_0_6_node_101 | 0.4 | n |  | TRUE
89 | bus_LV_261-51_0_6_node_59 | 0.4 | n |  | TRUE
90 | bus_LV_261-51_0_6_node_66 | 0.4 | n |  | TRUE
91 | bus_LV_261-51_0_6_node_56 | 0.4 | n |  | TRUE
92 | bus_LV_261-51_0_6_node_57 | 0.4 | n |  | TRUE
93 | bus_LV_261-51_0_6_node_121 | 0.4 | n |  | TRUE
94 | bus_LV_261-51_0_6_node_73 | 0.4 | n |  | TRUE
95 | bus_LV_261-51_0_6_node_80 | 0.4 | n |  | TRUE
96 | bus_LV_261-51_0_6_node_144 | 0.4 | n |  | TRUE
97 | bus_LV_261-51_0_6_node_146 | 0.4 | n |  | TRUE
98 | bus_LV_261-51_0_6_node_145 | 0.4 | n |  | TRUE
99 | bus_LV_261-51_0_6_node_114 | 0.4 | n |  | TRUE
100 | bus_LV_261-51_0_6_node_94 | 0.4 | n |  | TRUE
101 | bus_LV_261-51_0_6_node_92 | 0.4 | n |  | TRUE
102 | bus_LV_261-51_0_6_node_106 | 0.4 | n |  | TRUE
103 | bus_LV_261-51_0_6_node_105 | 0.4 | n |  | TRUE
104 | bus_LV_261-51_0_6_node_124 | 0.4 | n |  | TRUE
105 | bus_LV_261-51_0_6_node_71 | 0.4 | n |  | TRUE
106 | bus_LV_261-51_0_6_node_110 | 0.4 | n |  | TRUE
107 | bus_LV_261-51_0_6_node_138 | 0.4 | n |  | TRUE
108 | bus_LV_261-51_0_6_node_137 | 0.4 | n |  | TRUE
109 | bus_LV_261-51_0_6_node_58 | 0.4 | n |  | TRUE
110 | bus_LV_261-51_0_6_node_63 | 0.4 | n |  | TRUE
111 | bus_LV_261-51_0_6_node_64 | 0.4 | n |  | TRUE
112 | bus_LV_261-51_0_6_node_65 | 0.4 | n |  | TRUE
113 | bus_LV_261-51_0_6_node_67 | 0.4 | n |  | TRUE
114 | bus_LV_261-51_0_6_node_72 | 0.4 | n |  | TRUE
115 | bus_LV_261-51_0_6_node_147 | 0.4 | n |  | TRUE
116 | bus_LV_261-51_0_6_node_90 | 0.4 | n |  | TRUE
117 | bus_LV_261-51_0_6_node_91 | 0.4 | n |  | TRUE
118 | bus_LV_261-51_0_6_node_93 | 0.4 | n |  | TRUE
119 | bus_LV_261-51_0_6_node_95 | 0.4 | n |  | TRUE
120 | bus_LV_261-51_0_6_node_96 | 0.4 | n |  | TRUE
121 | bus_LV_261-51_0_6_node_97 | 0.4 | n |  | TRUE
122 | bus_LV_261-51_0_6_node_98 | 0.4 | n |  | TRUE
123 | bus_LV_261-51_0_6_node_99 | 0.4 | n |  | TRUE
124 | bus_LV_261-51_0_6_node_100 | 0.4 | n |  | TRUE
125 | bus_LV_261-51_0_6_node_142 | 0.4 | n |  | TRUE
126 | bus_LV_261-51_0_6_node_107 | 0.4 | n |  | TRUE
127 | bus_LV_261-51_0_6_node_108 | 0.4 | n |  | TRUE
128 | bus_LV_261-51_0_6_node_109 | 0.4 | n |  | TRUE
129 | bus_LV_261-51_0_6_node_120 | 0.4 | n |  | TRUE
130 | bus_LV_261-51_0_6_node_125 | 0.4 | n |  | TRUE
131 | bus_LV_261-51_0_6_node_123 | 0.4 | n |  | TRUE
132 | bus_LV_261-51_0_6_node_135 | 0.4 | n |  | TRUE
133 | bus_LV_261-51_0_6_node_136 | 0.4 | n |  | TRUE
134 | bus_MV_359_0_node_68 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-51_0_6_load_0 | 0 | 0.012201 | 0.0030578 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-51_0_6_load_1 | 1 | 0.0059031 | 0.0014795 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-51_0_6_load_2 | 2 | 0.010478 | 0.0026261 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-51_0_6_load_3 | 3 | 0.0042474 | 0.0010645 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-51_0_6_load_4 | 4 | 0.0082527 | 0.0020683 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-51_0_6_load_76 | 6 | 0.0041665 | 0.0010442 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-51_0_6_load_78 | 7 | 0.0059791 | 0.0014985 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-51_0_6_load_79 | 8 | 0.0060619 | 0.0015193 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-51_0_6_load_75 | 10 | 0.0069455 | 0.0017407 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-51_0_6_load_5 | 11 | 0.0010166 | 0.00025479 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-51_0_6_load_6 | 12 | 0.00085254 | 0.00021367 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-51_0_6_load_7 | 13 | 0.00085263 | 0.00021369 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-51_0_6_load_8 | 14 | 0.0016616 | 0.00041643 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-51_0_6_load_9 | 15 | 0.0023496 | 0.00058885 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-51_0_6_load_77 | 16 | 0.0024051 | 0.00060278 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-51_0_6_load_10 | 17 | 0.0036767 | 0.00092146 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-51_0_6_load_11 | 19 | 0.0060163 | 0.0015078 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_261-51_0_6_load_12 | 20 | 0.0026342 | 0.0006602 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_261-51_0_6_load_14 | 22 | 0.002645 | 0.00066291 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_261-51_0_6_load_16 | 24 | 0.0036314 | 0.0009101 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_261-51_0_6_load_69 | 25 | 0.0026729 | 0.00066988 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_261-51_0_6_load_143 | 26 | 0.0034033 | 0.00085296 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_261-51_0_6_load_61 | 27 | 0.0036705 | 0.0009199 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_261-51_0_6_load_82 | 28 | 0.0068144 | 0.0017078 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_261-51_0_6_load_148 | 31 | 0.017644 | 0.004422 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_261-51_0_6_load_104 | 33 | 0.0057521 | 0.0014416 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_261-51_0_6_load_102 | 34 | 0.010719 | 0.0026864 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_261-51_0_6_load_118 | 37 | 0.013777 | 0.0034529 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_261-51_0_6_load_130 | 41 | 0.0052054 | 0.0013046 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_261-51_0_6_load_84 | 44 | 0.0027019 | 0.00067715 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_261-51_0_6_load_133 | 46 | 0.0070822 | 0.001775 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_261-51_0_6_load_131 | 48 | 0.0090527 | 0.0022688 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_261-51_0_6_load_113 | 51 | 0.0075559 | 0.0018937 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_261-51_0_6_load_42 | 54 | 0.0013855 | 0.00034724 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_261-51_0_6_load_103 | 55 | 0.0059606 | 0.0014939 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_261-51_0_6_load_117 | 56 | 0.0043865 | 0.0010994 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_261-51_0_6_load_128 | 57 | 0.0038932 | 0.00097573 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_261-51_0_6_load_116 | 58 | 0.0064932 | 0.0016273 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_261-51_0_6_load_115 | 59 | 0.0046505 | 0.0011655 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_261-51_0_6_load_126 | 62 | 0.0060045 | 0.0015049 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_261-51_0_6_load_70 | 64 | 0.0034655 | 0.00086853 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_261-51_0_6_load_68 | 65 | 0.0032323 | 0.00081009 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_261-51_0_6_load_112 | 68 | 0.0039685 | 0.00099459 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_261-51_0_6_load_140 | 69 | 0.0023492 | 0.00058878 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_261-51_0_6_load_139 | 72 | 0.0052971 | 0.0013276 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_261-51_0_6_load_127 | 73 | 0.0047417 | 0.0011884 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_261-51_0_6_load_122 | 74 | 0.0085756 | 0.0021493 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_261-51_0_6_load_74 | 75 | 0.0071729 | 0.0017977 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_261-51_0_6_load_62 | 76 | 0.0037078 | 0.00092926 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_261-51_0_6_load_141 | 77 | 0.0041488 | 0.0010398 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_261-51_0_6_load_119 | 78 | 0.0090437 | 0.0022666 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_261-51_0_6_load_83 | 79 | 0.0075532 | 0.001893 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_261-51_0_6_load_81 | 80 | 0.008244 | 0.0020662 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_261-51_0_6_load_88 | 81 | 0.0087872 | 0.0022023 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_261-51_0_6_load_89 | 82 | 0.0091236 | 0.0022866 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_261-51_0_6_load_129 | 83 | 0.0051916 | 0.0013011 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_261-51_0_6_load_87 | 84 | 0.00206 | 0.00051628 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_261-51_0_6_load_85 | 85 | 0.0021923 | 0.00054945 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_261-51_0_6_load_134 | 86 | 0.0037734 | 0.00094571 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_261-51_0_6_load_132 | 87 | 0.0064198 | 0.001609 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_261-51_0_6_load_101 | 88 | 0.0091035 | 0.0022816 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_261-51_0_6_load_59 | 89 | 0.0039442 | 0.0009885 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_261-51_0_6_load_56 | 91 | 0.0039914 | 0.0010003 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_261-51_0_6_load_57 | 92 | 0.0036617 | 0.0009177 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_261-51_0_6_load_73 | 94 | 0.0078167 | 0.001959 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_261-51_0_6_load_80 | 95 | 0.0050845 | 0.0012743 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_261-51_0_6_load_144 | 96 | 0.0034782 | 0.00087171 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_261-51_0_6_load_146 | 97 | 0.0013202 | 0.00033087 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_261-51_0_6_load_145 | 98 | 0.0019699 | 0.00049371 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_261-51_0_6_load_114 | 99 | 0.0021396 | 0.00053623 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_261-51_0_6_load_94 | 100 | 0.0094587 | 0.0023706 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_261-51_0_6_load_92 | 101 | 0.004626 | 0.0011594 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_261-51_0_6_load_106 | 102 | 0.0075305 | 0.0018873 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_261-51_0_6_load_105 | 103 | 0.0032072 | 0.00080379 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_261-51_0_6_load_124 | 104 | 0.0075561 | 0.0018937 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_261-51_0_6_load_71 | 105 | 0.0036554 | 0.00091614 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_261-51_0_6_load_138 | 107 | 0.0067928 | 0.0017024 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_261-51_0_6_load_137 | 108 | 0.0041609 | 0.0010428 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_261-51_0_6_load_58 | 109 | 0.0040844 | 0.0010236 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_261-51_0_6_load_64 | 111 | 0.0036954 | 0.00092614 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_261-51_0_6_load_65 | 112 | 0.0038601 | 0.00096743 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_261-51_0_6_load_67 | 113 | 0.0038636 | 0.00096832 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_261-51_0_6_load_147 | 115 | 0.002094 | 0.00052481 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_261-51_0_6_load_90 | 116 | 0.0091996 | 0.0023056 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_261-51_0_6_load_91 | 117 | 0.0092176 | 0.0023101 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_261-51_0_6_load_93 | 118 | 0.0035589 | 0.00089194 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_261-51_0_6_load_95 | 119 | 0.0076307 | 0.0019124 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_261-51_0_6_load_96 | 120 | 0.013217 | 0.0033125 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_261-51_0_6_load_97 | 121 | 0.0081475 | 0.0020419 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_261-51_0_6_load_98 | 122 | 0.0225 | 0.005639 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_261-51_0_6_load_99 | 123 | 0.0084162 | 0.0021093 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_261-51_0_6_load_100 | 124 | 0.014888 | 0.0037313 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_261-51_0_6_load_142 | 125 | 0.0038149 | 0.0009561 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_261-51_0_6_load_107 | 126 | 0.0049144 | 0.0012317 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_261-51_0_6_load_108 | 127 | 0.0042602 | 0.0010677 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_261-51_0_6_load_109 | 128 | 0.019576 | 0.0049062 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_261-51_0_6_load_120 | 129 | 0.0058691 | 0.0014709 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_261-51_0_6_load_125 | 130 | 0.0047494 | 0.0011903 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_261-51_0_6_load_123 | 131 | 0.0060477 | 0.0015157 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_261-51_0_6_load_135 | 132 | 0.0043402 | 0.0010877 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_261-51_0_6_load_136 | 133 | 0.0037025 | 0.00092795 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 56 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-51_0_6_line_0 |  | 0 | 1 | 0.029246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-51_0_6_line_1 |  | 0 | 2 | 0.028388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-51_0_6_line_2 |  | 1 | 3 | 0.03732 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-51_0_6_line_3 |  | 2 | 4 | 0.026297 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-51_0_6_line_4 |  | 3 | 5 | 0.0039241 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_261-51_0_6_line_5 |  | 4 | 6 | 0.023259 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_261-51_0_6_line_6 |  | 5 | 7 | 0.003996 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_261-51_0_6_line_7 |  | 5 | 8 | 0.022456 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_261-51_0_6_line_8 |  | 5 | 9 | 0.096045 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_261-51_0_6_line_9 |  | 6 | 10 | 0.028488 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_261-51_0_6_line_10 |  | 8 | 43 | 0.012196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_261-51_0_6_line_11 |  | 9 | 28 | 0.037365 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_261-51_0_6_line_12 |  | 9 | 29 | 0.0073843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-51_0_6_line_13 |  | 11 | 12 | 0.027942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_261-51_0_6_line_14 |  | 11 | 13 | 0.026774 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_261-51_0_6_line_15 |  | 12 | 14 | 0.024447 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_261-51_0_6_line_16 |  | 13 | 15 | 0.03131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_261-51_0_6_line_17 |  | 14 | 16 | 0.016131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_261-51_0_6_line_18 |  | 15 | 17 | 0.021195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_261-51_0_6_line_19 |  | 16 | 18 | 0.01972 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_261-51_0_6_line_20 |  | 18 | 53 | 0.005144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_261-51_0_6_line_21 |  | 18 | 42 | 0.009348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_261-51_0_6_line_22 |  | 19 | 20 | 0.010989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_261-51_0_6_line_23 |  | 19 | 21 | 0.010863 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_261-51_0_6_line_24 |  | 20 | 22 | 0.0070745 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_261-51_0_6_line_25 |  | 21 | 23 | 0.020332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_261-51_0_6_line_26 |  | 21 | 24 | 0.014646 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_261-51_0_6_line_27 |  | 23 | 25 | 0.014474 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_261-51_0_6_line_28 |  | 23 | 26 | 0.0076566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_261-51_0_6_line_29 |  | 24 | 27 | 0.0079571 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_261-51_0_6_line_30 |  | 25 | 65 | 0.0079851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_261-51_0_6_line_31 |  | 26 | 75 | 0.019741 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_261-51_0_6_line_32 |  | 27 | 76 | 0.0080557 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_261-51_0_6_line_33 |  | 28 | 95 | 0.014356 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_261-51_0_6_line_34 |  | 29 | 33 | 0.012724 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_261-51_0_6_line_35 |  | 29 | 34 | 0.0062575 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
36 | LV_261-51_0_6_line_36 |  | 30 | 31 | 0.019316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_261-51_0_6_line_37 |  | 30 | 32 | 0.14113 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_261-51_0_6_line_38 |  | 32 | 69 | 0.012532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_261-51_0_6_line_39 |  | 33 | 77 | 2.0996e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_261-51_0_6_line_40 |  | 34 | 55 | 0.016418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
41 | LV_261-51_0_6_line_41 |  | 35 | 36 | 0.003101 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
42 | LV_261-51_0_6_line_42 |  | 35 | 37 | 0.012694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
43 | LV_261-51_0_6_line_43 |  | 36 | 49 | 0.011956 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
44 | LV_261-51_0_6_line_44 |  | 37 | 78 | 0.015763 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_261-51_0_6_line_45 |  | 38 | 39 | 0.015641 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_261-51_0_6_line_46 |  | 38 | 40 | 0.010757 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_261-51_0_6_line_47 |  | 38 | 41 | 0.010295 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_261-51_0_6_line_48 |  | 39 | 45 | 0.0093354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_261-51_0_6_line_49 |  | 39 | 46 | 0.0019427 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_261-51_0_6_line_50 |  | 40 | 58 | 0.017586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
51 | LV_261-51_0_6_line_51 |  | 40 | 59 | 0.03074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_261-51_0_6_line_52 |  | 40 | 50 | 0.050093 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_261-51_0_6_line_53 |  | 41 | 83 | 0.012 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_261-51_0_6_line_54 |  | 42 | 43 | 0.023731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_261-51_0_6_line_55 |  | 42 | 44 | 0.020327 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_261-51_0_6_line_56 |  | 43 | 84 | 0.047419 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_261-51_0_6_line_57 |  | 44 | 85 | 0.026695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_261-51_0_6_line_58 |  | 45 | 47 | 0.003667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_261-51_0_6_line_59 |  | 45 | 48 | 0.016484 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_261-51_0_6_line_60 |  | 46 | 86 | 0.014055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_261-51_0_6_line_61 |  | 47 | 57 | 0.034155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_261-51_0_6_line_62 |  | 48 | 87 | 0.031861 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_261-51_0_6_line_63 |  | 49 | 55 | 0.0022933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
64 | LV_261-51_0_6_line_64 |  | 49 | 56 | 0.019163 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
65 | LV_261-51_0_6_line_65 |  | 50 | 51 | 0.068301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_261-51_0_6_line_66 |  | 51 | 88 | 0.016427 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_261-51_0_6_line_67 |  | 52 | 53 | 0.001398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_261-51_0_6_line_68 |  | 52 | 54 | 0.011509 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_261-51_0_6_line_69 |  | 53 | 96 | 0.017272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_261-51_0_6_line_70 |  | 56 | 58 | 0.018942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
71 | LV_261-51_0_6_line_71 |  | 57 | 73 | 0.034253 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_261-51_0_6_line_72 |  | 59 | 99 | 0.01644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_261-51_0_6_line_73 |  | 60 | 61 | 0.023686 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_261-51_0_6_line_74 |  | 60 | 62 | 0.039491 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_261-51_0_6_line_75 |  | 61 | 74 | 0.038871 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_261-51_0_6_line_76 |  | 62 | 104 | 0.012899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_261-51_0_6_line_77 |  | 63 | 64 | 0.0074459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_261-51_0_6_line_78 |  | 63 | 65 | 0.0084693 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_261-51_0_6_line_79 |  | 64 | 105 | 0.0083288 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_261-51_0_6_line_80 |  | 66 | 67 | 0.11857 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_261-51_0_6_line_81 |  | 66 | 68 | 0.02178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_261-51_0_6_line_82 |  | 67 | 71 | 0.17335 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_261-51_0_6_line_83 |  | 67 | 73 | 0.1054 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_261-51_0_6_line_84 |  | 68 | 106 | 0.016613 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_261-51_0_6_line_85 |  | 69 | 71 | 0.02276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_261-51_0_6_line_86 |  | 70 | 71 | 0.0207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_261-51_0_6_line_87 |  | 70 | 72 | 0.023876 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_261-51_0_6_line_88 |  | 74 | 93 | 0.012423 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_261-51_0_6_line_89 |  | 76 | 110 | 0.012459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_261-51_0_6_line_90 |  | 77 | 125 | 0.019278 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_261-51_0_6_line_91 |  | 78 | 129 | 0.01285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_261-51_0_6_line_92 |  | 79 | 80 | 0.026563 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_261-51_0_6_line_93 |  | 80 | 95 | 0.02105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_261-51_0_6_line_94 |  | 81 | 82 | 0.025997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_261-51_0_6_line_95 |  | 82 | 116 | 0.025619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_261-51_0_6_line_96 |  | 84 | 115 | 0.0035634 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_261-51_0_6_line_97 |  | 86 | 132 | 0.010759 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_261-51_0_6_line_98 |  | 88 | 124 | 0.012557 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_261-51_0_6_line_99 |  | 89 | 90 | 0.0051232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_261-51_0_6_line_100 |  | 90 | 111 | 0.0030041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_261-51_0_6_line_101 |  | 90 | 110 | 0.025543 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_261-51_0_6_line_102 |  | 91 | 92 | 0.0081191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_261-51_0_6_line_103 |  | 92 | 109 | 0.0082211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_261-51_0_6_line_104 |  | 93 | 94 | 0.015267 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_261-51_0_6_line_105 |  | 94 | 114 | 0.014348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_261-51_0_6_line_106 |  | 96 | 98 | 0.031695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_261-51_0_6_line_107 |  | 97 | 98 | 0.03055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_261-51_0_6_line_108 |  | 99 | 117 | 0.0059278 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_261-51_0_6_line_109 |  | 100 | 101 | 0.016636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_261-51_0_6_line_110 |  | 101 | 118 | 0.0084324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_261-51_0_6_line_111 |  | 102 | 103 | 0.02257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_261-51_0_6_line_112 |  | 103 | 126 | 4.5578e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_261-51_0_6_line_113 |  | 104 | 131 | 0.012987 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_261-51_0_6_line_114 |  | 105 | 114 | 0.0024721 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_261-51_0_6_line_115 |  | 106 | 128 | 0.0062219 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_261-51_0_6_line_116 |  | 107 | 108 | 0.01453 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_261-51_0_6_line_117 |  | 108 | 133 | 0.010432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_261-51_0_6_line_118 |  | 109 | 110 | 0.01196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_261-51_0_6_line_119 |  | 111 | 112 | 0.021321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_261-51_0_6_line_120 |  | 112 | 113 | 0.0032837 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_261-51_0_6_line_121 |  | 116 | 117 | 0.026531 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_261-51_0_6_line_122 |  | 118 | 119 | 0.015815 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_261-51_0_6_line_123 |  | 119 | 120 | 0.015901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_261-51_0_6_line_124 |  | 120 | 121 | 0.013116 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_261-51_0_6_line_125 |  | 121 | 122 | 0.021676 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_261-51_0_6_line_126 |  | 122 | 123 | 0.0082277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_261-51_0_6_line_127 |  | 123 | 124 | 0.018798 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_261-51_0_6_line_128 |  | 125 | 127 | 3.1224e-06 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_261-51_0_6_line_129 |  | 126 | 127 | 0.01884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_261-51_0_6_line_130 |  | 129 | 130 | 0.010955 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_261-51_0_6_line_131 |  | 130 | 131 | 0.010977 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_261-51_0_6_line_132 |  | 132 | 133 | 0.010664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-51_0_6_trafo_117 | 0.63 MVA 20/0.4 kV | 134 | 56 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14
0 | 2682282.8223 | 1245450.4103 | 2682281.9382 | 1245473.8543 | 2682281.7307 | 1245479.6363
1 | 2682282.8223 | 1245450.4103 | 2682283.8921 | 1245422.0421
2 | 2682281.7307 | 1245479.6363 | 2682280.6444 | 1245509.9071 | 2682280.5989 | 1245513.1866 | 2682280.9348 | 1245515.1149 | 2682281.6221 | 1245516.7701
3 | 2682284.8623 | 1245395.7631 | 2682284.449 | 1245407.274 | 2682283.8921 | 1245422.0421
4 | 2682279.1617 | 1245519.8271 | 2682281.6221 | 1245516.7701 | 2682281.6221 | 1245516.7701
5 | 2682285.6967 | 1245372.5194 | 2682284.8623 | 1245395.7631
6 | 2682279.1617 | 1245519.8271 | 2682276.6627 | 1245522.9503
7 | 2682279.1617 | 1245519.8271 | 2682296.8926 | 1245533.6077
8 | 2682220.8547 | 1245474.9638 | 2682220.5852 | 1245470.4234 | 2682220.8649 | 1245461.6987 | 2682241.235 | 1245487.3776 | 2682250.3322 | 1245496.6549 | 2682273.4512 | 1245514.7998 | 2682279.1617 | 1245519.8271
9 | 2682286.7188 | 1245344.0501 | 2682285.6967 | 1245372.5194
10 | 2682306.583 | 1245541.0118 | 2682302.7016 | 1245538.1225 | 2682296.8926 | 1245533.6077
11 | 2682220.8547 | 1245474.9638 | 2682222.1604 | 1245500.6784 | 2682223.2413 | 1245503.918 | 2682223.5469 | 1245512.1142
12 | 2682213.476 | 1245475.2506 | 2682216.7571 | 1245475.1294 | 2682220.8547 | 1245474.9638
13 | 2682330.7062 | 1245452.1728 | 2682329.7536 | 1245480.0986
14 | 2682330.7062 | 1245452.1728 | 2682331.6189 | 1245425.4143
15 | 2682329.7536 | 1245480.0986 | 2682329.4022 | 1245490.4026 | 2682329.0009 | 1245504.534
16 | 2682331.6189 | 1245425.4143 | 2682332.4611 | 1245400.7242 | 2682332.6881 | 1245394.1221
17 | 2682328.543 | 1245520.6582 | 2682329.0009 | 1245504.534
18 | 2682332.6881 | 1245394.1221 | 2682333.4165 | 1245372.9397
19 | 2682332.9569 | 1245535.318 | 2682328.0957 | 1245535.5063 | 2682328.3966 | 1245525.8145 | 2682328.543 | 1245520.6582
20 | 2682332.9569 | 1245535.318 | 2682338.1127 | 1245535.1228
21 | 2682329.8197 | 1245544.1254 | 2682332.9569 | 1245535.318
22 | 2682266.6054 | 1245406.7479 | 2682255.6244 | 1245406.3364
23 | 2682277.4613 | 1245407.1547 | 2682266.6054 | 1245406.7479
24 | 2682255.6244 | 1245406.3364 | 2682248.5549 | 1245406.0715
25 | 2682277.4613 | 1245407.1547 | 2682278.2268 | 1245386.8395
26 | 2682277.4613 | 1245407.1547 | 2682276.9091 | 1245421.7901
27 | 2682278.2268 | 1245386.8395 | 2682278.7741 | 1245372.3758
28 | 2682278.2268 | 1245386.8395 | 2682270.5949 | 1245386.2248
29 | 2682276.6091 | 1245429.7416 | 2682276.9091 | 1245421.7901
30 | 2682279.076 | 1245364.3964 | 2682278.7741 | 1245372.3758
31 | 2682259.0622 | 1245377.789 | 2682258.3763 | 1245385.2408 | 2682270.5949 | 1245386.2248
32 | 2682276.6091 | 1245429.7416 | 2682276.3054 | 1245437.7915
33 | 2682224.0817 | 1245526.4605 | 2682223.5469 | 1245512.1142
34 | 2682213.476 | 1245475.2506 | 2682214.0124 | 1245487.9632
35 | 2682213.476 | 1245475.2506 | 2682213.1847 | 1245469
36 | 2681906.3981 | 1245463.7837 | 2681905.3371 | 1245471.6637 | 2681900.5614 | 1245481.9763
37 | 2681906.3981 | 1245463.7837 | 2681913.1826 | 1245467.1242 | 2681926.8421 | 1245472.728 | 2681959.816 | 1245487.5276 | 2681965.7936 | 1245473.2665 | 2681962.0603 | 1245471.6693 | 2681963.8083 | 1245467.6572 | 2681982.6593 | 1245423.4966 | 2681983.1499 | 1245421.9022 | 2681983.0793 | 1245420.4446 | 2681982.3995 | 1245418.7896 | 2681979.0272 | 1245414.0395
38 | 2681979.0272 | 1245414.0395 | 2681983.3648 | 1245402.282
39 | 2682214.0133 | 1245487.9842 | 2682214.0124 | 1245487.9632
40 | 2682213.1847 | 1245469 | 2682213.1441 | 1245468.1297 | 2682212.1341 | 1245462.5005 | 2682209.8085 | 1245456.9309 | 2682207.6244 | 1245453.8312
41 | 2682210.6754 | 1245438.5518 | 2682209.8002 | 1245439.5515 | 2682208.1221 | 1245440.1398
42 | 2682210.6754 | 1245438.5518 | 2682210.9062 | 1245432.8063 | 2682211.7695 | 1245425.9161
43 | 2682206.3035 | 1245451.9565 | 2682206.926 | 1245447.9289 | 2682208.1221 | 1245440.1398
44 | 2682211.7695 | 1245425.9161 | 2682213.7291 | 1245410.2751
45 | 2682160.9106 | 1245399.3227 | 2682160.0748 | 1245402.38 | 2682159.7984 | 1245404.878 | 2682161.0636 | 1245406.8192 | 2682167.1191 | 1245411.5064
46 | 2682161.2141 | 1245420.4979 | 2682164.9115 | 1245414.8672 | 2682167.1191 | 1245411.5064
47 | 2682167.1191 | 1245411.5064 | 2682175.3269 | 1245417.7214
48 | 2682151.9236 | 1245396.7964 | 2682156.8611 | 1245398.188 | 2682160.9106 | 1245399.3227
49 | 2682160.9106 | 1245399.3227 | 2682161.3581 | 1245397.4323
50 | 2682161.2141 | 1245420.4979 | 2682164.4502 | 1245420.3426 | 2682175.8973 | 1245428.9891
51 | 2682161.2141 | 1245420.4979 | 2682159.063 | 1245423.0477 | 2682160.2243 | 1245450.4268
52 | 2682150.8914 | 1245459.828 | 2682156.1186 | 1245459.9449 | 2682155.9725 | 1245420.3252 | 2682161.2141 | 1245420.4979
53 | 2682184.8934 | 1245424.9652 | 2682175.3269 | 1245417.7214
54 | 2682329.8197 | 1245544.1254 | 2682321.3176 | 1245544.7856 | 2682311.1066 | 1245542.8203 | 2682306.583 | 1245541.0118
55 | 2682329.8197 | 1245544.1254 | 2682326.4919 | 1245552.5186 | 2682323.5053 | 1245563.4151
56 | 2682306.583 | 1245541.0118 | 2682293.2319 | 1245569.2916 | 2682289.1349 | 1245574.3162 | 2682286.682 | 1245576.2948 | 2682281.3941 | 1245580.0949
57 | 2682323.5053 | 1245563.4151 | 2682316.4487 | 1245589.1606
58 | 2682148.3684 | 1245397.0696 | 2682149.9374 | 1245397.2581 | 2682151.3062 | 1245397.177 | 2682151.9236 | 1245396.7964
59 | 2682151.9236 | 1245396.7964 | 2682152.9955 | 1245395.7772 | 2682153.6221 | 1245394.7295 | 2682156.8051 | 1245381.3179
60 | 2682161.3581 | 1245397.4323 | 2682164.5955 | 1245383.7551
61 | 2682148.3684 | 1245397.0696 | 2682132.481 | 1245384.8407 | 2682128.0312 | 1245381.51 | 2682121.3492 | 1245376.1786
62 | 2682156.8051 | 1245381.3179 | 2682164.1623 | 1245350.318
63 | 2682206.3035 | 1245451.9565 | 2682207.6244 | 1245453.8312
64 | 2682206.3035 | 1245451.9565 | 2682191.0122 | 1245440.4062
65 | 2682150.8914 | 1245459.828 | 2682148.823 | 1245458.5985 | 2682146.7625 | 1245453.5218 | 2682139.1743 | 1245416.0339 | 2682137.1064 | 1245412.0357 | 2682134.4445 | 1245410.0085 | 2682131.142 | 1245409.4957 | 2682126.7702 | 1245409.8132 | 2682123.2514 | 1245412.9112 | 2682122.4392 | 1245414.6362
66 | 2682122.4392 | 1245414.6362 | 2682120.9314 | 1245417.8382 | 2682121.6611 | 1245430.7051
67 | 2682339.0886 | 1245536.126 | 2682338.1127 | 1245535.1228
68 | 2682339.0886 | 1245536.126 | 2682340.6883 | 1245536.8264 | 2682342.2941 | 1245537.0934 | 2682344.2724 | 1245537.1876 | 2682350.395 | 1245536.5602
69 | 2682338.1127 | 1245535.1228 | 2682337.3276 | 1245533.444 | 2682337.1158 | 1245531.2839 | 2682337.5722 | 1245518.0435
70 | 2682191.0122 | 1245440.4062 | 2682175.8973 | 1245428.9891
71 | 2682104.5497 | 1245347.7176 | 2682105.5548 | 1245353.4563 | 2682106.8022 | 1245358.3215 | 2682108.7639 | 1245362.8965 | 2682111.7498 | 1245367.1742 | 2682115.8343 | 1245371.7786 | 2682121.3492 | 1245376.1786
72 | 2682160.2243 | 1245450.4268 | 2682160.921 | 1245466.8516
73 | 2682226.1 | 1245310.8837 | 2682226.5291 | 1245307.1869 | 2682231.9909 | 1245307.8298 | 2682233.3234 | 1245298.3858 | 2682238.2112 | 1245299.0096
74 | 2682226.1 | 1245310.8837 | 2682223.7239 | 1245330.743 | 2682222.3597 | 1245341.3874 | 2682221.2709 | 1245350.0778
75 | 2682238.2112 | 1245299.0096 | 2682233.5073 | 1245337.5952
76 | 2682219.6674 | 1245362.8767 | 2682221.2709 | 1245350.0778
77 | 2682279.3963 | 1245355.9332 | 2682271.9733 | 1245355.3492
78 | 2682279.3963 | 1245355.9332 | 2682279.076 | 1245364.3964
79 | 2682263.6701 | 1245354.696 | 2682271.9733 | 1245355.3492
80 | 2682081.2591 | 1245245.0301 | 2682078.1468 | 1245246.5993 | 2682079.1617 | 1245251.339 | 2682080.2094 | 1245262.4505 | 2682080.4468 | 1245263.3099 | 2682083.2949 | 1245274.2684 | 2682086.4992 | 1245283.5195 | 2682087.804 | 1245288.0631 | 2682091.2145 | 1245297.695 | 2682087.9771 | 1245303.3877 | 2682086.3803 | 1245311.2046 | 2682086.751 | 1245319.905 | 2682087.1182 | 1245335.4102 | 2682083.8959 | 1245358.5714
81 | 2682083.8959 | 1245358.5714 | 2682082.2848 | 1245370.1464 | 2682080.7816 | 1245380.1273
82 | 2681991.2424 | 1245380.9287 | 2682015.9315 | 1245325.5408 | 2682018.5447 | 1245318.5273 | 2682023.7075 | 1245307.4684 | 2682029.3517 | 1245295.4822 | 2682052.1353 | 1245257.1583 | 2682054.9769 | 1245252.761 | 2682058.5746 | 1245249.9643 | 2682061.1179 | 1245249.6548 | 2682063.2118 | 1245250.1397 | 2682065.1346 | 1245250.978 | 2682066.421 | 1245252.4858 | 2682070.431 | 1245250.4731 | 2682078.1468 | 1245246.5993 | 2682081.2591 | 1245245.0301
83 | 2682081.2591 | 1245245.0301 | 2682081.433 | 1245246.6559 | 2682083.6621 | 1245255.9379 | 2682088.3422 | 1245275.3835 | 2682092.0707 | 1245287.6996 | 2682096.2256 | 1245302.5123 | 2682100.1978 | 1245322.871 | 2682104.5497 | 1245347.7176
84 | 2682078.3073 | 1245396.5551 | 2682080.7816 | 1245380.1273
85 | 2681991.2424 | 1245380.9287 | 2681983.3648 | 1245402.282
86 | 2681972.0355 | 1245373.2132 | 2681977.4985 | 1245375.4125 | 2681986.442 | 1245378.9053 | 2681991.2424 | 1245380.9287
87 | 2681972.0355 | 1245373.2132 | 2681981.3097 | 1245351.2125
88 | 2682232.0039 | 1245349.9273 | 2682233.5073 | 1245337.5952
89 | 2682275.8357 | 1245450.2414 | 2682276.3054 | 1245437.7915
90 | 2682214.0133 | 1245487.9842 | 2682214.8259 | 1245507.2454
91 | 2682213.7291 | 1245410.2751 | 2682215.3265 | 1245397.525
92 | 2682224.8658 | 1245547.496 | 2682225.8553 | 1245574.0402
93 | 2682224.0817 | 1245526.4605 | 2682224.8658 | 1245547.496
94 | 2682164.484 | 1245550.8504 | 2682163.3823 | 1245524.8772
95 | 2682163.3823 | 1245524.8772 | 2682162.2966 | 1245499.2813
96 | 2682278.5004 | 1245582.1745 | 2682281.3941 | 1245580.0949
97 | 2682164.5955 | 1245383.7551 | 2682167.0737 | 1245373.2854
98 | 2682121.6611 | 1245430.7051 | 2682122.3721 | 1245443.2423
99 | 2682250.233 | 1245449.3413 | 2682250.0141 | 1245454.4598
100 | 2682250.233 | 1245449.3413 | 2682250.3191 | 1245446.3384
101 | 2682250.233 | 1245449.3413 | 2682275.8357 | 1245450.2414
102 | 2682274.7697 | 1245478.5219 | 2682275.0755 | 1245470.4085
103 | 2682275.0755 | 1245470.4085 | 2682275.3852 | 1245462.1933
104 | 2682232.0039 | 1245349.9273 | 2682247.1352 | 1245351.9585
105 | 2682261.2057 | 1245354.5021 | 2682258.0546 | 1245353.4243 | 2682247.1352 | 1245351.9585
106 | 2682337.5722 | 1245518.0435 | 2682338.664 | 1245486.367
107 | 2682338.664 | 1245486.367 | 2682339.7164 | 1245455.8347
108 | 2682161.1722 | 1245472.774 | 2682160.921 | 1245466.8516
109 | 2682128.5168 | 1245545.0213 | 2682129.6998 | 1245561.6153
110 | 2682128.5168 | 1245545.0213 | 2682127.9172 | 1245536.6102
111 | 2682215.6222 | 1245526.1177 | 2682216.5736 | 1245548.6673
112 | 2682215.6222 | 1245526.1177 | 2682215.6202 | 1245526.0722
113 | 2682218.0529 | 1245375.7631 | 2682219.6674 | 1245362.8767
114 | 2682261.2057 | 1245354.5021 | 2682263.6701 | 1245354.696
115 | 2682078.3073 | 1245396.5551 | 2682077.3803 | 1245402.7075
116 | 2682171.933 | 1245352.7564 | 2682175.2799 | 1245338.617
117 | 2682169.5301 | 1245362.908 | 2682171.933 | 1245352.7564
118 | 2682275.8357 | 1245450.2414 | 2682275.3852 | 1245462.1933
119 | 2682250.3191 | 1245446.3384 | 2682250.9299 | 1245425.0256
120 | 2682251.0239 | 1245421.7432 | 2682250.9299 | 1245425.0256
121 | 2682161.1722 | 1245472.774 | 2682162.2966 | 1245499.2813
122 | 2682126.7925 | 1245520.8352 | 2682127.9172 | 1245536.6102
123 | 2682126.7925 | 1245520.8352 | 2682126.6944 | 1245519.4586 | 2682125.8722 | 1245504.9611
124 | 2682125.1296 | 1245491.8659 | 2682125.8722 | 1245504.9611
125 | 2682125.1296 | 1245491.8659 | 2682123.9023 | 1245470.2243
126 | 2682123.4364 | 1245462.0098 | 2682123.9023 | 1245470.2243
127 | 2682123.4364 | 1245462.0098 | 2682122.3721 | 1245443.2423
128 | 2682214.8261 | 1245507.2485 | 2682214.8259 | 1245507.2454
129 | 2682214.8261 | 1245507.2485 | 2682215.6202 | 1245526.0722
130 | 2682215.3265 | 1245397.525 | 2682216.6883 | 1245386.6549
131 | 2682218.0529 | 1245375.7631 | 2682216.6883 | 1245386.6549
132 | 2682167.0737 | 1245373.2854 | 2682169.5301 | 1245362.908

## bus_geodata
| x | y | coords
0 | 2682282.8223 | 1245450.4103
1 | 2682281.7307 | 1245479.6363
2 | 2682283.8921 | 1245422.0421
3 | 2682281.6221 | 1245516.7701
4 | 2682284.8623 | 1245395.7631
5 | 2682279.1617 | 1245519.8271
6 | 2682285.6967 | 1245372.5194
7 | 2682276.6627 | 1245522.9503
8 | 2682296.8926 | 1245533.6077
9 | 2682220.8547 | 1245474.9638
10 | 2682286.7188 | 1245344.0501
11 | 2682330.7062 | 1245452.1728
12 | 2682329.7536 | 1245480.0986
13 | 2682331.6189 | 1245425.4143
14 | 2682329.0009 | 1245504.534
15 | 2682332.6881 | 1245394.1221
16 | 2682328.543 | 1245520.6582
17 | 2682333.4165 | 1245372.9397
18 | 2682332.9569 | 1245535.318
19 | 2682266.6054 | 1245406.7479
20 | 2682255.6244 | 1245406.3364
21 | 2682277.4613 | 1245407.1547
22 | 2682248.5549 | 1245406.0715
23 | 2682278.2268 | 1245386.8395
24 | 2682276.9091 | 1245421.7901
25 | 2682278.7741 | 1245372.3758
26 | 2682270.5949 | 1245386.2248
27 | 2682276.6091 | 1245429.7416
28 | 2682223.5469 | 1245512.1142
29 | 2682213.476 | 1245475.2506
30 | 2681906.3981 | 1245463.7837
31 | 2681900.5614 | 1245481.9763
32 | 2681979.0272 | 1245414.0395
33 | 2682214.0124 | 1245487.9632
34 | 2682213.1847 | 1245469
35 | 2682210.6754 | 1245438.5518
36 | 2682208.1221 | 1245440.1398
37 | 2682211.7695 | 1245425.9161
38 | 2682167.1191 | 1245411.5064
39 | 2682160.9106 | 1245399.3227
40 | 2682161.2141 | 1245420.4979
41 | 2682175.3269 | 1245417.7214
42 | 2682329.8197 | 1245544.1254
43 | 2682306.583 | 1245541.0118
44 | 2682323.5053 | 1245563.4151
45 | 2682151.9236 | 1245396.7964
46 | 2682161.3581 | 1245397.4323
47 | 2682148.3684 | 1245397.0696
48 | 2682156.8051 | 1245381.3179
49 | 2682206.3035 | 1245451.9565
50 | 2682150.8914 | 1245459.828
51 | 2682122.4392 | 1245414.6362
52 | 2682339.0886 | 1245536.126
53 | 2682338.1127 | 1245535.1228
54 | 2682350.395 | 1245536.5602
55 | 2682207.6244 | 1245453.8312
56 | 2682191.0122 | 1245440.4062
57 | 2682121.3492 | 1245376.1786
58 | 2682175.8973 | 1245428.9891
59 | 2682160.2243 | 1245450.4267
60 | 2682226.1 | 1245310.8837
61 | 2682238.2112 | 1245299.0096
62 | 2682221.2709 | 1245350.0778
63 | 2682279.3963 | 1245355.9332
64 | 2682271.9733 | 1245355.3492
65 | 2682279.076 | 1245364.3964
66 | 2682083.8959 | 1245358.5714
67 | 2682081.2591 | 1245245.0301
68 | 2682080.7816 | 1245380.1273
69 | 2681983.3648 | 1245402.282
70 | 2681972.0355 | 1245373.2132
71 | 2681991.2424 | 1245380.9287
72 | 2681981.3097 | 1245351.2125
73 | 2682104.5497 | 1245347.7176
74 | 2682233.5073 | 1245337.5952
75 | 2682259.0622 | 1245377.789
76 | 2682276.3054 | 1245437.7915
77 | 2682214.0133 | 1245487.9842
78 | 2682213.7291 | 1245410.2751
79 | 2682225.8553 | 1245574.0402
80 | 2682224.8658 | 1245547.496
81 | 2682164.484 | 1245550.8504
82 | 2682163.3823 | 1245524.8772
83 | 2682184.8934 | 1245424.9652
84 | 2682281.3941 | 1245580.0949
85 | 2682316.4487 | 1245589.1606
86 | 2682164.5955 | 1245383.7551
87 | 2682164.1623 | 1245350.318
88 | 2682121.6611 | 1245430.7051
89 | 2682250.0141 | 1245454.4598
90 | 2682250.233 | 1245449.3413
91 | 2682274.7697 | 1245478.5219
92 | 2682275.0755 | 1245470.4085
93 | 2682232.0039 | 1245349.9273
94 | 2682247.1352 | 1245351.9585
95 | 2682224.0817 | 1245526.4605
96 | 2682337.5722 | 1245518.0435
97 | 2682339.7164 | 1245455.8347
98 | 2682338.664 | 1245486.367
99 | 2682160.921 | 1245466.8516
100 | 2682129.6998 | 1245561.6153
101 | 2682128.5168 | 1245545.0213
102 | 2682216.5736 | 1245548.6673
103 | 2682215.6222 | 1245526.1177
104 | 2682219.6674 | 1245362.8767
105 | 2682263.6701 | 1245354.696
106 | 2682078.3073 | 1245396.5551
107 | 2682175.2799 | 1245338.617
108 | 2682171.933 | 1245352.7564
109 | 2682275.3852 | 1245462.1933
110 | 2682275.8357 | 1245450.2414
111 | 2682250.3191 | 1245446.3384
112 | 2682250.9299 | 1245425.0256
113 | 2682251.0239 | 1245421.7432
114 | 2682261.2057 | 1245354.5021
115 | 2682278.5004 | 1245582.1745
116 | 2682162.2966 | 1245499.2813
117 | 2682161.1722 | 1245472.774
118 | 2682127.9172 | 1245536.6102
119 | 2682126.7925 | 1245520.8352
120 | 2682125.8722 | 1245504.9611
121 | 2682125.1296 | 1245491.8659
122 | 2682123.9023 | 1245470.2243
123 | 2682123.4364 | 1245462.0098
124 | 2682122.3721 | 1245443.2423
125 | 2682214.8259 | 1245507.2454
126 | 2682215.6202 | 1245526.0722
127 | 2682214.8261 | 1245507.2485
128 | 2682077.3803 | 1245402.7075
129 | 2682215.3265 | 1245397.525
130 | 2682216.6883 | 1245386.6549
131 | 2682218.0529 | 1245375.7631
132 | 2682167.0737 | 1245373.2854
133 | 2682169.5301 | 1245362.908
134 | 2682206.3035 | 1245451.9565

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98461 | -0.29595 | 0.012201 | 0.0030578
1 | 0.98574 | -0.27387 | 0.0059031 | 0.0014795
2 | 0.98383 | -0.31119 | 0.010478 | 0.0026261
3 | 0.98739 | -0.24182 | 0.0042474 | 0.0010645
4 | 0.98336 | -0.32037 | 0.0082527 | 0.0020683
5 | 0.98758 | -0.23816 | 0 | 0
6 | 0.98312 | -0.32503 | 0.0041665 | 0.0010442
7 | 0.98756 | -0.23859 | 0.0059791 | 0.0014985
8 | 0.98684 | -0.25265 | 0.0060619 | 0.0015193
9 | 0.99592 | -0.077705 | 0 | 0
10 | 0.98294 | -0.3286 | 0.0069455 | 0.0017407
11 | 0.98497 | -0.28909 | 0.0010166 | 0.00025479
12 | 0.98517 | -0.28512 | 0.00085254 | 0.00021367
13 | 0.9848 | -0.2924 | 0.00085263 | 0.00021369
14 | 0.98537 | -0.28128 | 0.0016616 | 0.00041643
15 | 0.98462 | -0.29579 | 0.0023496 | 0.00058885
16 | 0.98552 | -0.27827 | 0.0024051 | 0.00060278
17 | 0.98455 | -0.29719 | 0.0036767 | 0.00092146
18 | 0.98575 | -0.27373 | 0 | 0
19 | 0.97311 | -0.51797 | 0.0060163 | 0.0015078
20 | 0.97306 | -0.51903 | 0.0026342 | 0.0006602
21 | 0.97322 | -0.51571 | 0 | 0
22 | 0.97304 | -0.51938 | 0.002645 | 0.00066291
23 | 0.97416 | -0.49724 | 0 | 0
24 | 0.9727 | -0.52599 | 0.0036314 | 0.0009101
25 | 0.97497 | -0.48131 | 0.0026729 | 0.00066988
26 | 0.97409 | -0.49873 | 0.0034033 | 0.00085296
27 | 0.97245 | -0.53104 | 0.0036705 | 0.0009199
28 | 0.99498 | -0.095909 | 0.0068144 | 0.0017078
29 | 0.99675 | -0.06189 | 0 | 0
30 | 0.97756 | -0.43273 | 0 | 0
31 | 0.97725 | -0.43894 | 0.017644 | 0.004422
32 | 0.97987 | -0.38741 | 0 | 0
33 | 0.99636 | -0.0694 | 0.0057521 | 0.0014416
34 | 0.99719 | -0.053353 | 0.010719 | 0.0026864
35 | 0.99749 | -0.047625 | 0 | 0
36 | 0.99762 | -0.045046 | 0 | 0
37 | 0.99665 | -0.063478 | 0.013777 | 0.0034529
38 | 0.99515 | -0.092286 | 0 | 0
39 | 0.99367 | -0.12063 | 0 | 0
40 | 0.99627 | -0.070874 | 0 | 0
41 | 0.99505 | -0.09417 | 0.0052054 | 0.0013046
42 | 0.98594 | -0.27021 | 0 | 0
43 | 0.9865 | -0.25921 | 0 | 0
44 | 0.98584 | -0.272 | 0.0027019 | 0.00067715
45 | 0.99304 | -0.13266 | 0 | 0
46 | 0.99362 | -0.12166 | 0.0070822 | 0.001775
47 | 0.99285 | -0.13639 | 0 | 0
48 | 0.99281 | -0.13717 | 0.0090527 | 0.0022688
49 | 0.99815 | -0.035108 | 0 | 0
50 | 0.9912 | -0.16734 | 0 | 0
51 | 0.9843 | -0.30047 | 0.0075559 | 0.0018937
52 | 0.98571 | -0.27452 | 0 | 0
53 | 0.98572 | -0.27448 | 0 | 0
54 | 0.9857 | -0.2748 | 0.0013855 | 0.00034724
55 | 0.99803 | -0.037412 | 0.0059606 | 0.0014939
56 | 1 | 0 | -0.59603 | -0.15195
57 | 0.99103 | -0.17118 | 0.0038932 | 0.00097573
58 | 0.99842 | -0.029976 | 0.0064932 | 0.0016273
59 | 0.99506 | -0.09418 | 0.0046505 | 0.0011655
60 | 0.98539 | -0.27836 | 0 | 0
61 | 0.98342 | -0.31645 | 0 | 0
62 | 0.98868 | -0.21519 | 0.0060045 | 0.0015049
63 | 0.97596 | -0.46192 | 0 | 0
64 | 0.97642 | -0.45294 | 0.0034655 | 0.00086853
65 | 0.97544 | -0.47213 | 0.0032323 | 0.00081009
66 | 0.98199 | -0.34629 | 0 | 0
67 | 0.98457 | -0.29595 | 0 | 0
68 | 0.98151 | -0.35556 | 0.0039685 | 0.00099459
69 | 0.98008 | -0.3834 | 0.0023492 | 0.00058878
70 | 0.9804 | -0.37713 | 0 | 0
71 | 0.9805 | -0.37514 | 0 | 0
72 | 0.98028 | -0.37942 | 0.0052971 | 0.0013276
73 | 0.98933 | -0.20381 | 0.0047417 | 0.0011884
74 | 0.98018 | -0.37929 | 0.0085756 | 0.0021493
75 | 0.97395 | -0.50133 | 0.0071729 | 0.0017977
76 | 0.97222 | -0.53562 | 0.0037078 | 0.00092926
77 | 0.99636 | -0.069411 | 0.0041488 | 0.0010398
78 | 0.99477 | -0.099139 | 0.0090437 | 0.0022666
79 | 0.99422 | -0.11059 | 0.0075532 | 0.001893
80 | 0.9944 | -0.10705 | 0.008244 | 0.0020662
81 | 0.993 | -0.13395 | 0.0087872 | 0.0022023
82 | 0.99321 | -0.12991 | 0.0091236 | 0.0022866
83 | 0.99499 | -0.095266 | 0.0051916 | 0.0013011
84 | 0.98632 | -0.26274 | 0.00206 | 0.00051628
85 | 0.98579 | -0.27305 | 0.0021923 | 0.00054945
86 | 0.99332 | -0.12731 | 0.0037734 | 0.00094571
87 | 0.99262 | -0.14079 | 0.0064198 | 0.001609
88 | 0.98276 | -0.33053 | 0.0091035 | 0.0022816
89 | 0.97152 | -0.54946 | 0.0039442 | 0.0009885
90 | 0.97154 | -0.54909 | 0 | 0
91 | 0.97168 | -0.5462 | 0.0039914 | 0.0010003
92 | 0.97171 | -0.5456 | 0.0036617 | 0.0009177
93 | 0.97925 | -0.39753 | 0 | 0
94 | 0.9781 | -0.41999 | 0.0078167 | 0.001959
95 | 0.9947 | -0.10119 | 0.0050845 | 0.0012743
96 | 0.98561 | -0.27658 | 0.0034782 | 0.00087171
97 | 0.98548 | -0.27918 | 0.0013202 | 0.00033087
98 | 0.98551 | -0.27845 | 0.0019699 | 0.00049371
99 | 0.99448 | -0.10532 | 0.0021396 | 0.00053623
100 | 0.97752 | -0.43323 | 0.0094587 | 0.0023706
101 | 0.97766 | -0.43036 | 0.004626 | 0.0011594
102 | 0.99552 | -0.085627 | 0.0075305 | 0.0018873
103 | 0.99567 | -0.082639 | 0.0032072 | 0.00080379
104 | 0.98983 | -0.19327 | 0.0075561 | 0.0018937
105 | 0.97695 | -0.44239 | 0.0036554 | 0.00091614
106 | 0.98121 | -0.36145 | 0 | 0
107 | 0.9928 | -0.13745 | 0.0067928 | 0.0017024
108 | 0.99289 | -0.1357 | 0.0041609 | 0.0010428
109 | 0.97177 | -0.54444 | 0.0040844 | 0.0010236
110 | 0.9719 | -0.54185 | 0 | 0
111 | 0.9715 | -0.54972 | 0.0036954 | 0.00092614
112 | 0.97135 | -0.55277 | 0.0038601 | 0.00096743
113 | 0.97134 | -0.553 | 0.0038636 | 0.00096832
114 | 0.97712 | -0.43909 | 0 | 0
115 | 0.98631 | -0.26287 | 0.002094 | 0.00052481
116 | 0.99363 | -0.12181 | 0.0091996 | 0.0023056
117 | 0.99429 | -0.10912 | 0.0092176 | 0.0023101
118 | 0.97777 | -0.4282 | 0.0035589 | 0.00089194
119 | 0.97803 | -0.42311 | 0.0076307 | 0.0019124
120 | 0.9784 | -0.41579 | 0.013217 | 0.0033125
121 | 0.97887 | -0.4066 | 0.0081475 | 0.0020419
122 | 0.97981 | -0.38823 | 0.0225 | 0.005639
123 | 0.98033 | -0.37791 | 0.0084162 | 0.0021093
124 | 0.98169 | -0.3515 | 0.014888 | 0.0037313
125 | 0.99594 | -0.077445 | 0.0038149 | 0.0009561
126 | 0.99567 | -0.08263 | 0.0049144 | 0.0012317
127 | 0.99594 | -0.077447 | 0.0042602 | 0.0010677
128 | 0.9811 | -0.36365 | 0.019576 | 0.0049062
129 | 0.99334 | -0.12626 | 0.0058691 | 0.0014709
130 | 0.99219 | -0.1483 | 0.0047494 | 0.0011903
131 | 0.99107 | -0.16951 | 0.0060477 | 0.0015157
132 | 0.99314 | -0.13092 | 0.0043402 | 0.0010877
133 | 0.993 | -0.13368 | 0.0037025 | 0.00092795
134 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.042077 | -0.010557 | 0.042122 | 0.010585 | 4.4355e-05 | 2.8015e-05 | 0.063595 | 0.063594 | 0.063595 | 0.98461 | -0.29595 | 0.98574 | -0.27387 | 17.471
1 | 0.029877 | 0.0074996 | -0.029855 | -0.0074861 | 2.1707e-05 | 1.3532e-05 | 0.045156 | 0.045156 | 0.045156 | 0.98461 | -0.29595 | 0.98383 | -0.31119 | 12.4055
2 | -0.048025 | -0.012065 | 0.048098 | 0.012111 | 7.3571e-05 | 4.6609e-05 | 0.072505 | 0.072505 | 0.072505 | 0.98574 | -0.27387 | 0.98739 | -0.24182 | 19.919
3 | 0.019377 | 0.00486 | -0.019368 | -0.0048549 | 8.4707e-06 | 5.0875e-06 | 0.029308 | 0.029308 | 0.029308 | 0.98383 | -0.31119 | 0.98336 | -0.32037 | 8.0518
4 | -0.052346 | -0.013176 | 0.052355 | 0.013182 | 9.162e-06 | 5.8135e-06 | 0.078906 | 0.078906 | 0.078906 | 0.98739 | -0.24182 | 0.98758 | -0.23816 | 21.6775
5 | 0.011116 | 0.0027866 | -0.011113 | -0.0027853 | 2.4677e-06 | 1.2843e-06 | 0.016821 | 0.016821 | 0.016821 | 0.98336 | -0.32037 | 0.98312 | -0.32503 | 4.621
6 | 0.0059792 | 0.0014985 | -0.0059791 | -0.0014985 | 1.2162e-07 | 2.6709e-08 | 0.009009 | 0.0090091 | 0.0090091 | 0.98758 | -0.23816 | 0.98756 | -0.23859 | 2.475
7 | 0.036142 | 0.0090774 | -0.036117 | -0.0090617 | 2.4979e-05 | 1.57e-05 | 0.054463 | 0.054463 | 0.054463 | 0.98758 | -0.23816 | 0.98684 | -0.25265 | 14.9625
8 | -0.094476 | -0.023758 | 0.095206 | 0.024224 | 0.00073012 | 0.00046604 | 0.14238 | 0.14238 | 0.14238 | 0.98758 | -0.23816 | 0.99592 | -0.077705 | 39.115
9 | 0.0069467 | 0.0017411 | -0.0069455 | -0.0017407 | 1.181e-06 | 3.9469e-07 | 0.010514 | 0.010514 | 0.010514 | 0.98312 | -0.32503 | 0.98294 | -0.3286 | 2.8886
10 | 0.030055 | 0.0075425 | -0.030046 | -0.0075366 | 9.3947e-06 | 5.8569e-06 | 0.045323 | 0.045323 | 0.045323 | 0.98684 | -0.25265 | 0.9865 | -0.25921 | 12.4514
11 | 0.027731 | 0.0069624 | -0.027707 | -0.0069475 | 2.406e-05 | 1.4912e-05 | 0.041438 | 0.041438 | 0.041438 | 0.99592 | -0.077705 | 0.99498 | -0.095909 | 11.3841
12 | -0.12294 | -0.031186 | 0.12303 | 0.031246 | 9.3563e-05 | 5.9784e-05 | 0.18382 | 0.18382 | 0.18382 | 0.99592 | -0.077705 | 0.99675 | -0.06189 | 50.4988
13 | -0.0078978 | -0.0019793 | 0.0078993 | 0.0019799 | 1.4916e-06 | 5.9893e-07 | 0.011931 | 0.011931 | 0.011931 | 0.98497 | -0.28909 | 0.98517 | -0.28512 | 3.2778
14 | 0.0068812 | 0.0017245 | -0.0068801 | -0.0017241 | 1.085e-06 | 3.537e-07 | 0.010396 | 0.010396 | 0.010396 | 0.98497 | -0.28909 | 0.9848 | -0.2924 | 2.8559
15 | -0.0087518 | -0.0021935 | 0.0087534 | 0.0021942 | 1.6019e-06 | 7.1389e-07 | 0.013219 | 0.013219 | 0.013219 | 0.98517 | -0.28512 | 0.98537 | -0.28128 | 3.6316
16 | 0.0060275 | 0.0015104 | -0.0060265 | -0.0015102 | 9.7389e-07 | 2.2498e-07 | 0.0091073 | 0.0091075 | 0.0091075 | 0.9848 | -0.2924 | 0.98462 | -0.29579 | 2.5021
17 | -0.010415 | -0.0026107 | 0.010416 | 0.0026114 | 1.4963e-06 | 7.5214e-07 | 0.015728 | 0.015728 | 0.015728 | 0.98537 | -0.28128 | 0.98552 | -0.27827 | 4.3209
18 | 0.0036769 | 0.00092135 | -0.0036767 | -0.00092146 | 2.4542e-07 | -1.1249e-07 | 0.0055567 | 0.0055568 | 0.0055568 | 0.98462 | -0.29579 | 0.98455 | -0.29719 | 1.5266
19 | -0.012822 | -0.0032142 | 0.012824 | 0.0032157 | 2.7714e-06 | 1.5224e-06 | 0.019359 | 0.019359 | 0.019359 | 0.98552 | -0.27827 | 0.98575 | -0.27373 | 5.3185
20 | 0.0081551 | 0.0020431 | -0.0081548 | -0.002043 | 2.9232e-07 | 1.2151e-07 | 0.01231 | 0.01231 | 0.01231 | 0.98575 | -0.27373 | 0.98572 | -0.27448 | 3.3819
21 | -0.020979 | -0.0052589 | 0.020983 | 0.005261 | 3.5158e-06 | 2.1309e-06 | 0.031669 | 0.031669 | 0.031669 | 0.98575 | -0.27373 | 0.98594 | -0.27021 | 8.7003
22 | 0.0052796 | 0.0013231 | -0.0052793 | -0.0013231 | 2.6858e-07 | 3.5382e-08 | 0.0080732 | 0.0080732 | 0.0080732 | 0.97311 | -0.51797 | 0.97306 | -0.51903 | 2.2179
23 | -0.011296 | -0.0028309 | 0.011297 | 0.0028316 | 1.2154e-06 | 6.429e-07 | 0.017273 | 0.017273 | 0.017273 | 0.97311 | -0.51797 | 0.97322 | -0.51571 | 4.7453
24 | 0.0026451 | 0.00066285 | -0.002645 | -0.00066291 | 4.3405e-08 | -6.0097e-08 | 0.0040449 | 0.0040449 | 0.0040449 | 0.97306 | -0.51903 | 0.97304 | -0.51938 | 1.1112
25 | -0.049458 | -0.012414 | 0.049502 | 0.012441 | 4.3606e-05 | 2.7655e-05 | 0.075626 | 0.075626 | 0.075626 | 0.97322 | -0.51571 | 0.97416 | -0.49724 | 20.7763
26 | 0.038161 | 0.0095822 | -0.038142 | -0.0095704 | 1.8701e-05 | 1.1787e-05 | 0.058353 | 0.058353 | 0.058353 | 0.97322 | -0.51571 | 0.9727 | -0.52599 | 16.0311
27 | -0.06008 | -0.015093 | 0.060125 | 0.015122 | 4.5724e-05 | 2.9083e-05 | 0.091783 | 0.091783 | 0.091783 | 0.97416 | -0.49724 | 0.97497 | -0.48131 | 25.2152
28 | 0.010578 | 0.0026514 | -0.010577 | -0.002651 | 7.4959e-07 | 3.8442e-07 | 0.016158 | 0.016158 | 0.016158 | 0.97416 | -0.49724 | 0.97409 | -0.49873 | 4.4389
29 | 0.034511 | 0.0086603 | -0.034503 | -0.0086551 | 8.318e-06 | 5.2248e-06 | 0.052798 | 0.052798 | 0.052798 | 0.9727 | -0.52599 | 0.97245 | -0.53104 | 14.5049
30 | -0.062798 | -0.015792 | 0.062826 | 0.015809 | 2.7518e-05 | 1.7512e-05 | 0.095863 | 0.095863 | 0.095863 | 0.97497 | -0.48131 | 0.97544 | -0.47213 | 26.3359
31 | 0.0071738 | 0.001798 | -0.0071729 | -0.0017977 | 8.8906e-07 | 3.2329e-07 | 0.010959 | 0.010959 | 0.010959 | 0.97409 | -0.49873 | 0.97395 | -0.50133 | 3.0107
32 | 0.030832 | 0.0077351 | -0.030825 | -0.0077309 | 6.7248e-06 | 4.2039e-06 | 0.047181 | 0.047182 | 0.047182 | 0.97245 | -0.53104 | 0.97222 | -0.53562 | 12.962
33 | 0.020893 | 0.0052397 | -0.020887 | -0.0052365 | 5.2564e-06 | 3.1777e-06 | 0.031247 | 0.031247 | 0.031247 | 0.99498 | -0.095909 | 0.9947 | -0.10119 | 8.5843
34 | 0.033654 | 0.0084437 | -0.033642 | -0.0084362 | 1.2046e-05 | 7.5434e-06 | 0.050244 | 0.050245 | 0.050245 | 0.99675 | -0.06189 | 0.99636 | -0.0694 | 13.8034
35 | -0.15669 | -0.03969 | 0.15675 | 0.039731 | 6.4277e-05 | 4.0974e-05 | 0.23406 | 0.23406 | 0.23406 | 0.99675 | -0.06189 | 0.99719 | -0.053353 | 32.1511
36 | 0.017649 | 0.0044251 | -0.017644 | -0.004422 | 5.228e-06 | 3.1038e-06 | 0.026865 | 0.026866 | 0.026866 | 0.97756 | -0.43273 | 0.97725 | -0.43894 | 7.3806
37 | -0.017649 | -0.0044251 | 0.017687 | 0.0044477 | 3.8196e-05 | 2.2672e-05 | 0.026865 | 0.026865 | 0.026865 | 0.97756 | -0.43273 | 0.97987 | -0.38741 | 7.3806
38 | -0.017687 | -0.0044477 | 0.017691 | 0.0044497 | 3.3918e-06 | 2.0128e-06 | 0.026865 | 0.026865 | 0.026865 | 0.97987 | -0.38741 | 0.98008 | -0.3834 | 7.3804
39 | 0.02789 | 0.0069945 | -0.02789 | -0.0069945 | 1.366e-08 | 8.4674e-09 | 0.041654 | 0.041654 | 0.041654 | 0.99636 | -0.0694 | 0.99636 | -0.069411 | 11.4434
40 | -0.16747 | -0.042417 | 0.1676 | 0.042499 | 0.00012832 | 8.1482e-05 | 0.25005 | 0.25005 | 0.25005 | 0.99719 | -0.053353 | 0.99803 | -0.037412 | 22.8988
41 | -0.14462 | -0.037085 | 0.14464 | 0.037097 | 1.8092e-05 | 1.1457e-05 | 0.21604 | 0.21604 | 0.21604 | 0.99749 | -0.047625 | 0.99762 | -0.045046 | 19.7838
42 | 0.14462 | 0.037085 | -0.14451 | -0.037014 | 0.00011109 | 7.0765e-05 | 0.21604 | 0.21604 | 0.21604 | 0.99749 | -0.047625 | 0.99665 | -0.063478 | 29.6757
43 | -0.14464 | -0.037097 | 0.14471 | 0.037141 | 6.9752e-05 | 4.4173e-05 | 0.21604 | 0.21604 | 0.21604 | 0.99762 | -0.045046 | 0.99815 | -0.035108 | 19.7838
44 | 0.13073 | 0.033561 | -0.13051 | -0.033417 | 0.00022586 | 0.00014434 | 0.19547 | 0.19547 | 0.19547 | 0.99665 | -0.063478 | 0.99477 | -0.099139 | 53.7005
45 | 0.10363 | 0.026288 | -0.10349 | -0.026198 | 0.00014105 | 9.0066e-05 | 0.15507 | 0.15507 | 0.15507 | 0.99515 | -0.092286 | 0.99367 | -0.12063 | 42.602
46 | -0.11403 | -0.028895 | 0.11415 | 0.02897 | 0.00011743 | 7.5016e-05 | 0.17062 | 0.17062 | 0.17062 | 0.99515 | -0.092286 | 0.99627 | -0.070874 | 46.8735
47 | 0.010398 | 0.0026062 | -0.010397 | -0.0026058 | 9.3332e-07 | 4.6358e-07 | 0.015548 | 0.015548 | 0.015548 | 0.99515 | -0.092286 | 0.99505 | -0.09417 | 4.2715
48 | 0.073626 | 0.018708 | -0.073583 | -0.018681 | 4.2625e-05 | 2.7159e-05 | 0.11035 | 0.11035 | 0.11035 | 0.99367 | -0.12063 | 0.99304 | -0.13266 | 30.3146
49 | 0.029866 | 0.00749 | -0.029865 | -0.0074891 | 1.4573e-06 | 9.0752e-07 | 0.044726 | 0.044726 | 0.044726 | 0.99367 | -0.12063 | 0.99362 | -0.12166 | 12.2875
50 | -0.26813 | -0.068243 | 0.26866 | 0.068582 | 0.00052981 | 0.00033862 | 0.40085 | 0.40085 | 0.40085 | 0.99627 | -0.070874 | 0.99842 | -0.029976 | 55.0619
51 | 0.043218 | 0.010869 | -0.04317 | -0.010838 | 4.8051e-05 | 3.0353e-05 | 0.064563 | 0.064564 | 0.064564 | 0.99627 | -0.070874 | 0.99506 | -0.09418 | 17.7372
52 | 0.11077 | 0.028405 | -0.11025 | -0.028076 | 0.00051557 | 0.00032932 | 0.16567 | 0.16567 | 0.16567 | 0.99627 | -0.070874 | 0.9912 | -0.16734 | 45.5134
53 | 0.0051919 | 0.0013012 | -0.0051916 | -0.0013011 | 2.7125e-07 | 1.7738e-08 | 0.007764 | 0.0077641 | 0.0077641 | 0.99505 | -0.09417 | 0.99499 | -0.095266 | 2.133
54 | -0.025878 | -0.0064873 | 0.025891 | 0.0064957 | 1.3575e-05 | 8.385e-06 | 0.039056 | 0.039056 | 0.039056 | 0.98594 | -0.27021 | 0.9865 | -0.25921 | 10.7298
55 | 0.0048947 | 0.0012263 | -0.0048943 | -0.0012263 | 4.1598e-07 | 7.0213e-09 | 0.0073872 | 0.0073873 | 0.0073873 | 0.98594 | -0.27021 | 0.98584 | -0.272 | 2.0295
56 | 0.0041547 | 0.0010409 | -0.004154 | -0.0010411 | 6.9837e-07 | -1.5836e-07 | 0.0062668 | 0.006267 | 0.006267 | 0.9865 | -0.25921 | 0.98632 | -0.26274 | 1.7217
57 | 0.0021924 | 0.00054918 | -0.0021923 | -0.00054945 | 1.0962e-07 | -2.702e-07 | 0.0033091 | 0.0033092 | 0.0033092 | 0.98584 | -0.272 | 0.98579 | -0.27305 | 0.90913
58 | 0.058106 | 0.014801 | -0.058096 | -0.014795 | 1.0445e-05 | 6.6375e-06 | 0.087154 | 0.087154 | 0.087154 | 0.99304 | -0.13266 | 0.99285 | -0.13639 | 23.9433
59 | 0.015477 | 0.00388 | -0.015474 | -0.0038781 | 3.3248e-06 | 1.9146e-06 | 0.023192 | 0.023192 | 0.023192 | 0.99304 | -0.13266 | 0.99281 | -0.13717 | 6.3714
60 | 0.022783 | 0.0057142 | -0.022777 | -0.0057104 | 6.1361e-06 | 3.7451e-06 | 0.03412 | 0.03412 | 0.03412 | 0.99362 | -0.12166 | 0.99332 | -0.12731 | 9.3737
61 | 0.058096 | 0.014795 | -0.057998 | -0.014733 | 9.7289e-05 | 6.1824e-05 | 0.087154 | 0.087154 | 0.087154 | 0.99285 | -0.13639 | 0.99103 | -0.17118 | 23.9434
62 | 0.0064209 | 0.0016093 | -0.0064198 | -0.001609 | 1.1066e-06 | 2.9627e-07 | 0.0096236 | 0.0096238 | 0.0096238 | 0.99281 | -0.13717 | 0.99262 | -0.14079 | 2.6439
63 | 0.17358 | 0.044005 | -0.17356 | -0.043992 | 1.9221e-05 | 1.2212e-05 | 0.25894 | 0.25894 | 0.25894 | 0.99815 | -0.035108 | 0.99803 | -0.037412 | 23.7126
64 | -0.31829 | -0.081145 | 0.31883 | 0.08149 | 0.00054042 | 0.00034512 | 0.47498 | 0.47498 | 0.47498 | 0.99815 | -0.035108 | 1 | 0 | 43.4963
65 | 0.11025 | 0.028076 | -0.10955 | -0.027627 | 0.00070297 | 0.00044903 | 0.16567 | 0.16567 | 0.16567 | 0.9912 | -0.16734 | 0.9843 | -0.30047 | 45.5134
66 | 0.10199 | 0.025733 | -0.10184 | -0.025639 | 0.00014656 | 9.359e-05 | 0.15425 | 0.15425 | 0.15425 | 0.9843 | -0.30047 | 0.98276 | -0.33053 | 42.3754
67 | -0.0013855 | -0.00034711 | 0.0013855 | 0.00034709 | 2.2933e-09 | -1.6353e-08 | 0.0020915 | 0.0020915 | 0.0020915 | 0.98571 | -0.27452 | 0.98572 | -0.27448 | 0.57459
68 | 0.0013855 | 0.00034711 | -0.0013855 | -0.00034724 | 1.8881e-08 | -1.3463e-07 | 0.0020915 | 0.0020916 | 0.0020916 | 0.98571 | -0.27452 | 0.9857 | -0.2748 | 0.57461
69 | 0.0067693 | 0.0016959 | -0.0067686 | -0.0016957 | 6.7633e-07 | 2.127e-07 | 0.010219 | 0.010219 | 0.010219 | 0.98572 | -0.27448 | 0.98561 | -0.27658 | 2.8073
70 | 0.27555 | 0.070464 | -0.27516 | -0.070209 | 0.00039905 | 0.00025465 | 0.41053 | 0.41053 | 0.41053 | 1 | 0 | 0.99842 | -0.029976 | 37.5941
71 | 0.054105 | 0.013757 | -0.05402 | -0.013703 | 8.4919e-05 | 5.3907e-05 | 0.081308 | 0.081308 | 0.081308 | 0.99103 | -0.17118 | 0.98933 | -0.20381 | 22.3375
72 | 0.03852 | 0.0096729 | -0.038499 | -0.00966 | 2.046e-05 | 1.2881e-05 | 0.057609 | 0.057609 | 0.057609 | 0.99506 | -0.09418 | 0.99448 | -0.10532 | 15.8267
73 | 0.090342 | 0.023004 | -0.090176 | -0.022898 | 0.00016562 | 0.0001057 | 0.13655 | 0.13655 | 0.13655 | 0.98539 | -0.27836 | 0.98342 | -0.31645 | 37.5144
74 | -0.090342 | -0.023004 | 0.090618 | 0.02318 | 0.00027614 | 0.00017622 | 0.13655 | 0.13655 | 0.13655 | 0.98539 | -0.27836 | 0.98868 | -0.21519 | 37.5143
75 | 0.090176 | 0.022898 | -0.089904 | -0.022724 | 0.00027181 | 0.00017346 | 0.13655 | 0.13655 | 0.13655 | 0.98342 | -0.31645 | 0.98018 | -0.37929 | 37.5144
76 | -0.096622 | -0.024685 | 0.096725 | 0.02475 | 0.00010253 | 6.5452e-05 | 0.14559 | 0.14559 | 0.14559 | 0.98868 | -0.21519 | 0.98983 | -0.19327 | 39.9969
77 | -0.06609 | -0.01664 | 0.066119 | 0.016658 | 2.8367e-05 | 1.8062e-05 | 0.10079 | 0.10079 | 0.10079 | 0.97596 | -0.46192 | 0.97642 | -0.45294 | 27.6905
78 | 0.06609 | 0.01664 | -0.066058 | -0.016619 | 3.2266e-05 | 2.0544e-05 | 0.10079 | 0.10079 | 0.10079 | 0.97596 | -0.46192 | 0.97544 | -0.47213 | 27.6905
79 | -0.069584 | -0.017526 | 0.069619 | 0.017549 | 3.5143e-05 | 2.2387e-05 | 0.10607 | 0.10607 | 0.10607 | 0.97642 | -0.45294 | 0.97695 | -0.44239 | 29.1414
80 | -0.023562 | -0.0059117 | 0.023619 | 0.0059465 | 5.6689e-05 | 3.4777e-05 | 0.035706 | 0.035706 | 0.035706 | 0.98199 | -0.34629 | 0.98457 | -0.29595 | 9.8095
81 | 0.023562 | 0.0059117 | -0.023552 | -0.0059053 | 1.0413e-05 | 6.3891e-06 | 0.035706 | 0.035707 | 0.035707 | 0.98199 | -0.34629 | 0.98151 | -0.35556 | 9.8095
82 | 0.025442 | 0.0064304 | -0.025346 | -0.006371 | 9.6215e-05 | 5.9382e-05 | 0.038471 | 0.038472 | 0.038472 | 0.98457 | -0.29595 | 0.9805 | -0.37514 | 10.5692
83 | -0.049061 | -0.012377 | 0.049279 | 0.012515 | 0.00021748 | 0.00013784 | 0.074177 | 0.074177 | 0.074177 | 0.98457 | -0.29595 | 0.98933 | -0.20381 | 20.3783
84 | 0.019583 | 0.0049107 | -0.019578 | -0.0049074 | 5.4917e-06 | 3.3048e-06 | 0.02969 | 0.02969 | 0.02969 | 0.98151 | -0.35556 | 0.98121 | -0.36145 | 8.1567
85 | -0.02004 | -0.0050385 | 0.020048 | 0.0050433 | 7.9041e-06 | 4.7717e-06 | 0.030432 | 0.030431 | 0.030432 | 0.98008 | -0.3834 | 0.9805 | -0.37514 | 8.3603
86 | -0.0052977 | -0.0013277 | 0.0052982 | 0.0013277 | 5.0185e-07 | 6.0131e-08 | 0.0080406 | 0.0080405 | 0.0080406 | 0.9804 | -0.37713 | 0.9805 | -0.37514 | 2.209
87 | 0.0052977 | 0.0013277 | -0.0052971 | -0.0013276 | 5.7886e-07 | 6.9432e-08 | 0.0080406 | 0.0080407 | 0.0080407 | 0.9804 | -0.37713 | 0.98028 | -0.37942 | 2.209
88 | 0.081328 | 0.020575 | -0.081257 | -0.02053 | 7.1095e-05 | 4.5345e-05 | 0.12353 | 0.12353 | 0.12353 | 0.98018 | -0.37929 | 0.97925 | -0.39753 | 33.9379
89 | 0.027118 | 0.0068017 | -0.02711 | -0.0067967 | 8.0489e-06 | 4.9969e-06 | 0.041507 | 0.041507 | 0.041507 | 0.97222 | -0.53562 | 0.9719 | -0.54185 | 11.4029
90 | 0.023741 | 0.0059548 | -0.023732 | -0.0059492 | 9.0893e-06 | 5.5662e-06 | 0.035458 | 0.035458 | 0.035458 | 0.99636 | -0.069411 | 0.99594 | -0.077445 | 9.7412
91 | 0.12146 | 0.031151 | -0.1213 | -0.031049 | 0.00015951 | 0.00010192 | 0.18194 | 0.18194 | 0.18194 | 0.99477 | -0.099139 | 0.99334 | -0.12626 | 49.9841
92 | -0.0075532 | -0.001893 | 0.0075545 | 0.0018935 | 1.273e-06 | 4.7016e-07 | 0.011305 | 0.011305 | 0.011305 | 0.99422 | -0.11059 | 0.9944 | -0.10705 | 3.1057
93 | -0.015799 | -0.0039596 | 0.015803 | 0.0039622 | 4.4118e-06 | 2.5504e-06 | 0.023641 | 0.023641 | 0.023641 | 0.9944 | -0.10705 | 0.9947 | -0.10119 | 6.4948
94 | -0.0087872 | -0.0022023 | 0.0087889 | 0.002203 | 1.6903e-06 | 7.4542e-07 | 0.013168 | 0.013168 | 0.013168 | 0.993 | -0.13395 | 0.99321 | -0.12991 | 3.6175
95 | -0.017912 | -0.0044896 | 0.017919 | 0.0044937 | 6.9189e-06 | 4.0964e-06 | 0.026836 | 0.026836 | 0.026836 | 0.99321 | -0.12991 | 0.99363 | -0.12181 | 7.3726
96 | 0.002094 | 0.00052477 | -0.002094 | -0.00052481 | 1.3337e-08 | -3.6943e-08 | 0.0031592 | 0.0031592 | 0.0031592 | 0.98632 | -0.26274 | 0.98631 | -0.26287 | 0.86791
97 | 0.019003 | 0.0047647 | -0.019 | -0.0047627 | 3.2697e-06 | 1.9534e-06 | 0.028468 | 0.028468 | 0.028468 | 0.99332 | -0.12731 | 0.99314 | -0.13092 | 7.8208
98 | 0.092741 | 0.023358 | -0.092649 | -0.023299 | 9.2907e-05 | 5.9302e-05 | 0.14046 | 0.14046 | 0.14046 | 0.98276 | -0.33053 | 0.98169 | -0.3515 | 38.5886
99 | -0.0039442 | -0.0009885 | 0.0039443 | 0.00098849 | 7.0113e-08 | -1.8567e-08 | 0.0060411 | 0.0060411 | 0.0060411 | 0.97152 | -0.54946 | 0.97154 | -0.54909 | 1.6596
100 | 0.011421 | 0.0028625 | -0.01142 | -0.0028623 | 3.4469e-07 | 1.834e-07 | 0.017492 | 0.017492 | 0.017492 | 0.97154 | -0.54909 | 0.9715 | -0.54972 | 4.8055
101 | -0.015365 | -0.003851 | 0.01537 | 0.0038541 | 5.3047e-06 | 3.0786e-06 | 0.023533 | 0.023533 | 0.023533 | 0.97154 | -0.54909 | 0.9719 | -0.54185 | 6.4651
102 | -0.0039914 | -0.0010003 | 0.0039915 | 0.0010003 | 1.1375e-07 | -2.7771e-08 | 0.0061124 | 0.0061124 | 0.0061124 | 0.97168 | -0.5462 | 0.97171 | -0.5456 | 1.6792
103 | -0.0076532 | -0.001918 | 0.0076536 | 0.0019182 | 4.2343e-07 | 1.6915e-07 | 0.01172 | 0.01172 | 0.01172 | 0.97171 | -0.5456 | 0.97177 | -0.54444 | 3.2197
104 | 0.081257 | 0.02053 | -0.08117 | -0.020474 | 8.7369e-05 | 5.5724e-05 | 0.12353 | 0.12353 | 0.12353 | 0.97925 | -0.39753 | 0.9781 | -0.41999 | 33.9379
105 | 0.073353 | 0.018515 | -0.073286 | -0.018472 | 6.7061e-05 | 4.2739e-05 | 0.11164 | 0.11164 | 0.11164 | 0.9781 | -0.41999 | 0.97712 | -0.43909 | 30.6709
106 | 0.0032904 | 0.000824 | -0.0032902 | -0.00082422 | 2.933e-07 | -2.1619e-07 | 0.0049675 | 0.0049676 | 0.0049676 | 0.98561 | -0.27658 | 0.98551 | -0.27845 | 1.3647
107 | -0.0013202 | -0.00033087 | 0.0013202 | 0.00033051 | 4.5521e-08 | -3.6012e-07 | 0.0019934 | 0.0019933 | 0.0019934 | 0.98548 | -0.27918 | 0.98551 | -0.27845 | 0.54764
108 | 0.03636 | 0.0091238 | -0.036353 | -0.0091196 | 6.5803e-06 | 4.1345e-06 | 0.054408 | 0.054408 | 0.054408 | 0.99448 | -0.10532 | 0.99429 | -0.10912 | 14.9472
109 | -0.0094587 | -0.0023706 | 0.00946 | 0.0023712 | 1.2933e-06 | 6.1915e-07 | 0.014398 | 0.014398 | 0.014398 | 0.97752 | -0.43323 | 0.97766 | -0.43036 | 3.9556
110 | -0.014086 | -0.0035306 | 0.014087 | 0.0035314 | 1.4534e-06 | 8.2445e-07 | 0.021439 | 0.021439 | 0.021439 | 0.97766 | -0.43036 | 0.97777 | -0.4282 | 5.8899
111 | -0.0075305 | -0.0018873 | 0.0075315 | 0.0018877 | 1.0723e-06 | 3.9277e-07 | 0.011256 | 0.011256 | 0.011256 | 0.99552 | -0.085627 | 0.99567 | -0.082639 | 3.0923
112 | -0.010739 | -0.0026915 | 0.010739 | 0.0026915 | 4.4014e-09 | 2.2252e-09 | 0.016049 | 0.016049 | 0.016049 | 0.99567 | -0.082639 | 0.99567 | -0.08263 | 4.409
113 | -0.10428 | -0.026644 | 0.1044 | 0.02672 | 0.00011997 | 7.661e-05 | 0.15695 | 0.15695 | 0.15695 | 0.98983 | -0.19327 | 0.99107 | -0.16951 | 43.1175
114 | -0.073275 | -0.018465 | 0.073286 | 0.018472 | 1.1555e-05 | 7.3639e-06 | 0.11164 | 0.11164 | 0.11164 | 0.97695 | -0.44239 | 0.97712 | -0.43909 | 30.6709
115 | 0.019578 | 0.0049074 | -0.019576 | -0.0049062 | 2.0568e-06 | 1.2377e-06 | 0.02969 | 0.02969 | 0.02969 | 0.98121 | -0.36145 | 0.9811 | -0.36365 | 8.1567
116 | -0.0067928 | -0.0017024 | 0.0067933 | 0.0017026 | 5.6478e-07 | 1.7355e-07 | 0.010181 | 0.010181 | 0.010181 | 0.9928 | -0.13745 | 0.99289 | -0.1357 | 2.797
117 | -0.010954 | -0.0027454 | 0.010955 | 0.0027459 | 1.0543e-06 | 5.3983e-07 | 0.016417 | 0.016417 | 0.016417 | 0.99289 | -0.1357 | 0.993 | -0.13368 | 4.5101
118 | -0.011738 | -0.0029418 | 0.011739 | 0.0029426 | 1.4489e-06 | 7.7913e-07 | 0.017974 | 0.017974 | 0.017974 | 0.97177 | -0.54444 | 0.9719 | -0.54185 | 4.9378
119 | 0.0077249 | 0.0019362 | -0.0077238 | -0.0019357 | 1.1194e-06 | 4.5242e-07 | 0.011832 | 0.011832 | 0.011832 | 0.9715 | -0.54972 | 0.97135 | -0.55277 | 3.2506
120 | 0.0038637 | 0.00096831 | -0.0038636 | -0.00096832 | 4.3139e-08 | -1.3038e-08 | 0.0059188 | 0.0059188 | 0.0059188 | 0.97135 | -0.55277 | 0.97134 | -0.553 | 1.626
121 | -0.027119 | -0.0067994 | 0.027135 | 0.0068095 | 1.641e-05 | 1.0159e-05 | 0.040613 | 0.040613 | 0.040613 | 0.99363 | -0.12181 | 0.99429 | -0.10912 | 11.1575
122 | -0.017646 | -0.0044233 | 0.017651 | 0.0044259 | 4.2772e-06 | 2.539e-06 | 0.026855 | 0.026855 | 0.026855 | 0.97777 | -0.4282 | 0.97803 | -0.42311 | 7.3778
123 | -0.025281 | -0.0063383 | 0.02529 | 0.0063438 | 8.8223e-06 | 5.4466e-06 | 0.038465 | 0.038465 | 0.038465 | 0.97803 | -0.42311 | 0.9784 | -0.41579 | 10.5673
124 | -0.038507 | -0.0096562 | 0.038524 | 0.0096669 | 1.6871e-05 | 1.0632e-05 | 0.058566 | 0.058566 | 0.058566 | 0.9784 | -0.41579 | 0.97887 | -0.4066 | 16.0896
125 | -0.046671 | -0.011709 | 0.046712 | 0.011735 | 4.092e-05 | 2.5916e-05 | 0.070951 | 0.070951 | 0.070951 | 0.97887 | -0.4066 | 0.97981 | -0.38823 | 19.4921
126 | -0.069212 | -0.017374 | 0.069246 | 0.017395 | 3.4095e-05 | 2.1717e-05 | 0.10512 | 0.10512 | 0.10512 | 0.97981 | -0.38823 | 0.98033 | -0.37791 | 28.8795
127 | -0.077663 | -0.019505 | 0.077761 | 0.019567 | 9.7979e-05 | 6.2469e-05 | 0.1179 | 0.1179 | 0.1179 | 0.98033 | -0.37791 | 0.98169 | -0.3515 | 32.389
128 | 0.019917 | 0.0049931 | -0.019917 | -0.0049931 | 1.0368e-09 | 6.0565e-10 | 0.029758 | 0.029758 | 0.029758 | 0.99594 | -0.077445 | 0.99594 | -0.077447 | 8.1754
129 | -0.015653 | -0.0039232 | 0.015657 | 0.0039254 | 3.8664e-06 | 2.2294e-06 | 0.023393 | 0.023393 | 0.023393 | 0.99567 | -0.08263 | 0.99594 | -0.077447 | 6.4268
130 | 0.11543 | 0.029578 | -0.11531 | -0.029499 | 0.00012317 | 7.8685e-05 | 0.17315 | 0.17315 | 0.17315 | 0.99334 | -0.12626 | 0.99219 | -0.1483 | 47.5688
131 | 0.11056 | 0.028309 | -0.11045 | -0.028236 | 0.00011347 | 7.2478e-05 | 0.16603 | 0.16603 | 0.16603 | 0.99219 | -0.1483 | 0.99107 | -0.16951 | 45.612
132 | 0.01466 | 0.003675 | -0.014658 | -0.0036739 | 1.9294e-06 | 1.0968e-06 | 0.021965 | 0.021965 | 0.021965 | 0.99314 | -0.13092 | 0.993 | -0.13368 | 6.0343

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.60042 | 0.15305

## res_load
| p_mw | q_mvar
0 | 0.012201 | 0.0030578
1 | 0.0059031 | 0.0014795
2 | 0.010478 | 0.0026261
3 | 0.0042474 | 0.0010645
4 | 0.0082527 | 0.0020683
5 | 0.0041665 | 0.0010442
6 | 0.0059791 | 0.0014985
7 | 0.0060619 | 0.0015193
8 | 0.0069455 | 0.0017407
9 | 0.0010166 | 0.00025479
10 | 0.00085254 | 0.00021367
11 | 0.00085263 | 0.00021369
12 | 0.0016616 | 0.00041643
13 | 0.0023496 | 0.00058885
14 | 0.0024051 | 0.00060278
15 | 0.0036767 | 0.00092146
16 | 0.0060163 | 0.0015078
17 | 0.0026342 | 0.0006602
18 | 0.002645 | 0.00066291
19 | 0.0036314 | 0.0009101
20 | 0.0026729 | 0.00066988
21 | 0.0034033 | 0.00085296
22 | 0.0036705 | 0.0009199
23 | 0.0068144 | 0.0017078
24 | 0.017644 | 0.004422
25 | 0.0057521 | 0.0014416
26 | 0.010719 | 0.0026864
27 | 0.013777 | 0.0034529
28 | 0.0052054 | 0.0013046
29 | 0.0027019 | 0.00067715
30 | 0.0070822 | 0.001775
31 | 0.0090527 | 0.0022688
32 | 0.0075559 | 0.0018937
33 | 0.0013855 | 0.00034724
34 | 0.0059606 | 0.0014939
35 | 0.0043865 | 0.0010994
36 | 0.0038932 | 0.00097573
37 | 0.0064932 | 0.0016273
38 | 0.0046505 | 0.0011655
39 | 0.0060045 | 0.0015049
40 | 0.0034655 | 0.00086853
41 | 0.0032323 | 0.00081009
42 | 0.0039685 | 0.00099459
43 | 0.0023492 | 0.00058878
44 | 0.0052971 | 0.0013276
45 | 0.0047417 | 0.0011884
46 | 0.0085756 | 0.0021493
47 | 0.0071729 | 0.0017977
48 | 0.0037078 | 0.00092926
49 | 0.0041488 | 0.0010398
50 | 0.0090437 | 0.0022666
51 | 0.0075532 | 0.001893
52 | 0.008244 | 0.0020662
53 | 0.0087872 | 0.0022023
54 | 0.0091236 | 0.0022866
55 | 0.0051916 | 0.0013011
56 | 0.00206 | 0.00051628
57 | 0.0021923 | 0.00054945
58 | 0.0037734 | 0.00094571
59 | 0.0064198 | 0.001609
60 | 0.0091035 | 0.0022816
61 | 0.0039442 | 0.0009885
62 | 0.0039914 | 0.0010003
63 | 0.0036617 | 0.0009177
64 | 0.0078167 | 0.001959
65 | 0.0050845 | 0.0012743
66 | 0.0034782 | 0.00087171
67 | 0.0013202 | 0.00033087
68 | 0.0019699 | 0.00049371
69 | 0.0021396 | 0.00053623
70 | 0.0094587 | 0.0023706
71 | 0.004626 | 0.0011594
72 | 0.0075305 | 0.0018873
73 | 0.0032072 | 0.00080379
74 | 0.0075561 | 0.0018937
75 | 0.0036554 | 0.00091614
76 | 0.0067928 | 0.0017024
77 | 0.0041609 | 0.0010428
78 | 0.0040844 | 0.0010236
79 | 0.0036954 | 0.00092614
80 | 0.0038601 | 0.00096743
81 | 0.0038636 | 0.00096832
82 | 0.002094 | 0.00052481
83 | 0.0091996 | 0.0023056
84 | 0.0092176 | 0.0023101
85 | 0.0035589 | 0.00089194
86 | 0.0076307 | 0.0019124
87 | 0.013217 | 0.0033125
88 | 0.0081475 | 0.0020419
89 | 0.0225 | 0.005639
90 | 0.0084162 | 0.0021093
91 | 0.014888 | 0.0037313
92 | 0.0038149 | 0.0009561
93 | 0.0049144 | 0.0012317
94 | 0.0042602 | 0.0010677
95 | 0.019576 | 0.0049062
96 | 0.0058691 | 0.0014709
97 | 0.0047494 | 0.0011903
98 | 0.0060477 | 0.0015157
99 | 0.0043402 | 0.0010877
100 | 0.0037025 | 0.00092795

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1