## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-520_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-520_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-520_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_261-520_0_5_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_261-520_0_5_node_25 | 0.4 | n |  | TRUE
5 | bus_LV_261-520_0_5_node_9 | 0.4 | n |  | TRUE
6 | bus_LV_261-520_0_5_node_27 | 0.4 | n |  | TRUE
7 | bus_LV_261-520_0_5_node_4 | 0.4 | n |  | TRUE
8 | bus_LV_261-520_0_5_node_28 | 0.4 | n |  | TRUE
9 | bus_LV_261-520_0_5_node_26 | 0.4 | n |  | TRUE
10 | bus_LV_261-520_0_5_node_5 | 0.4 | n |  | TRUE
11 | bus_LV_261-520_0_5_node_8 | 0.4 | n |  | TRUE
12 | bus_LV_261-520_0_5_node_41 | 0.4 | n |  | TRUE
13 | bus_LV_261-520_0_5_node_6 | 0.4 | n |  | TRUE
14 | bus_LV_261-520_0_5_node_30 | 0.4 | n |  | TRUE
15 | bus_LV_261-520_0_5_node_34 | 0.4 | n |  | TRUE
16 | bus_LV_261-520_0_5_node_7 | 0.4 | n |  | TRUE
17 | bus_LV_261-520_0_5_node_35 | 0.4 | n |  | TRUE
18 | bus_LV_261-520_0_5_node_36 | 0.4 | n |  | TRUE
19 | bus_LV_261-520_0_5_node_33 | 0.4 | n |  | TRUE
20 | bus_LV_261-520_0_5_node_73 | 0.4 | n |  | TRUE
21 | bus_LV_261-520_0_5_node_10 | 0.4 | n |  | TRUE
22 | bus_LV_261-520_0_5_node_16 | 0.4 | n |  | TRUE
23 | bus_LV_261-520_0_5_node_11 | 0.4 | n |  | TRUE
24 | bus_LV_261-520_0_5_node_15 | 0.4 | n |  | TRUE
25 | bus_LV_261-520_0_5_node_14 | 0.4 | n |  | TRUE
26 | bus_LV_261-520_0_5_node_59 | 0.4 | n |  | TRUE
27 | bus_LV_261-520_0_5_node_12 | 0.4 | n |  | TRUE
28 | bus_LV_261-520_0_5_node_63 | 0.4 | n |  | TRUE
29 | bus_LV_261-520_0_5_node_64 | 0.4 | n |  | TRUE
30 | bus_LV_261-520_0_5_node_13 | 0.4 | n |  | TRUE
31 | bus_LV_261-520_0_5_node_62 | 0.4 | n |  | TRUE
32 | bus_LV_261-520_0_5_node_51 | 0.4 | n |  | TRUE
33 | bus_LV_261-520_0_5_node_50 | 0.4 | n |  | TRUE
34 | bus_LV_261-520_0_5_node_38 | 0.4 | n |  | TRUE
35 | bus_LV_261-520_0_5_node_75 | 0.4 | n |  | TRUE
36 | bus_LV_261-520_0_5_node_18 | 0.4 | n |  | TRUE
37 | bus_LV_261-520_0_5_node_74 | 0.4 | n |  | TRUE
38 | bus_LV_261-520_0_5_node_37 | 0.4 | n |  | TRUE
39 | bus_LV_261-520_0_5_node_19 | 0.4 | n |  | TRUE
40 | bus_LV_261-520_0_5_node_20 | 0.4 | n |  | TRUE
41 | bus_LV_261-520_0_5_node_66 | 0.4 | n |  | TRUE
42 | bus_LV_261-520_0_5_node_72 | 0.4 | n |  | TRUE
43 | bus_LV_261-520_0_5_node_52 | 0.4 | n |  | TRUE
44 | bus_LV_261-520_0_5_node_21 | 0.4 | n |  | TRUE
45 | bus_LV_261-520_0_5_node_22 | 0.4 | n |  | TRUE
46 | bus_LV_261-520_0_5_node_58 | 0.4 | n |  | TRUE
47 | bus_LV_261-520_0_5_node_42 | 0.4 | n |  | TRUE
48 | bus_LV_261-520_0_5_node_29 | 0.4 | n |  | TRUE
49 | bus_LV_261-520_0_5_node_49 | 0.4 | n |  | TRUE
50 | bus_LV_261-520_0_5_node_46 | 0.4 | n |  | TRUE
51 | bus_LV_261-520_0_5_node_39 | 0.4 | n |  | TRUE
52 | bus_LV_261-520_0_5_node_60 | 0.4 | n |  | TRUE
53 | bus_LV_261-520_0_5_node_43 | 0.4 | n |  | TRUE
54 | bus_LV_261-520_0_5_node_44 | 0.4 | n |  | TRUE
55 | bus_LV_261-520_0_5_node_56 | 0.4 | n |  | TRUE
56 | bus_LV_261-520_0_5_node_57 | 0.4 | n |  | TRUE
57 | bus_LV_261-520_0_5_node_67 | 0.4 | n |  | TRUE
58 | bus_LV_261-520_0_5_node_54 | 0.4 | n |  | TRUE
59 | bus_LV_261-520_0_5_node_31 | 0.4 | n |  | TRUE
60 | bus_LV_261-520_0_5_node_32 | 0.4 | n |  | TRUE
61 | bus_LV_261-520_0_5_node_40 | 0.4 | n |  | TRUE
62 | bus_LV_261-520_0_5_node_47 | 0.4 | n |  | TRUE
63 | bus_LV_261-520_0_5_node_48 | 0.4 | n |  | TRUE
64 | bus_LV_261-520_0_5_node_53 | 0.4 | n |  | TRUE
65 | bus_LV_261-520_0_5_node_55 | 0.4 | n |  | TRUE
66 | bus_LV_261-520_0_5_node_61 | 0.4 | n |  | TRUE
67 | bus_LV_261-520_0_5_node_70 | 0.4 | n |  | TRUE
68 | bus_LV_261-520_0_5_node_68 | 0.4 | n |  | TRUE
69 | bus_LV_261-520_0_5_node_69 | 0.4 | n |  | TRUE
70 | bus_LV_261-520_0_5_node_71 | 0.4 | n |  | TRUE
71 | bus_MV_545_0_node_40 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-520_0_5_load_0 | 0 | 0.0053745 | 0.001347 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-520_0_5_load_3 | 3 | 0.001929 | 0.00048345 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-520_0_5_load_25 | 4 | 0.017135 | 0.0042945 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-520_0_5_load_27 | 6 | 0.0066043 | 0.0016552 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-520_0_5_load_28 | 8 | 0.0041763 | 0.0010467 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-520_0_5_load_26 | 9 | 0.0066642 | 0.0016702 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-520_0_5_load_41 | 12 | 0.0089483 | 0.0022427 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-520_0_5_load_30 | 14 | 0.0031164 | 0.00078104 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-520_0_5_load_34 | 15 | 0.0067891 | 0.0017015 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-520_0_5_load_35 | 17 | 0.020118 | 0.0050419 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-520_0_5_load_36 | 18 | 0.039662 | 0.0099403 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-520_0_5_load_33 | 19 | 0.028965 | 0.0072593 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-520_0_5_load_73 | 20 | 0.0012516 | 0.00031369 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-520_0_5_load_59 | 26 | 0.016032 | 0.0040181 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-520_0_5_load_63 | 28 | 0.042373 | 0.01062 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-520_0_5_load_64 | 29 | 0.077824 | 0.019504 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-520_0_5_load_62 | 31 | 0.0049298 | 0.0012355 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_261-520_0_5_load_50 | 33 | 0.0023838 | 0.00059745 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_261-520_0_5_load_38 | 34 | 0.020393 | 0.0051109 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_261-520_0_5_load_75 | 35 | 0.033908 | 0.008498 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_261-520_0_5_load_74 | 37 | 0.003867 | 0.00096916 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_261-520_0_5_load_66 | 41 | 0.00097009 | 0.00024313 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_261-520_0_5_load_72 | 42 | 0.00055423 | 0.0001389 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_261-520_0_5_load_52 | 43 | 0.0017838 | 0.00044705 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_261-520_0_5_load_58 | 46 | 0.0047813 | 0.0011983 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_261-520_0_5_load_42 | 47 | 0.0093177 | 0.0023352 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_261-520_0_5_load_29 | 48 | 0.0046972 | 0.0011772 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_261-520_0_5_load_49 | 49 | 0.025047 | 0.0062774 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_261-520_0_5_load_46 | 50 | 0.0010451 | 0.00026193 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_261-520_0_5_load_39 | 51 | 0.0057266 | 0.0014352 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_261-520_0_5_load_60 | 52 | 0.015448 | 0.0038716 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_261-520_0_5_load_44 | 54 | 0.011542 | 0.0028927 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_261-520_0_5_load_56 | 55 | 0.0066841 | 0.0016752 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_261-520_0_5_load_57 | 56 | 0.0078957 | 0.0019788 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_261-520_0_5_load_67 | 57 | 0.0028503 | 0.00071435 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_261-520_0_5_load_54 | 58 | 0.0049907 | 0.0012508 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_261-520_0_5_load_31 | 59 | 0.0068729 | 0.0017225 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_261-520_0_5_load_32 | 60 | 0.032602 | 0.0081707 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_261-520_0_5_load_40 | 61 | 0.0068929 | 0.0017275 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_261-520_0_5_load_47 | 62 | 0.0010618 | 0.00026612 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_261-520_0_5_load_48 | 63 | 0.001259 | 0.00031553 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_261-520_0_5_load_53 | 64 | 0.0050477 | 0.0012651 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_261-520_0_5_load_55 | 65 | 0.0064789 | 0.0016238 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_261-520_0_5_load_61 | 66 | 0.00071414 | 0.00017898 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_261-520_0_5_load_70 | 67 | 0.00070668 | 0.00017711 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_261-520_0_5_load_68 | 68 | 0.00074092 | 0.00018569 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_261-520_0_5_load_69 | 69 | 0.00074769 | 0.00018739 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_261-520_0_5_load_71 | 70 | 0.0007704 | 0.00019308 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 18 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-520_0_5_line_0 |  | 0 | 1 | 0.0086147 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-520_0_5_line_1 |  | 0 | 2 | 0.022903 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-520_0_5_line_2 |  | 1 | 3 | 0.031169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-520_0_5_line_3 |  | 2 | 4 | 0.010832 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-520_0_5_line_4 |  | 2 | 5 | 0.033805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_261-520_0_5_line_5 |  | 3 | 6 | 0.0076244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_261-520_0_5_line_6 |  | 4 | 21 | 0.041948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_261-520_0_5_line_7 |  | 5 | 20 | 0.018695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_261-520_0_5_line_8 |  | 6 | 9 | 0.01534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_261-520_0_5_line_9 |  | 7 | 8 | 0.013246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_261-520_0_5_line_10 |  | 7 | 9 | 0.021248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_261-520_0_5_line_11 |  | 8 | 13 | 0.017918 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_261-520_0_5_line_12 |  | 10 | 11 | 0.049892 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-520_0_5_line_13 |  | 10 | 12 | 0.021903 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_261-520_0_5_line_14 |  | 11 | 20 | 0.039612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_261-520_0_5_line_15 |  | 12 | 47 | 0.034901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_261-520_0_5_line_16 |  | 13 | 14 | 0.0084443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_261-520_0_5_line_17 |  | 13 | 15 | 0.014171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
18 | LV_261-520_0_5_line_18 |  | 14 | 48 | 0.043358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_261-520_0_5_line_19 |  | 15 | 19 | 0.028909 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
20 | LV_261-520_0_5_line_20 |  | 16 | 17 | 0.016676 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
21 | LV_261-520_0_5_line_21 |  | 16 | 18 | 0.030972 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
22 | LV_261-520_0_5_line_22 |  | 16 | 19 | 0.016238 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
23 | LV_261-520_0_5_line_23 |  | 17 | 34 | 0.017722 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
24 | LV_261-520_0_5_line_24 |  | 18 | 51 | 0.013527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_261-520_0_5_line_25 |  | 21 | 22 | 0.10746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_261-520_0_5_line_26 |  | 22 | 35 | 0.14005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_261-520_0_5_line_27 |  | 23 | 24 | 0.005893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_261-520_0_5_line_28 |  | 23 | 25 | 0.055053 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_261-520_0_5_line_29 |  | 23 | 26 | 0.030748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_261-520_0_5_line_30 |  | 24 | 34 | 0.014164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
31 | LV_261-520_0_5_line_31 |  | 24 | 30 | 0.013331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_261-520_0_5_line_32 |  | 25 | 32 | 0.024005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_261-520_0_5_line_33 |  | 25 | 33 | 0.013169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_261-520_0_5_line_34 |  | 26 | 52 | 0.014263 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_261-520_0_5_line_35 |  | 27 | 28 | 0.011178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_261-520_0_5_line_36 |  | 27 | 29 | 0.017422 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_261-520_0_5_line_37 |  | 28 | 30 | 0.0072964 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_261-520_0_5_line_38 |  | 30 | 31 | 0.02602 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_261-520_0_5_line_39 |  | 32 | 55 | 0.05617 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_261-520_0_5_line_40 |  | 32 | 56 | 0.029449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_261-520_0_5_line_41 |  | 33 | 45 | 0.0027077 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_261-520_0_5_line_42 |  | 36 | 37 | 0.016758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_261-520_0_5_line_43 |  | 36 | 38 | 0.040219 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_261-520_0_5_line_44 |  | 38 | 49 | 0.013093 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_261-520_0_5_line_45 |  | 38 | 50 | 0.012626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_261-520_0_5_line_46 |  | 39 | 40 | 0.1492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_261-520_0_5_line_47 |  | 39 | 41 | 0.0023 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_261-520_0_5_line_48 |  | 40 | 42 | 0.018555 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_261-520_0_5_line_49 |  | 40 | 43 | 0.027587 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_261-520_0_5_line_50 |  | 41 | 57 | 0.013267 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_261-520_0_5_line_51 |  | 43 | 45 | 0.013946 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_261-520_0_5_line_52 |  | 44 | 45 | 0.011672 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_261-520_0_5_line_53 |  | 44 | 46 | 0.066217 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_261-520_0_5_line_54 |  | 46 | 58 | 0.014367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_261-520_0_5_line_55 |  | 47 | 53 | 0.016751 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_261-520_0_5_line_56 |  | 48 | 59 | 0.0036478 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_261-520_0_5_line_57 |  | 50 | 62 | 0.0088135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_261-520_0_5_line_58 |  | 51 | 61 | 0.002191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_261-520_0_5_line_59 |  | 52 | 66 | 0.014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_261-520_0_5_line_60 |  | 53 | 54 | 0.035552 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_261-520_0_5_line_61 |  | 55 | 65 | 0.040357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_261-520_0_5_line_62 |  | 58 | 64 | 0.016124 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_261-520_0_5_line_63 |  | 59 | 60 | 0.0062395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_261-520_0_5_line_64 |  | 62 | 63 | 0.023052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_261-520_0_5_line_65 |  | 63 | 64 | 0.013287 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_261-520_0_5_line_66 |  | 66 | 67 | 0.013935 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_261-520_0_5_line_67 |  | 67 | 68 | 0.012168 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_261-520_0_5_line_68 |  | 68 | 69 | 0.013971 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_261-520_0_5_line_69 |  | 69 | 70 | 0.0099772 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-520_0_5_trafo_36 | 0.63 MVA 20/0.4 kV | 71 | 18 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2681453.4343 | 1245897.207 | 2681461.6072 | 1245894.4837
1 | 2681483.3687 | 1245887.3443 | 2681472.1822 | 1245890.9599 | 2681461.6072 | 1245894.4837
2 | 2681453.4343 | 1245897.207 | 2681452.087 | 1245899.0343 | 2681449.9186 | 1245901.7843 | 2681448.8168 | 1245904.4378 | 2681448.2717 | 1245907.2657 | 2681448.3356 | 1245910.3132 | 2681449.0503 | 1245913.2919 | 2681454.1065 | 1245925.27 | 2681454.2537 | 1245925.7793
3 | 2681483.3687 | 1245887.3443 | 2681493.6749 | 1245884.0105
4 | 2681457.2017 | 1245881.4695 | 2681457.8012 | 1245887.3264 | 2681457.9671 | 1245888.9966 | 2681470.0047 | 1245885.0257 | 2681474.4367 | 1245885.7982 | 2681483.3687 | 1245887.3443
5 | 2681455.3937 | 1245933.2586 | 2681455.4824 | 1245932.3607 | 2681455.1162 | 1245928.7642 | 2681454.2537 | 1245925.7793
6 | 2681533.5869 | 1245871.1002 | 2681493.6749 | 1245884.0105
7 | 2681457.2017 | 1245881.4695 | 2681446.4165 | 1245885.024 | 2681441.2185 | 1245886.6538 | 2681439.3532 | 1245886.969
8 | 2681455.3937 | 1245933.2586 | 2681455.0523 | 1245936.7135 | 2681453.6881 | 1245940.8756 | 2681451.7551 | 1245944.0847 | 2681449.2613 | 1245946.8747
9 | 2681429.4279 | 1245951.3057 | 2681430.9041 | 1245964.4691
10 | 2681429.4279 | 1245951.3057 | 2681433.1726 | 1245952.0576 | 2681436.5857 | 1245952.1935 | 2681439.9768 | 1245951.7397 | 2681443.2397 | 1245950.7171 | 2681446.2833 | 1245949.1577 | 2681449.2613 | 1245946.8747
11 | 2681432.901 | 1245982.2759 | 2681430.9041 | 1245964.4691
12 | 2681402.8935 | 1245877.0097 | 2681397.3778 | 1245883.0717 | 2681392.8521 | 1245888.0244 | 2681403.5111 | 1245899.1565 | 2681408.1316 | 1245906.0138 | 2681410.1404 | 1245909.9331 | 2681410.9401 | 1245911.6675 | 2681412.3097 | 1245916.4676
13 | 2681412.3097 | 1245916.4676 | 2681415.2206 | 1245928.9722 | 2681416.687 | 1245937.9168
14 | 2681402.8935 | 1245877.0097 | 2681408.9263 | 1245881.707 | 2681415.2885 | 1245885.5193 | 2681422.6611 | 1245887.8333 | 2681431.2372 | 1245888.3403 | 2681439.3532 | 1245886.969
15 | 2681420.6635 | 1245972.5898 | 2681419.3102 | 1245960.1733 | 2681416.7334 | 1245938.1997 | 2681416.687 | 1245937.9168
16 | 2681432.901 | 1245982.2759 | 2681441.2949 | 1245981.3548
17 | 2681432.901 | 1245982.2759 | 2681434.4825 | 1245996.3587
18 | 2681484.394 | 1245976.625 | 2681441.2949 | 1245981.3548
19 | 2681434.4825 | 1245996.3587 | 2681436.9266 | 1246018.1239 | 2681438.1391 | 1246025.0254
20 | 2681440.9488 | 1246041.0181 | 2681444.5713 | 1246057.2958
21 | 2681440.9488 | 1246041.0181 | 2681460.475 | 1246037.4836 | 2681459.1047 | 1246026.4395
22 | 2681440.9488 | 1246041.0181 | 2681438.1391 | 1246025.0254
23 | 2681448.8272 | 1246074.4878 | 2681447.2607 | 1246069.3809 | 2681444.5713 | 1246057.2958
24 | 2681457.439 | 1246013.0153 | 2681459.1047 | 1246026.4395
25 | 2681533.5869 | 1245871.1002 | 2681539.4536 | 1245869.1906 | 2681565.1545 | 1245860.6265 | 2681618.5301 | 1245842.8255 | 2681623.8779 | 1245859.9448
26 | 2681542.2115 | 1245959.2607 | 2681544.9672 | 1245957.2082 | 2681553.2911 | 1245951.8743 | 2681557.8968 | 1245953.7501 | 2681564.2487 | 1245957.2066 | 2681621.4019 | 1245869.6623 | 2681623.224 | 1245865.1841 | 2681623.8779 | 1245859.9448
27 | 2681455.0733 | 1246093.5391 | 2681452.9807 | 1246088.0286
28 | 2681455.0733 | 1246093.5391 | 2681457.3333 | 1246099.519 | 2681462.6195 | 1246109.5878 | 2681467.2166 | 1246117.579 | 2681473.5789 | 1246126.862 | 2681483.7982 | 1246140.2677
29 | 2681455.0733 | 1246093.5391 | 2681461.0545 | 1246090.4301 | 2681467.0941 | 1246086.3656 | 2681472.129 | 1246081.1866 | 2681478.0552 | 1246073.7569
30 | 2681452.9807 | 1246088.0286 | 2681448.8272 | 1246074.4878
31 | 2681440.1622 | 1246091.6775 | 2681447.1153 | 1246089.8605 | 2681452.9807 | 1246088.0286
32 | 2681502.7461 | 1246125.4616 | 2681483.7982 | 1246140.2677
33 | 2681483.7982 | 1246140.2677 | 2681491.8138 | 1246150.7167
34 | 2681478.0552 | 1246073.7569 | 2681486.9493 | 1246062.6063
35 | 2681434.8445 | 1246073.9916 | 2681437.3475 | 1246083.1771 | 2681437.8687 | 1246084.751
36 | 2681434.8445 | 1246073.9916 | 2681433.2963 | 1246073.9481 | 2681417.5679 | 1246071.8059
37 | 2681440.1622 | 1246091.6775 | 2681437.8687 | 1246084.751
38 | 2681440.1622 | 1246091.6775 | 2681445.3684 | 1246104.2804 | 2681448.1513 | 1246105.7419 | 2681452.2229 | 1246114.0371
39 | 2681502.7461 | 1246125.4616 | 2681506.0065 | 1246119.124 | 2681510.1915 | 1246113.1216 | 2681535.9221 | 1246080.2741
40 | 2681502.7461 | 1246125.4616 | 2681499.1099 | 1246116.8276 | 2681505.3884 | 1246105.2832 | 2681509.7003 | 1246099.8456
41 | 2681493.4618 | 1246152.8652 | 2681491.8138 | 1246150.7167
42 | 2681368.2812 | 1246140.6934 | 2681375.9354 | 1246125.7765
43 | 2681345.9308 | 1246106.1729 | 2681343.9374 | 1246110.4931 | 2681369.0003 | 1246122.4345 | 2681375.9354 | 1246125.7765
44 | 2681345.9308 | 1246106.1729 | 2681334.0895 | 1246100.5866
45 | 2681345.9308 | 1246106.1729 | 2681357.3087 | 1246111.6469
46 | 2681518.314 | 1246186.142 | 2681536.3262 | 1246210.2516 | 2681543.5962 | 1246219.9919 | 2681552.2891 | 1246232.2871 | 2681580.2171 | 1246192.9869 | 2681573.4842 | 1246187.5904 | 2681570.0453 | 1246180.549 | 2681579.0696 | 1246166.5741 | 2681570.4428 | 1246160.451
47 | 2681570.4428 | 1246160.451 | 2681568.5816 | 1246159.0996
48 | 2681533.1031 | 1246174.8815 | 2681518.314 | 1246186.142
49 | 2681518.314 | 1246186.142 | 2681501.8068 | 1246164.039
50 | 2681557.8457 | 1246151.3044 | 2681568.5816 | 1246159.0996
51 | 2681493.4618 | 1246152.8652 | 2681501.8068 | 1246164.039
52 | 2681483.7254 | 1246159.3028 | 2681488.5059 | 1246156.1439 | 2681493.4618 | 1246152.8652
53 | 2681483.7254 | 1246159.3028 | 2681482.7361 | 1246161.4685 | 2681481.2597 | 1246163.3496 | 2681479.3956 | 1246164.8473 | 2681476.8566 | 1246165.98 | 2681474.1008 | 1246166.398 | 2681471.3403 | 1246166.0598 | 2681425.557 | 1246144.2692
54 | 2681412.5839 | 1246138.0947 | 2681425.557 | 1246144.2692
55 | 2681422.4166 | 1245989.2482 | 2681422.0143 | 1245984.984 | 2681420.6635 | 1245972.5898
56 | 2681484.394 | 1245976.625 | 2681488.02 | 1245976.2271
57 | 2681357.3087 | 1246111.6469 | 2681365.2509 | 1246115.468
58 | 2681457.1692 | 1246010.841 | 2681457.439 | 1246013.0153
59 | 2681495.6792 | 1246051.6616 | 2681486.9493 | 1246062.6063
60 | 2681386.7727 | 1245990.182 | 2681416.8476 | 1245989.294 | 2681422.4166 | 1245989.2482
61 | 2681560.809 | 1246048.5036 | 2681535.9221 | 1246080.2741
62 | 2681412.5839 | 1246138.0947 | 2681398.025 | 1246131.1654
63 | 2681494.2223 | 1245975.5464 | 2681488.02 | 1245976.2271
64 | 2681386.0273 | 1246125.455 | 2681384.3522 | 1246124.6578 | 2681365.2509 | 1246115.468
65 | 2681386.0273 | 1246125.455 | 2681398.025 | 1246131.1654
66 | 2681504.3688 | 1246040.7675 | 2681495.6792 | 1246051.6616
67 | 2681511.9562 | 1246031.2551 | 2681504.3688 | 1246040.7675
68 | 2681511.9562 | 1246031.2551 | 2681520.6679 | 1246020.3332
69 | 2681526.8893 | 1246012.5334 | 2681520.6679 | 1246020.3332

## bus_geodata
| x | y | coords
0 | 2681461.6072 | 1245894.4837
1 | 2681453.4343 | 1245897.207
2 | 2681483.3687 | 1245887.3443
3 | 2681454.2537 | 1245925.7793
4 | 2681493.6749 | 1245884.0105
5 | 2681457.2017 | 1245881.4695
6 | 2681455.3937 | 1245933.2586
7 | 2681429.4279 | 1245951.3057
8 | 2681430.9041 | 1245964.4691
9 | 2681449.2613 | 1245946.8748
10 | 2681412.3097 | 1245916.4676
11 | 2681402.8935 | 1245877.0097
12 | 2681416.687 | 1245937.9168
13 | 2681432.901 | 1245982.2759
14 | 2681441.2949 | 1245981.3548
15 | 2681434.4824 | 1245996.3587
16 | 2681440.9489 | 1246041.0181
17 | 2681444.5713 | 1246057.2958
18 | 2681459.1047 | 1246026.4395
19 | 2681438.1391 | 1246025.0254
20 | 2681439.3532 | 1245886.969
21 | 2681533.5869 | 1245871.1002
22 | 2681623.8779 | 1245859.9448
23 | 2681455.0733 | 1246093.5391
24 | 2681452.9807 | 1246088.0286
25 | 2681483.7982 | 1246140.2677
26 | 2681478.0552 | 1246073.7569
27 | 2681434.8445 | 1246073.9916
28 | 2681437.8687 | 1246084.751
29 | 2681417.5679 | 1246071.8059
30 | 2681440.1622 | 1246091.6775
31 | 2681452.2229 | 1246114.0371
32 | 2681502.7461 | 1246125.4616
33 | 2681491.8138 | 1246150.7167
34 | 2681448.8272 | 1246074.4878
35 | 2681542.2115 | 1245959.2607
36 | 2681375.9354 | 1246125.7765
37 | 2681368.2812 | 1246140.6934
38 | 2681345.9308 | 1246106.1729
39 | 2681570.4428 | 1246160.451
40 | 2681518.314 | 1246186.142
41 | 2681568.5816 | 1246159.0996
42 | 2681533.1031 | 1246174.8815
43 | 2681501.8068 | 1246164.039
44 | 2681483.7254 | 1246159.3028
45 | 2681493.4618 | 1246152.8652
46 | 2681425.557 | 1246144.2692
47 | 2681420.6635 | 1245972.5898
48 | 2681484.394 | 1245976.625
49 | 2681334.0895 | 1246100.5866
50 | 2681357.3087 | 1246111.6469
51 | 2681457.439 | 1246013.0153
52 | 2681486.9493 | 1246062.6063
53 | 2681422.4166 | 1245989.2482
54 | 2681386.7727 | 1245990.182
55 | 2681535.9221 | 1246080.2741
56 | 2681509.7003 | 1246099.8456
57 | 2681557.8457 | 1246151.3044
58 | 2681412.5839 | 1246138.0947
59 | 2681488.02 | 1245976.2271
60 | 2681494.2223 | 1245975.5464
61 | 2681457.1692 | 1246010.841
62 | 2681365.2509 | 1246115.468
63 | 2681386.0273 | 1246125.455
64 | 2681398.025 | 1246131.1654
65 | 2681560.809 | 1246048.5036
66 | 2681495.6792 | 1246051.6616
67 | 2681504.3688 | 1246040.7675
68 | 2681511.9562 | 1246031.2551
69 | 2681520.6679 | 1246020.3332
70 | 2681526.8893 | 1246012.5334
71 | 2681457.1692 | 1246010.841

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98358 | -0.31434 | 0.0053745 | 0.001347
1 | 0.98428 | -0.30077 | 0 | 0
2 | 0.98183 | -0.34828 | 0 | 0
3 | 0.98681 | -0.25183 | 0.001929 | 0.00048345
4 | 0.98132 | -0.35829 | 0.017135 | 0.0042945
5 | 0.98086 | -0.36729 | 0 | 0
6 | 0.98745 | -0.23963 | 0.0066043 | 0.0016552
7 | 0.99084 | -0.17452 | 0 | 0
8 | 0.9921 | -0.1504 | 0.0041763 | 0.0010467
9 | 0.98882 | -0.21334 | 0.0066642 | 0.0016702
10 | 0.97784 | -0.42634 | 0 | 0
11 | 0.97922 | -0.39926 | 0 | 0
12 | 0.97723 | -0.43825 | 0.0089483 | 0.0022427
13 | 0.99388 | -0.11655 | 0 | 0
14 | 0.99351 | -0.1236 | 0.0031164 | 0.00078104
15 | 0.99489 | -0.097296 | 0.0067891 | 0.0017015
16 | 0.99667 | -0.063297 | 0 | 0
17 | 0.99561 | -0.08362 | 0.020118 | 0.0050419
18 | 1 | 0 | -0.48713 | -0.12377
19 | 0.99596 | -0.076834 | 0.028965 | 0.0072593
20 | 0.98032 | -0.37782 | 0.0012516 | 0.00031369
21 | 0.97999 | -0.38407 | 0 | 0
22 | 0.97659 | -0.45044 | 0 | 0
23 | 0.99242 | -0.14498 | 0 | 0
24 | 0.99302 | -0.13332 | 0 | 0
25 | 0.98853 | -0.22002 | 0 | 0
26 | 0.99143 | -0.16413 | 0.016032 | 0.0040181
27 | 0.98989 | -0.19387 | 0 | 0
28 | 0.99069 | -0.17841 | 0.042373 | 0.01062
29 | 0.98865 | -0.21802 | 0.077824 | 0.019504
30 | 0.9915 | -0.16285 | 0 | 0
31 | 0.99138 | -0.16512 | 0.0049298 | 0.0012355
32 | 0.98806 | -0.22904 | 0 | 0
33 | 0.98785 | -0.2331 | 0.0023838 | 0.00059745
34 | 0.99457 | -0.10369 | 0.020393 | 0.0051109
35 | 0.97216 | -0.53763 | 0.033908 | 0.008498
36 | 0.98143 | -0.35809 | 0 | 0
37 | 0.98137 | -0.35926 | 0.003867 | 0.00096916
38 | 0.98157 | -0.35527 | 0 | 0
39 | 0.987 | -0.24957 | 0 | 0
40 | 0.98753 | -0.23937 | 0 | 0
41 | 0.987 | -0.24973 | 0.00097009 | 0.00024313
42 | 0.98752 | -0.23956 | 0.00055423 | 0.0001389
43 | 0.98764 | -0.23721 | 0.0017838 | 0.00044705
44 | 0.98721 | -0.24551 | 0 | 0
45 | 0.98772 | -0.23568 | 0 | 0
46 | 0.98433 | -0.30145 | 0.0047813 | 0.0011983
47 | 0.97656 | -0.45154 | 0.0093177 | 0.0023352
48 | 0.99176 | -0.15748 | 0.0046972 | 0.0011772
49 | 0.98127 | -0.36121 | 0.025047 | 0.0062774
50 | 0.98191 | -0.34867 | 0.0010451 | 0.00026193
51 | 0.99985 | -0.0029758 | 0.0057266 | 0.0014352
52 | 0.99118 | -0.16897 | 0.015448 | 0.0038716
53 | 0.97638 | -0.45508 | 0 | 0
54 | 0.976 | -0.46258 | 0.011542 | 0.0028927
55 | 0.98738 | -0.24225 | 0.0066841 | 0.0016752
56 | 0.98785 | -0.23319 | 0.0078957 | 0.0019788
57 | 0.98696 | -0.25041 | 0.0028503 | 0.00071435
58 | 0.98377 | -0.3124 | 0.0049907 | 0.0012508
59 | 0.99163 | -0.16003 | 0.0068729 | 0.0017225
60 | 0.99145 | -0.16364 | 0.032602 | 0.0081707
61 | 0.99983 | -0.0032391 | 0.0068929 | 0.0017275
62 | 0.98215 | -0.3439 | 0.0010618 | 0.00026612
63 | 0.98282 | -0.33098 | 0.001259 | 0.00031553
64 | 0.98321 | -0.32325 | 0.0050477 | 0.0012651
65 | 0.98714 | -0.24693 | 0.0064789 | 0.0016238
66 | 0.99113 | -0.16988 | 0.00071414 | 0.00017898
67 | 0.9911 | -0.17062 | 0.00070668 | 0.00017711
68 | 0.99107 | -0.17111 | 0.00074092 | 0.00018569
69 | 0.99105 | -0.17148 | 0.00074769 | 0.00018739
70 | 0.99104 | -0.17162 | 0.0007704 | 0.00019308
71 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.088078 | -0.022301 | 0.088136 | 0.022338 | 5.743e-05 | 3.6645e-05 | 0.13333 | 0.13333 | 0.13333 | 0.98358 | -0.31434 | 0.98428 | -0.30077 | 36.6296
1 | 0.082704 | 0.020954 | -0.082569 | -0.020869 | 0.00013463 | 8.5872e-05 | 0.1252 | 0.1252 | 0.1252 | 0.98358 | -0.31434 | 0.98183 | -0.34828 | 34.3959
2 | -0.088136 | -0.022338 | 0.088344 | 0.022471 | 0.00020778 | 0.00013259 | 0.13333 | 0.13333 | 0.13333 | 0.98428 | -0.30077 | 0.98681 | -0.25183 | 36.6295
3 | 0.05136 | 0.012992 | -0.051335 | -0.012976 | 2.4638e-05 | 1.5632e-05 | 0.077882 | 0.077882 | 0.077882 | 0.98183 | -0.34828 | 0.98132 | -0.35829 | 21.3961
4 | 0.031209 | 0.0078769 | -0.031181 | -0.0078592 | 2.8385e-05 | 1.7739e-05 | 0.047319 | 0.047319 | 0.047319 | 0.98183 | -0.34828 | 0.98086 | -0.36729 | 12.9998
5 | -0.090273 | -0.022954 | 0.090326 | 0.022988 | 5.307e-05 | 3.3867e-05 | 0.13624 | 0.13624 | 0.13624 | 0.98681 | -0.25183 | 0.98745 | -0.23963 | 37.4286
6 | 0.0342 | 0.0086815 | -0.034158 | -0.0086549 | 4.237e-05 | 2.6587e-05 | 0.051899 | 0.051899 | 0.051899 | 0.98132 | -0.35829 | 0.97999 | -0.38407 | 14.2579
7 | 0.031181 | 0.0078592 | -0.031165 | -0.0078494 | 1.5698e-05 | 9.8107e-06 | 0.047319 | 0.047319 | 0.047319 | 0.98086 | -0.36729 | 0.98032 | -0.37782 | 12.9999
8 | -0.09693 | -0.024643 | 0.097053 | 0.024722 | 0.00012294 | 7.8488e-05 | 0.14619 | 0.14619 | 0.14619 | 0.98745 | -0.23963 | 0.98882 | -0.21334 | 40.1627
9 | -0.10391 | -0.026516 | 0.10403 | 0.026593 | 0.00012122 | 7.7413e-05 | 0.15622 | 0.15622 | 0.15622 | 0.99084 | -0.17452 | 0.9921 | -0.1504 | 42.9178
10 | 0.10391 | 0.026516 | -0.10372 | -0.026392 | 0.00019446 | 0.00012418 | 0.15622 | 0.15622 | 0.15622 | 0.99084 | -0.17452 | 0.98882 | -0.21334 | 42.9178
11 | -0.10821 | -0.02764 | 0.10839 | 0.027753 | 0.0001774 | 0.0001133 | 0.16248 | 0.16248 | 0.16248 | 0.9921 | -0.1504 | 0.99388 | -0.11655 | 44.6386
12 | -0.029844 | -0.0074925 | 0.029883 | 0.0075165 | 3.8597e-05 | 2.4075e-05 | 0.04542 | 0.04542 | 0.04542 | 0.97784 | -0.42634 | 0.97922 | -0.39926 | 12.478
13 | 0.029844 | 0.0074925 | -0.029828 | -0.0074819 | 1.6945e-05 | 1.057e-05 | 0.04542 | 0.04542 | 0.04542 | 0.97784 | -0.42634 | 0.97723 | -0.43825 | 12.4781
14 | -0.029883 | -0.0075165 | 0.029914 | 0.0075357 | 3.0644e-05 | 1.9113e-05 | 0.04542 | 0.04542 | 0.04542 | 0.97922 | -0.39926 | 0.98032 | -0.37782 | 12.478
15 | 0.020879 | 0.0052392 | -0.020866 | -0.0052312 | 1.3231e-05 | 8.0306e-06 | 0.031795 | 0.031795 | 0.031795 | 0.97723 | -0.43825 | 0.97656 | -0.45154 | 8.7348
16 | 0.047386 | 0.011913 | -0.04737 | -0.011903 | 1.5944e-05 | 1.0095e-05 | 0.070958 | 0.070958 | 0.070958 | 0.99388 | -0.11655 | 0.99351 | -0.1236 | 19.4941
17 | -0.15577 | -0.039667 | 0.15592 | 0.039759 | 0.0001448 | 9.2304e-05 | 0.23344 | 0.23344 | 0.23344 | 0.99388 | -0.11655 | 0.99489 | -0.097296 | 32.0662
18 | 0.044254 | 0.011122 | -0.044182 | -0.011077 | 7.1451e-05 | 4.5168e-05 | 0.066291 | 0.066291 | 0.066291 | 0.99351 | -0.1236 | 0.99176 | -0.15748 | 18.2118
19 | -0.16271 | -0.041461 | 0.16287 | 0.041562 | 0.00016082 | 0.00010142 | 0.2436 | 0.2436 | 0.2436 | 0.99489 | -0.097296 | 0.99596 | -0.076834 | 16.7305
20 | 0.27946 | 0.07079 | -0.27919 | -0.070616 | 0.0002725 | 0.00017353 | 0.41749 | 0.41749 | 0.41749 | 0.99667 | -0.063297 | 0.99561 | -0.08362 | 28.6741
21 | -0.47142 | -0.11969 | 0.47286 | 0.12061 | 0.0014406 | 0.00092035 | 0.70436 | 0.70436 | 0.70436 | 0.99667 | -0.063297 | 1 | 0 | 48.3766
22 | 0.19196 | 0.048901 | -0.19183 | -0.048821 | 0.00012528 | 7.933e-05 | 0.28687 | 0.28687 | 0.28687 | 0.99667 | -0.063297 | 0.99596 | -0.076834 | 19.7026
23 | 0.25907 | 0.065574 | -0.25882 | -0.065416 | 0.00024939 | 0.00015869 | 0.38743 | 0.38743 | 0.38743 | 0.99561 | -0.08362 | 0.99457 | -0.10369 | 26.609
24 | 0.012621 | 0.0031637 | -0.01262 | -0.0031628 | 1.7893e-06 | 9.677e-07 | 0.018781 | 0.018781 | 0.018781 | 1 | 0 | 0.99985 | -0.0029758 | 5.1596
25 | 0.034158 | 0.0086549 | -0.034049 | -0.0085868 | 0.00010854 | 6.8118e-05 | 0.051899 | 0.051899 | 0.051899 | 0.97999 | -0.38407 | 0.97659 | -0.45044 | 14.258
26 | 0.034049 | 0.0085868 | -0.033908 | -0.008498 | 0.00014147 | 8.8794e-05 | 0.051899 | 0.0519 | 0.0519 | 0.97659 | -0.45044 | 0.97216 | -0.53763 | 14.2582
27 | -0.11249 | -0.028425 | 0.11255 | 0.028465 | 6.2923e-05 | 4.0195e-05 | 0.16874 | 0.16874 | 0.16874 | 0.99242 | -0.14498 | 0.99302 | -0.13332 | 46.3576
28 | 0.077288 | 0.01959 | -0.077011 | -0.019413 | 0.00027762 | 0.00017697 | 0.11596 | 0.11596 | 0.11596 | 0.99242 | -0.14498 | 0.98853 | -0.22002 | 31.8581
29 | 0.035197 | 0.0088342 | -0.035165 | -0.008814 | 3.2119e-05 | 2.0159e-05 | 0.052779 | 0.052779 | 0.052779 | 0.99242 | -0.14498 | 0.99143 | -0.16413 | 14.4997
30 | -0.23809 | -0.060088 | 0.23843 | 0.060305 | 0.0003383 | 0.00021615 | 0.35692 | 0.35692 | 0.35692 | 0.99302 | -0.13332 | 0.99457 | -0.10369 | 49.0271
31 | 0.12554 | 0.031624 | -0.12536 | -0.031511 | 0.00017702 | 0.00011312 | 0.18818 | 0.18818 | 0.18818 | 0.99302 | -0.13332 | 0.9915 | -0.16285 | 51.6966
32 | 0.021079 | 0.0052889 | -0.02107 | -0.0052834 | 9.0642e-06 | 5.4935e-06 | 0.031732 | 0.031732 | 0.031732 | 0.98853 | -0.22002 | 0.98806 | -0.22904 | 8.7176
33 | 0.055932 | 0.014124 | -0.055897 | -0.014102 | 3.5038e-05 | 2.2256e-05 | 0.084231 | 0.084231 | 0.084231 | 0.98853 | -0.22002 | 0.98785 | -0.2331 | 23.1405
34 | 0.019133 | 0.0047959 | -0.019128 | -0.0047933 | 4.4106e-06 | 2.6389e-06 | 0.028716 | 0.028716 | 0.028716 | 0.99143 | -0.16413 | 0.99118 | -0.16897 | 7.8891
35 | -0.077913 | -0.019562 | 0.077971 | 0.019598 | 5.7512e-05 | 3.6664e-05 | 0.11713 | 0.11713 | 0.11713 | 0.98989 | -0.19387 | 0.99069 | -0.17841 | 32.1791
36 | 0.077913 | 0.019562 | -0.077824 | -0.019504 | 8.9638e-05 | 5.7144e-05 | 0.11713 | 0.11713 | 0.11713 | 0.98989 | -0.19387 | 0.98865 | -0.21802 | 32.1791
37 | -0.12034 | -0.030218 | 0.12043 | 0.030275 | 8.9417e-05 | 5.7133e-05 | 0.18078 | 0.18078 | 0.18078 | 0.99069 | -0.17841 | 0.9915 | -0.16285 | 49.6638
38 | 0.0049304 | 0.0012355 | -0.0049298 | -0.0012355 | 5.3423e-07 | 6.3687e-09 | 0.0073994 | 0.0073995 | 0.0073995 | 0.9915 | -0.16285 | 0.99138 | -0.16512 | 2.0328
39 | 0.013173 | 0.0033039 | -0.013164 | -0.0032994 | 8.2904e-06 | 4.5869e-06 | 0.019839 | 0.019839 | 0.019839 | 0.98806 | -0.22904 | 0.98738 | -0.24225 | 5.4503
40 | 0.0078972 | 0.0019795 | -0.0078957 | -0.0019788 | 1.5621e-06 | 6.2266e-07 | 0.011893 | 0.011893 | 0.011893 | 0.98806 | -0.22904 | 0.98785 | -0.23319 | 3.2674
41 | 0.053513 | 0.013505 | -0.053506 | -0.013501 | 6.603e-06 | 4.1913e-06 | 0.080641 | 0.080641 | 0.080641 | 0.98785 | -0.2331 | 0.98772 | -0.23568 | 22.154
42 | 0.0038672 | 0.00096908 | -0.003867 | -0.00096916 | 2.1604e-07 | -7.3482e-08 | 0.0058633 | 0.0058634 | 0.0058634 | 0.98143 | -0.35809 | 0.98137 | -0.35926 | 1.6108
43 | -0.0038672 | -0.00096908 | 0.0038677 | 0.00096891 | 5.1848e-07 | -1.7647e-07 | 0.0058633 | 0.0058631 | 0.0058633 | 0.98143 | -0.35809 | 0.98157 | -0.35527 | 1.6108
44 | 0.025054 | 0.0062818 | -0.025047 | -0.0062774 | 7.083e-06 | 4.3677e-06 | 0.037982 | 0.037982 | 0.037982 | 0.98157 | -0.35527 | 0.98127 | -0.36121 | 10.4346
45 | -0.028922 | -0.0072507 | 0.028931 | 0.0072564 | 9.1022e-06 | 5.6657e-06 | 0.043845 | 0.043845 | 0.043845 | 0.98157 | -0.35527 | 0.98191 | -0.34867 | 12.0453
46 | -0.0038205 | -0.00095735 | 0.0038223 | 0.00095663 | 1.8559e-06 | -7.2008e-07 | 0.0057597 | 0.0057591 | 0.0057597 | 0.987 | -0.24957 | 0.98753 | -0.23937 | 1.5823
47 | 0.0038205 | 0.00095735 | -0.0038205 | -0.00095736 | 2.8614e-08 | -1.1083e-08 | 0.0057597 | 0.0057598 | 0.0057598 | 0.987 | -0.24957 | 0.987 | -0.24973 | 1.5824
48 | 0.00055424 | 0.00013867 | -0.00055423 | -0.0001389 | 4.8524e-09 | -2.3429e-07 | 0.00083505 | 0.00083513 | 0.00083513 | 0.98753 | -0.23937 | 0.98752 | -0.23956 | 0.22943
49 | -0.0043766 | -0.0010953 | 0.004377 | 0.0010952 | 4.4982e-07 | -6.5103e-08 | 0.0065941 | 0.006594 | 0.0065941 | 0.98753 | -0.23937 | 0.98764 | -0.23721 | 1.8116
50 | 0.0028504 | 0.00071423 | -0.0028503 | -0.00071435 | 9.1875e-08 | -1.1075e-07 | 0.0042972 | 0.0042973 | 0.0042973 | 0.987 | -0.24973 | 0.98696 | -0.25041 | 1.1806
51 | -0.0061608 | -0.0015423 | 0.0061612 | 0.0015424 | 4.5052e-07 | 1.0985e-07 | 0.0092815 | 0.0092814 | 0.0092815 | 0.98764 | -0.23721 | 0.98772 | -0.23568 | 2.5499
52 | -0.047323 | -0.011944 | 0.047345 | 0.011958 | 2.2289e-05 | 1.4115e-05 | 0.071359 | 0.071359 | 0.071359 | 0.98721 | -0.24551 | 0.98772 | -0.23568 | 19.6042
53 | 0.047323 | 0.011944 | -0.047196 | -0.011864 | 0.00012644 | 8.008e-05 | 0.071359 | 0.071359 | 0.071359 | 0.98721 | -0.24551 | 0.98433 | -0.30145 | 19.6043
54 | 0.042415 | 0.010666 | -0.042393 | -0.010652 | 2.2159e-05 | 1.3999e-05 | 0.064131 | 0.064132 | 0.064132 | 0.98433 | -0.30145 | 0.98377 | -0.3124 | 17.6186
55 | 0.011548 | 0.002896 | -0.011546 | -0.0028949 | 1.9451e-06 | 1.0353e-06 | 0.017597 | 0.017597 | 0.017597 | 0.97656 | -0.45154 | 0.97638 | -0.45508 | 4.8344
56 | 0.039485 | 0.0098998 | -0.03948 | -0.0098968 | 4.8012e-06 | 3.0257e-06 | 0.059244 | 0.059244 | 0.059244 | 0.99176 | -0.15748 | 0.99163 | -0.16003 | 16.2757
57 | -0.029976 | -0.0075183 | 0.029983 | 0.0075225 | 6.8209e-06 | 4.2539e-06 | 0.045429 | 0.045429 | 0.045429 | 0.98191 | -0.34867 | 0.98215 | -0.3439 | 12.4804
58 | 0.006893 | 0.0017276 | -0.0068929 | -0.0017275 | 8.6464e-08 | 2.6602e-08 | 0.010259 | 0.010259 | 0.010259 | 0.99985 | -0.0029758 | 0.99983 | -0.0032391 | 2.8183
59 | 0.0036802 | 0.00092165 | -0.00368 | -0.00092173 | 1.6024e-07 | -7.7881e-08 | 0.0055247 | 0.0055247 | 0.0055247 | 0.99118 | -0.16897 | 0.99113 | -0.16988 | 1.5178
60 | 0.011546 | 0.0028949 | -0.011542 | -0.0028927 | 4.1284e-06 | 2.1977e-06 | 0.017597 | 0.017597 | 0.017597 | 0.97638 | -0.45508 | 0.976 | -0.46258 | 4.8344
61 | 0.0064803 | 0.0016242 | -0.0064789 | -0.0016238 | 1.4434e-06 | 4.0775e-07 | 0.009766 | 0.0097662 | 0.0097662 | 0.98738 | -0.24225 | 0.98714 | -0.24693 | 2.683
62 | 0.037402 | 0.0094009 | -0.037383 | -0.0093887 | 1.9358e-05 | 1.2185e-05 | 0.056583 | 0.056583 | 0.056583 | 0.98377 | -0.3124 | 0.98321 | -0.32325 | 15.5447
63 | 0.032607 | 0.0081742 | -0.032602 | -0.0081707 | 5.6019e-06 | 3.5047e-06 | 0.04893 | 0.04893 | 0.04893 | 0.99163 | -0.16003 | 0.99145 | -0.16364 | 13.4424
64 | -0.031045 | -0.0077887 | 0.031064 | 0.0078006 | 1.9126e-05 | 1.1949e-05 | 0.047037 | 0.047037 | 0.047037 | 0.98215 | -0.3439 | 0.98282 | -0.33098 | 12.9224
65 | -0.032323 | -0.0081161 | 0.032335 | 0.0081236 | 1.1936e-05 | 7.4706e-06 | 0.048944 | 0.048943 | 0.048944 | 0.98282 | -0.33098 | 0.98321 | -0.32325 | 13.446
66 | 0.0029659 | 0.00074275 | -0.0029658 | -0.00074286 | 1.036e-07 | -1.1328e-07 | 0.0044526 | 0.0044526 | 0.0044526 | 0.99113 | -0.16988 | 0.9911 | -0.17062 | 1.2233
67 | 0.0022591 | 0.00056575 | -0.002259 | -0.00056587 | 5.2488e-08 | -1.232e-07 | 0.0033916 | 0.0033917 | 0.0033917 | 0.9911 | -0.17062 | 0.99107 | -0.17111 | 0.93178
68 | 0.0015181 | 0.00038018 | -0.0015181 | -0.00038034 | 2.7217e-08 | -1.6261e-07 | 0.0022792 | 0.0022793 | 0.0022793 | 0.99107 | -0.17111 | 0.99105 | -0.17148 | 0.62618
69 | 0.00077041 | 0.00019296 | -0.0007704 | -0.00019308 | 5.006e-09 | -1.2536e-07 | 0.0011567 | 0.0011567 | 0.0011567 | 0.99105 | -0.17148 | 0.99104 | -0.17162 | 0.31778

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.52679 | 0.13371

## res_load
| p_mw | q_mvar
0 | 0.0053745 | 0.001347
1 | 0.001929 | 0.00048345
2 | 0.017135 | 0.0042945
3 | 0.0066043 | 0.0016552
4 | 0.0041763 | 0.0010467
5 | 0.0066642 | 0.0016702
6 | 0.0089483 | 0.0022427
7 | 0.0031164 | 0.00078104
8 | 0.0067891 | 0.0017015
9 | 0.020118 | 0.0050419
10 | 0.039662 | 0.0099403
11 | 0.028965 | 0.0072593
12 | 0.0012516 | 0.00031369
13 | 0.016032 | 0.0040181
14 | 0.042373 | 0.01062
15 | 0.077824 | 0.019504
16 | 0.0049298 | 0.0012355
17 | 0.0023838 | 0.00059745
18 | 0.020393 | 0.0051109
19 | 0.033908 | 0.008498
20 | 0.003867 | 0.00096916
21 | 0.00097009 | 0.00024313
22 | 0.00055423 | 0.0001389
23 | 0.0017838 | 0.00044705
24 | 0.0047813 | 0.0011983
25 | 0.0093177 | 0.0023352
26 | 0.0046972 | 0.0011772
27 | 0.025047 | 0.0062774
28 | 0.0010451 | 0.00026193
29 | 0.0057266 | 0.0014352
30 | 0.015448 | 0.0038716
31 | 0.011542 | 0.0028927
32 | 0.0066841 | 0.0016752
33 | 0.0078957 | 0.0019788
34 | 0.0028503 | 0.00071435
35 | 0.0049907 | 0.0012508
36 | 0.0068729 | 0.0017225
37 | 0.032602 | 0.0081707
38 | 0.0068929 | 0.0017275
39 | 0.0010618 | 0.00026612
40 | 0.001259 | 0.00031553
41 | 0.0050477 | 0.0012651
42 | 0.0064789 | 0.0016238
43 | 0.00071414 | 0.00017898
44 | 0.00070668 | 0.00017711
45 | 0.00074092 | 0.00018569
46 | 0.00074769 | 0.00018739
47 | 0.0007704 | 0.00019308

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1