## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-531_0_8_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-531_0_8_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-531_0_8_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_261-531_0_8_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_261-531_0_8_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_261-531_0_8_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_261-531_0_8_node_55 | 0.4 | n |  | TRUE
7 | bus_LV_261-531_0_8_node_60 | 0.4 | n |  | TRUE
8 | bus_LV_261-531_0_8_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_261-531_0_8_node_54 | 0.4 | n |  | TRUE
10 | bus_LV_261-531_0_8_node_52 | 0.4 | n |  | TRUE
11 | bus_LV_261-531_0_8_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_261-531_0_8_node_133 | 0.4 | n |  | TRUE
13 | bus_LV_261-531_0_8_node_11 | 0.4 | n |  | TRUE
14 | bus_LV_261-531_0_8_node_8 | 0.4 | n |  | TRUE
15 | bus_LV_261-531_0_8_node_56 | 0.4 | n |  | TRUE
16 | bus_LV_261-531_0_8_node_10 | 0.4 | n |  | TRUE
17 | bus_LV_261-531_0_8_node_61 | 0.4 | n |  | TRUE
18 | bus_LV_261-531_0_8_node_53 | 0.4 | n |  | TRUE
19 | bus_LV_261-531_0_8_node_49 | 0.4 | n |  | TRUE
20 | bus_LV_261-531_0_8_node_12 | 0.4 | n |  | TRUE
21 | bus_LV_261-531_0_8_node_132 | 0.4 | n |  | TRUE
22 | bus_LV_261-531_0_8_node_105 | 0.4 | n |  | TRUE
23 | bus_LV_261-531_0_8_node_15 | 0.4 | n |  | TRUE
24 | bus_LV_261-531_0_8_node_16 | 0.4 | n |  | TRUE
25 | bus_LV_261-531_0_8_node_126 | 0.4 | n |  | TRUE
26 | bus_LV_261-531_0_8_node_125 | 0.4 | n |  | TRUE
27 | bus_LV_261-531_0_8_node_18 | 0.4 | n |  | TRUE
28 | bus_LV_261-531_0_8_node_87 | 0.4 | n |  | TRUE
29 | bus_LV_261-531_0_8_node_33 | 0.4 | n |  | TRUE
30 | bus_LV_261-531_0_8_node_35 | 0.4 | n |  | TRUE
31 | bus_LV_261-531_0_8_node_66 | 0.4 | n |  | TRUE
32 | bus_LV_261-531_0_8_node_19 | 0.4 | n |  | TRUE
33 | bus_LV_261-531_0_8_node_101 | 0.4 | n |  | TRUE
34 | bus_LV_261-531_0_8_node_99 | 0.4 | n |  | TRUE
35 | bus_LV_261-531_0_8_node_21 | 0.4 | n |  | TRUE
36 | bus_LV_261-531_0_8_node_129 | 0.4 | n |  | TRUE
37 | bus_LV_261-531_0_8_node_22 | 0.4 | n |  | TRUE
38 | bus_LV_261-531_0_8_node_32 | 0.4 | n |  | TRUE
39 | bus_LV_261-531_0_8_node_107 | 0.4 | n |  | TRUE
40 | bus_LV_261-531_0_8_node_23 | 0.4 | n |  | TRUE
41 | bus_LV_261-531_0_8_node_47 | 0.4 | n |  | TRUE
42 | bus_LV_261-531_0_8_node_90 | 0.4 | n |  | TRUE
43 | bus_LV_261-531_0_8_node_106 | 0.4 | n |  | TRUE
44 | bus_LV_261-531_0_8_node_24 | 0.4 | n |  | TRUE
45 | bus_LV_261-531_0_8_node_130 | 0.4 | n |  | TRUE
46 | bus_LV_261-531_0_8_node_26 | 0.4 | n |  | TRUE
47 | bus_LV_261-531_0_8_node_27 | 0.4 | n |  | TRUE
48 | bus_LV_261-531_0_8_node_111 | 0.4 | n |  | TRUE
49 | bus_LV_261-531_0_8_node_34 | 0.4 | n |  | TRUE
50 | bus_LV_261-531_0_8_node_120 | 0.4 | n |  | TRUE
51 | bus_LV_261-531_0_8_node_30 | 0.4 | n |  | TRUE
52 | bus_LV_261-531_0_8_node_86 | 0.4 | n |  | TRUE
53 | bus_LV_261-531_0_8_node_31 | 0.4 | n |  | TRUE
54 | bus_LV_261-531_0_8_node_134 | 0.4 | n |  | TRUE
55 | bus_LV_261-531_0_8_node_108 | 0.4 | n |  | TRUE
56 | bus_LV_261-531_0_8_node_128 | 0.4 | n |  | TRUE
57 | bus_LV_261-531_0_8_node_135 | 0.4 | n |  | TRUE
58 | bus_LV_261-531_0_8_node_112 | 0.4 | n |  | TRUE
59 | bus_LV_261-531_0_8_node_95 | 0.4 | n |  | TRUE
60 | bus_LV_261-531_0_8_node_121 | 0.4 | n |  | TRUE
61 | bus_LV_261-531_0_8_node_36 | 0.4 | n |  | TRUE
62 | bus_LV_261-531_0_8_node_131 | 0.4 | n |  | TRUE
63 | bus_LV_261-531_0_8_node_42 | 0.4 | n |  | TRUE
64 | bus_LV_261-531_0_8_node_104 | 0.4 | n |  | TRUE
65 | bus_LV_261-531_0_8_node_37 | 0.4 | n |  | TRUE
66 | bus_LV_261-531_0_8_node_39 | 0.4 | n |  | TRUE
67 | bus_LV_261-531_0_8_node_127 | 0.4 | n |  | TRUE
68 | bus_LV_261-531_0_8_node_38 | 0.4 | n |  | TRUE
69 | bus_LV_261-531_0_8_node_82 | 0.4 | n |  | TRUE
70 | bus_LV_261-531_0_8_node_73 | 0.4 | n |  | TRUE
71 | bus_LV_261-531_0_8_node_81 | 0.4 | n |  | TRUE
72 | bus_LV_261-531_0_8_node_41 | 0.4 | n |  | TRUE
73 | bus_LV_261-531_0_8_node_124 | 0.4 | n |  | TRUE
74 | bus_LV_261-531_0_8_node_79 | 0.4 | n |  | TRUE
75 | bus_LV_261-531_0_8_node_115 | 0.4 | n |  | TRUE
76 | bus_LV_261-531_0_8_node_43 | 0.4 | n |  | TRUE
77 | bus_LV_261-531_0_8_node_74 | 0.4 | n |  | TRUE
78 | bus_LV_261-531_0_8_node_72 | 0.4 | n |  | TRUE
79 | bus_LV_261-531_0_8_node_45 | 0.4 | n |  | TRUE
80 | bus_LV_261-531_0_8_node_48 | 0.4 | n |  | TRUE
81 | bus_LV_261-531_0_8_node_88 | 0.4 | n |  | TRUE
82 | bus_LV_261-531_0_8_node_46 | 0.4 | n |  | TRUE
83 | bus_LV_261-531_0_8_node_117 | 0.4 | n |  | TRUE
84 | bus_LV_261-531_0_8_node_96 | 0.4 | n |  | TRUE
85 | bus_LV_261-531_0_8_node_136 | 0.4 | n |  | TRUE
86 | bus_LV_261-531_0_8_node_57 | 0.4 | n |  | TRUE
87 | bus_LV_261-531_0_8_node_50 | 0.4 | n |  | TRUE
88 | bus_LV_261-531_0_8_node_103 | 0.4 | n |  | TRUE
89 | bus_LV_261-531_0_8_node_100 | 0.4 | n |  | TRUE
90 | bus_LV_261-531_0_8_node_97 | 0.4 | n |  | TRUE
91 | bus_LV_261-531_0_8_node_64 | 0.4 | n |  | TRUE
92 | bus_LV_261-531_0_8_node_98 | 0.4 | n |  | TRUE
93 | bus_LV_261-531_0_8_node_89 | 0.4 | n |  | TRUE
94 | bus_LV_261-531_0_8_node_110 | 0.4 | n |  | TRUE
95 | bus_LV_261-531_0_8_node_119 | 0.4 | n |  | TRUE
96 | bus_LV_261-531_0_8_node_109 | 0.4 | n |  | TRUE
97 | bus_LV_261-531_0_8_node_113 | 0.4 | n |  | TRUE
98 | bus_LV_261-531_0_8_node_94 | 0.4 | n |  | TRUE
99 | bus_LV_261-531_0_8_node_102 | 0.4 | n |  | TRUE
100 | bus_LV_261-531_0_8_node_75 | 0.4 | n |  | TRUE
101 | bus_LV_261-531_0_8_node_122 | 0.4 | n |  | TRUE
102 | bus_LV_261-531_0_8_node_123 | 0.4 | n |  | TRUE
103 | bus_LV_261-531_0_8_node_84 | 0.4 | n |  | TRUE
104 | bus_LV_261-531_0_8_node_69 | 0.4 | n |  | TRUE
105 | bus_LV_261-531_0_8_node_77 | 0.4 | n |  | TRUE
106 | bus_LV_261-531_0_8_node_76 | 0.4 | n |  | TRUE
107 | bus_LV_261-531_0_8_node_67 | 0.4 | n |  | TRUE
108 | bus_LV_261-531_0_8_node_68 | 0.4 | n |  | TRUE
109 | bus_LV_261-531_0_8_node_116 | 0.4 | n |  | TRUE
110 | bus_LV_261-531_0_8_node_93 | 0.4 | n |  | TRUE
111 | bus_LV_261-531_0_8_node_92 | 0.4 | n |  | TRUE
112 | bus_LV_261-531_0_8_node_51 | 0.4 | n |  | TRUE
113 | bus_LV_261-531_0_8_node_58 | 0.4 | n |  | TRUE
114 | bus_LV_261-531_0_8_node_59 | 0.4 | n |  | TRUE
115 | bus_LV_261-531_0_8_node_114 | 0.4 | n |  | TRUE
116 | bus_LV_261-531_0_8_node_62 | 0.4 | n |  | TRUE
117 | bus_LV_261-531_0_8_node_63 | 0.4 | n |  | TRUE
118 | bus_LV_261-531_0_8_node_65 | 0.4 | n |  | TRUE
119 | bus_LV_261-531_0_8_node_70 | 0.4 | n |  | TRUE
120 | bus_LV_261-531_0_8_node_71 | 0.4 | n |  | TRUE
121 | bus_LV_261-531_0_8_node_83 | 0.4 | n |  | TRUE
122 | bus_LV_261-531_0_8_node_118 | 0.4 | n |  | TRUE
123 | bus_LV_261-531_0_8_node_78 | 0.4 | n |  | TRUE
124 | bus_LV_261-531_0_8_node_80 | 0.4 | n |  | TRUE
125 | bus_LV_261-531_0_8_node_137 | 0.4 | n |  | TRUE
126 | bus_MV_524_0_node_64 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-531_0_8_load_0 | 0 | 0.0032316 | 0.00080991 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-531_0_8_load_1 | 1 | 0.001989 | 0.00049848 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-531_0_8_load_3 | 3 | 0.0021721 | 0.00054439 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-531_0_8_load_4 | 4 | 0.0030322 | 0.00075993 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-531_0_8_load_55 | 6 | 0.0024826 | 0.00062219 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-531_0_8_load_60 | 7 | 0.00426 | 0.0010677 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-531_0_8_load_52 | 10 | 0.061109 | 0.015315 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-531_0_8_load_133 | 12 | 0.0058793 | 0.0014735 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-531_0_8_load_56 | 15 | 0.0036921 | 0.00092532 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-531_0_8_load_61 | 17 | 0.0018953 | 0.000475 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-531_0_8_load_53 | 18 | 0.0024335 | 0.00060989 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-531_0_8_load_49 | 19 | 0.0030637 | 0.00076784 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-531_0_8_load_132 | 21 | 0.0025056 | 0.00062796 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-531_0_8_load_126 | 25 | 0.0061285 | 0.001536 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-531_0_8_load_125 | 26 | 0.0041386 | 0.0010372 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-531_0_8_load_66 | 31 | 0.0024862 | 0.00062309 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-531_0_8_load_101 | 33 | 0.0084828 | 0.002126 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_261-531_0_8_load_99 | 34 | 0.008986 | 0.0022521 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_261-531_0_8_load_129 | 36 | 0.0068302 | 0.0017118 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_261-531_0_8_load_107 | 39 | 0.0068026 | 0.0017049 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_261-531_0_8_load_106 | 43 | 0.0046851 | 0.0011742 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_261-531_0_8_load_130 | 45 | 0.0078979 | 0.0019794 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_261-531_0_8_load_111 | 48 | 0.0088314 | 0.0022134 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_261-531_0_8_load_120 | 50 | 0.0093697 | 0.0023483 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_261-531_0_8_load_86 | 52 | 0.010484 | 0.0026276 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_261-531_0_8_load_134 | 54 | 0.0072436 | 0.0018154 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_261-531_0_8_load_128 | 56 | 0.0068903 | 0.0017269 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_261-531_0_8_load_135 | 57 | 0.0082156 | 0.002059 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_261-531_0_8_load_121 | 60 | 0.0091471 | 0.0022925 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_261-531_0_8_load_131 | 62 | 0.050973 | 0.012775 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_261-531_0_8_load_127 | 67 | 0.0081383 | 0.0020396 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_261-531_0_8_load_82 | 69 | 0.0013039 | 0.00032678 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_261-531_0_8_load_81 | 71 | 0.0086244 | 0.0021615 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_261-531_0_8_load_124 | 73 | 0.010959 | 0.0027466 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_261-531_0_8_load_115 | 75 | 0.00096875 | 0.00024279 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_261-531_0_8_load_74 | 77 | 0.0052401 | 0.0013133 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_261-531_0_8_load_72 | 78 | 0.0036821 | 0.00092282 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_261-531_0_8_load_88 | 81 | 0.007096 | 0.0017784 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_261-531_0_8_load_117 | 83 | 0.011863 | 0.0029732 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_261-531_0_8_load_96 | 84 | 0.0083465 | 0.0020918 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_261-531_0_8_load_136 | 85 | 0.05369 | 0.013456 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_261-531_0_8_load_50 | 87 | 0.0030637 | 0.00076784 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_261-531_0_8_load_103 | 88 | 0.035134 | 0.0088053 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_261-531_0_8_load_100 | 89 | 0.0034346 | 0.0008608 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_261-531_0_8_load_97 | 90 | 0.0082352 | 0.0020639 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_261-531_0_8_load_64 | 91 | 0.0035812 | 0.00089754 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_261-531_0_8_load_89 | 93 | 0.0076002 | 0.0019048 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_261-531_0_8_load_110 | 94 | 0.0071853 | 0.0018008 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_261-531_0_8_load_119 | 95 | 0.0078307 | 0.0019625 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_261-531_0_8_load_109 | 96 | 0.009153 | 0.002294 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_261-531_0_8_load_113 | 97 | 0.0083415 | 0.0020906 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_261-531_0_8_load_102 | 99 | 0.0062299 | 0.0015614 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_261-531_0_8_load_75 | 100 | 0.0030505 | 0.00076452 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_261-531_0_8_load_122 | 101 | 0.010683 | 0.0026774 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_261-531_0_8_load_123 | 102 | 0.01191 | 0.0029849 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_261-531_0_8_load_77 | 105 | 0.0021285 | 0.00053345 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_261-531_0_8_load_76 | 106 | 0.0050666 | 0.0012698 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_261-531_0_8_load_67 | 107 | 0.0038179 | 0.00095685 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_261-531_0_8_load_68 | 108 | 0.0031729 | 0.00079519 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_261-531_0_8_load_116 | 109 | 0.0039083 | 0.0009795 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_261-531_0_8_load_93 | 110 | 0.0084662 | 0.0021218 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_261-531_0_8_load_92 | 111 | 0.0095909 | 0.0024037 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_261-531_0_8_load_51 | 112 | 0.0043892 | 0.0011 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_261-531_0_8_load_59 | 114 | 0.0021525 | 0.00053947 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_261-531_0_8_load_114 | 115 | 0.0028995 | 0.00072668 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_261-531_0_8_load_62 | 116 | 0.0041472 | 0.0010394 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_261-531_0_8_load_63 | 117 | 0.0046058 | 0.0011543 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_261-531_0_8_load_65 | 118 | 0.0041644 | 0.0010437 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_261-531_0_8_load_70 | 119 | 0.0044744 | 0.0011214 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_261-531_0_8_load_71 | 120 | 0.0043814 | 0.0010981 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_261-531_0_8_load_78 | 123 | 0.0021289 | 0.00053354 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_261-531_0_8_load_80 | 124 | 0.0035195 | 0.00088206 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_261-531_0_8_load_137 | 125 | 0.0073355 | 0.0018384 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 112 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-531_0_8_line_0 |  | 0 | 1 | 0.020884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-531_0_8_line_1 |  | 0 | 2 | 0.017585 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-531_0_8_line_2 |  | 1 | 3 | 0.0082445 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-531_0_8_line_3 |  | 2 | 4 | 0.0069423 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-531_0_8_line_4 |  | 2 | 5 | 0.011939 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_261-531_0_8_line_5 |  | 3 | 6 | 0.018163 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_261-531_0_8_line_6 |  | 5 | 7 | 0.024626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_261-531_0_8_line_7 |  | 6 | 14 | 0.025927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_261-531_0_8_line_8 |  | 7 | 16 | 0.013677 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_261-531_0_8_line_9 |  | 8 | 9 | 0.027056 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_261-531_0_8_line_10 |  | 8 | 10 | 0.0098129 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_261-531_0_8_line_11 |  | 9 | 85 | 0.015662 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_261-531_0_8_line_12 |  | 10 | 18 | 0.015966 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-531_0_8_line_13 |  | 11 | 12 | 0.001315 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_261-531_0_8_line_14 |  | 11 | 13 | 0.030747 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_261-531_0_8_line_15 |  | 13 | 19 | 0.025607 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
16 | LV_261-531_0_8_line_16 |  | 13 | 14 | 0.002741 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
17 | LV_261-531_0_8_line_17 |  | 14 | 15 | 0.011813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
18 | LV_261-531_0_8_line_18 |  | 15 | 86 | 0.004185 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
19 | LV_261-531_0_8_line_19 |  | 16 | 17 | 0.02446 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_261-531_0_8_line_20 |  | 16 | 18 | 0.0087208 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_261-531_0_8_line_21 |  | 19 | 87 | 0.017757 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
22 | LV_261-531_0_8_line_22 |  | 20 | 21 | 0.009466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_261-531_0_8_line_23 |  | 20 | 22 | 0.017526 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_261-531_0_8_line_24 |  | 22 | 88 | 0.022416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_261-531_0_8_line_25 |  | 22 | 24 | 0.042275 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_261-531_0_8_line_26 |  | 23 | 24 | 0.062205 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_261-531_0_8_line_27 |  | 23 | 25 | 0.021679 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_261-531_0_8_line_28 |  | 24 | 26 | 0.040272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_261-531_0_8_line_29 |  | 27 | 28 | 0.004835 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
30 | LV_261-531_0_8_line_30 |  | 27 | 29 | 0.0261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_261-531_0_8_line_31 |  | 27 | 30 | 0.037217 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_261-531_0_8_line_32 |  | 27 | 31 | 0.036379 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
33 | LV_261-531_0_8_line_33 |  | 28 | 89 | 0.01167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
34 | LV_261-531_0_8_line_34 |  | 28 | 90 | 0.018642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_261-531_0_8_line_35 |  | 29 | 57 | 0.011484 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_261-531_0_8_line_36 |  | 29 | 58 | 0.003908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_261-531_0_8_line_37 |  | 30 | 59 | 0.031774 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_261-531_0_8_line_38 |  | 30 | 60 | 0.018954 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_261-531_0_8_line_39 |  | 31 | 91 | 0.017076 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
40 | LV_261-531_0_8_line_40 |  | 32 | 33 | 0.030322 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_261-531_0_8_line_41 |  | 32 | 34 | 0.0024942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_261-531_0_8_line_42 |  | 34 | 92 | 0.016873 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_261-531_0_8_line_43 |  | 35 | 36 | 0.010395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_261-531_0_8_line_44 |  | 35 | 37 | 0.015493 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_261-531_0_8_line_45 |  | 37 | 38 | 0.04152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_261-531_0_8_line_46 |  | 37 | 39 | 0.017255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_261-531_0_8_line_47 |  | 38 | 56 | 0.011102 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_261-531_0_8_line_48 |  | 38 | 46 | 0.039442 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_261-531_0_8_line_49 |  | 39 | 55 | 0.020103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_261-531_0_8_line_50 |  | 40 | 41 | 0.14535 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_261-531_0_8_line_51 |  | 40 | 42 | 0.058368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_261-531_0_8_line_52 |  | 40 | 43 | 0.02617 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_261-531_0_8_line_53 |  | 41 | 83 | 0.019278 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_261-531_0_8_line_54 |  | 41 | 79 | 0.030903 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_261-531_0_8_line_55 |  | 41 | 82 | 0.028179 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_261-531_0_8_line_56 |  | 42 | 93 | 0.032785 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_261-531_0_8_line_57 |  | 44 | 45 | 0.011668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_261-531_0_8_line_58 |  | 44 | 46 | 0.046252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_261-531_0_8_line_59 |  | 44 | 47 | 0.043361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_261-531_0_8_line_60 |  | 46 | 48 | 0.0065658 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_261-531_0_8_line_61 |  | 47 | 49 | 0.040154 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_261-531_0_8_line_62 |  | 47 | 50 | 0.0090659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_261-531_0_8_line_63 |  | 48 | 94 | 0.0096928 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_261-531_0_8_line_64 |  | 49 | 51 | 0.004116 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_261-531_0_8_line_65 |  | 50 | 95 | 0.007909 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_261-531_0_8_line_66 |  | 51 | 52 | 0.0030359 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_261-531_0_8_line_67 |  | 53 | 54 | 0.010287 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_261-531_0_8_line_68 |  | 53 | 55 | 0.007865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_261-531_0_8_line_69 |  | 55 | 96 | 0.004088 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_261-531_0_8_line_70 |  | 58 | 97 | 0.005621 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_261-531_0_8_line_71 |  | 58 | 94 | 0.022939 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_261-531_0_8_line_72 |  | 59 | 98 | 0.027525 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_261-531_0_8_line_73 |  | 61 | 62 | 0.00641 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_261-531_0_8_line_74 |  | 61 | 63 | 0.18675 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_261-531_0_8_line_75 |  | 61 | 64 | 0.028269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_261-531_0_8_line_76 |  | 63 | 74 | 0.016564 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_261-531_0_8_line_77 |  | 63 | 75 | 0.018523 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_261-531_0_8_line_78 |  | 64 | 99 | 0.018227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_261-531_0_8_line_79 |  | 65 | 66 | 0.003766 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_261-531_0_8_line_80 |  | 65 | 67 | 0.014471 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_261-531_0_8_line_81 |  | 66 | 72 | 0.025811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_261-531_0_8_line_82 |  | 67 | 82 | 0.013054 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_261-531_0_8_line_83 |  | 68 | 69 | 0.030176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_261-531_0_8_line_84 |  | 68 | 70 | 0.008878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
85 | LV_261-531_0_8_line_85 |  | 68 | 71 | 0.010428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
86 | LV_261-531_0_8_line_86 |  | 70 | 100 | 0.012214 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_261-531_0_8_line_87 |  | 70 | 78 | 0.042383 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
88 | LV_261-531_0_8_line_88 |  | 71 | 74 | 0.016131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
89 | LV_261-531_0_8_line_89 |  | 72 | 73 | 0.02247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_261-531_0_8_line_90 |  | 74 | 105 | 0.008389 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_261-531_0_8_line_91 |  | 76 | 77 | 0.0062343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
92 | LV_261-531_0_8_line_92 |  | 76 | 78 | 0.015134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
93 | LV_261-531_0_8_line_93 |  | 77 | 106 | 0.02206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
94 | LV_261-531_0_8_line_94 |  | 79 | 80 | 0.015082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_261-531_0_8_line_95 |  | 79 | 81 | 0.012184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_261-531_0_8_line_96 |  | 80 | 84 | 0.023159 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_261-531_0_8_line_97 |  | 83 | 109 | 0.0048457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_261-531_0_8_line_98 |  | 86 | 113 | 0.006082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
99 | LV_261-531_0_8_line_99 |  | 86 | 114 | 0.012736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_261-531_0_8_line_100 |  | 87 | 112 | 0.018015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
101 | LV_261-531_0_8_line_101 |  | 88 | 99 | 0.025271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_261-531_0_8_line_102 |  | 89 | 113 | 0.014225 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
103 | LV_261-531_0_8_line_103 |  | 90 | 92 | 0.017878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_261-531_0_8_line_104 |  | 91 | 116 | 0.017835 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
105 | LV_261-531_0_8_line_105 |  | 98 | 111 | 0.019196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_261-531_0_8_line_106 |  | 101 | 102 | 0.0049074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_261-531_0_8_line_107 |  | 102 | 103 | 0.019932 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_261-531_0_8_line_108 |  | 103 | 104 | 0.035428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_261-531_0_8_line_109 |  | 104 | 120 | 0.0052756 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_261-531_0_8_line_110 |  | 104 | 121 | 0.032357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_261-531_0_8_line_111 |  | 104 | 108 | 0.017975 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_261-531_0_8_line_112 |  | 105 | 123 | 0.031761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_261-531_0_8_line_113 |  | 106 | 112 | 0.021517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
114 | LV_261-531_0_8_line_114 |  | 107 | 108 | 0.021956 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_261-531_0_8_line_115 |  | 109 | 121 | 0.017478 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_261-531_0_8_line_116 |  | 110 | 111 | 0.0056778 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_261-531_0_8_line_117 |  | 113 | 115 | 0.008396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_261-531_0_8_line_118 |  | 116 | 117 | 0.021156 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_261-531_0_8_line_119 |  | 117 | 118 | 0.020307 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_261-531_0_8_line_120 |  | 118 | 119 | 0.023093 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_261-531_0_8_line_121 |  | 119 | 120 | 0.016544 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_261-531_0_8_line_122 |  | 121 | 122 | 0.022788 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_261-531_0_8_line_123 |  | 122 | 125 | 0.001422 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_261-531_0_8_line_124 |  | 123 | 124 | 0.00071002 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-531_0_8_trafo_51 | 0.63 MVA 20/0.4 kV | 126 | 112 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21
0 | 2683374.0981 | 1253044.5607 | 2683390.7888 | 1253032.0085
1 | 2683359.4447 | 1253054.1743 | 2683364.5897 | 1253051.6114 | 2683372.6884 | 1253045.6209 | 2683374.0981 | 1253044.5607
2 | 2683390.7888 | 1253032.0085 | 2683397.378 | 1253027.0532
3 | 2683359.4447 | 1253054.1743 | 2683354.9318 | 1253059.4496
4 | 2683353.721 | 1253043.697 | 2683356.502 | 1253048.7844 | 2683359.4447 | 1253054.1743
5 | 2683411.8943 | 1253016.1362 | 2683397.378 | 1253027.0532
6 | 2683353.721 | 1253043.697 | 2683359.0831 | 1253040.192 | 2683373.6517 | 1253029.2503
7 | 2683432.6158 | 1253000.5527 | 2683411.8943 | 1253016.1362
8 | 2683384.5882 | 1253021.0365 | 2683373.6517 | 1253029.2503
9 | 2683394.7486 | 1252979.5816 | 2683400.6641 | 1252986.6146 | 2683412.1756 | 1253000.3203
10 | 2683412.1756 | 1253000.3203 | 2683404.3288 | 1253006.2127
11 | 2683394.7486 | 1252979.5816 | 2683384.6619 | 1252967.5751
12 | 2683404.3288 | 1253006.2127 | 2683391.5617 | 1253015.7998
13 | 2683427.6708 | 1252976.5984 | 2683426.9163 | 1252975.5203
14 | 2683427.6708 | 1252976.5984 | 2683433.7683 | 1252984.101 | 2683437.9528 | 1252989.1971 | 2683431.0643 | 1252994.4485 | 2683434.8124 | 1252998.9046
15 | 2683434.8124 | 1252998.9046 | 2683455.1793 | 1252983.3835
16 | 2683432.6158 | 1253000.5527 | 2683434.8124 | 1252998.9046
17 | 2683432.6158 | 1253000.5527 | 2683433.929 | 1253002.1502 | 2683439.7316 | 1253009.9798
18 | 2683442.2234 | 1253013.3421 | 2683439.7316 | 1253009.9798
19 | 2683384.5882 | 1253021.0365 | 2683373.587 | 1253006.9933 | 2683369.4058 | 1253001.8599
20 | 2683384.5882 | 1253021.0365 | 2683391.5617 | 1253015.7998
21 | 2683455.1793 | 1252983.3835 | 2683469.3027 | 1252972.6204
22 | 2683431.181 | 1252806.7534 | 2683431.9575 | 1252805.2076 | 2683435.5557 | 1252798.3531
23 | 2683451.2953 | 1252806.0584 | 2683440.958 | 1252801.1202 | 2683435.5557 | 1252798.3531
24 | 2683451.2953 | 1252806.0584 | 2683469.2023 | 1252819.5429
25 | 2683451.2953 | 1252806.0584 | 2683433.5067 | 1252829.6923 | 2683426.5867 | 1252840.3807
26 | 2683369.9636 | 1252828.5971 | 2683377.5148 | 1252827.7471 | 2683395.0642 | 1252825.3701 | 2683400.9976 | 1252831.6806 | 2683411.1273 | 1252831.0004 | 2683426.5867 | 1252840.3807
27 | 2683369.9636 | 1252828.5971 | 2683375.1167 | 1252822.2648 | 2683378.7543 | 1252812.075 | 2683379.5284 | 1252809.4932
28 | 2683426.5867 | 1252840.3807 | 2683439.2626 | 1252846.4526 | 2683446.6513 | 1252852.8392 | 2683453.9796 | 1252867.567
29 | 2683464.1896 | 1253042.8959 | 2683462.6936 | 1253040.8845 | 2683461.8338 | 1253039.7826 | 2683461.2784 | 1253039.0298
30 | 2683464.1896 | 1253042.8959 | 2683466.0338 | 1253045.3682 | 2683471.9656 | 1253041.0708 | 2683481.3496 | 1253053.6458
31 | 2683464.1896 | 1253042.8959 | 2683466.0338 | 1253045.3682 | 2683471.9656 | 1253041.0708 | 2683474.9852 | 1253038.8561 | 2683493.835 | 1253025.5672
32 | 2683464.1896 | 1253042.8959 | 2683469.2771 | 1253039.0647 | 2683490.6567 | 1253022.976 | 2683493.2559 | 1253021.0201
33 | 2683461.2784 | 1253039.0298 | 2683454.3263 | 1253029.656
34 | 2683461.2784 | 1253039.0298 | 2683447.5157 | 1253049.0546 | 2683446.2635 | 1253050.0756
35 | 2683472.0993 | 1253060.4873 | 2683481.3496 | 1253053.6458
36 | 2683483.6901 | 1253056.7811 | 2683481.3496 | 1253053.6458
37 | 2683493.835 | 1253025.5672 | 2683519.1464 | 1253006.265
38 | 2683493.835 | 1253025.5672 | 2683505.3481 | 1253040.6236
39 | 2683493.2559 | 1253021.0201 | 2683506.9002 | 1253010.7519
40 | 2683418.0451 | 1253074.3587 | 2683413.1263 | 1253079.0707 | 2683403.549 | 1253096.2822 | 2683401.7527 | 1253099.646
41 | 2683418.0451 | 1253074.3587 | 2683419.8427 | 1253072.6296
42 | 2683432.4077 | 1253061.3733 | 2683422.8646 | 1253069.723 | 2683419.8427 | 1253072.6296
43 | 2683452.0376 | 1253134.6049 | 2683453.9564 | 1253138.2124 | 2683456.995 | 1253143.7483
44 | 2683460.2118 | 1253125.9357 | 2683450.028 | 1253131.0183 | 2683452.0376 | 1253134.6049
45 | 2683460.2118 | 1253125.9357 | 2683465.9572 | 1253123.0701 | 2683478.2431 | 1253116.6161 | 2683493.1742 | 1253108.2757 | 2683495.1608 | 1253111.8842
46 | 2683460.2118 | 1253125.9357 | 2683459.1666 | 1253124.5978 | 2683456.0021 | 1253122.1069 | 2683449.1815 | 1253112.8104
47 | 2683495.1608 | 1253111.8842 | 2683497.2969 | 1253115.5949 | 2683501.2939 | 1253121.1332
48 | 2683504.4204 | 1253087.7966 | 2683507.5013 | 1253091.932 | 2683511.0125 | 1253094.4612 | 2683511.9267 | 1253095.4526 | 2683512.9203 | 1253096.7009 | 2683504.1576 | 1253102.1481 | 2683493.1742 | 1253108.2757 | 2683495.1608 | 1253111.8842
49 | 2683436.7523 | 1253100.0859 | 2683438.7653 | 1253098.6131 | 2683449.1815 | 1253112.8104
50 | 2683634.6941 | 1253007.1066 | 2683637.6794 | 1253011.0628 | 2683640.847 | 1253008.5279 | 2683647.1095 | 1253016.0886 | 2683663.0077 | 1253037.0733 | 2683666.6823 | 1253041.9178 | 2683670.4361 | 1253048.0976 | 2683660.7459 | 1253052.9422 | 2683663.3727 | 1253059.3063 | 2683704.0222 | 1253041.9118 | 2683710.6431 | 1253058.2732 | 2683713.4737 | 1253060.3592 | 2683714.7819 | 1253063.9026
51 | 2683707.1784 | 1253105.3042 | 2683724.4403 | 1253098.6653 | 2683728.0265 | 1253097.4817 | 2683724.812 | 1253089.4525 | 2683720.8178 | 1253079.4663 | 2683714.7819 | 1253063.9026
52 | 2683714.7819 | 1253063.9026 | 2683690.613 | 1253073.9391
53 | 2683634.6941 | 1253007.1066 | 2683633.4718 | 1253005.4881 | 2683623.0841 | 1252991.7162
54 | 2683617.2978 | 1253027.5209 | 2683614.4408 | 1253024.1002 | 2683621.8009 | 1253017.5214 | 2683634.6941 | 1253007.1066
55 | 2683634.6941 | 1253007.1066 | 2683653.3357 | 1252992.0251 | 2683656.1365 | 1252995.1559
56 | 2683707.1784 | 1253105.3042 | 2683687.6443 | 1253113.6011 | 2683676.934 | 1253117.9574
57 | 2683540.1346 | 1253084.2529 | 2683542.7901 | 1253088.5936 | 2683547.2723 | 1253093.4271
58 | 2683504.4204 | 1253087.7966 | 2683507.5013 | 1253091.932 | 2683511.0125 | 1253094.4612 | 2683511.9267 | 1253095.4526 | 2683512.9203 | 1253096.7009 | 2683524.0584 | 1253089.7749 | 2683537.9053 | 1253080.7299 | 2683540.1346 | 1253084.2529
59 | 2683554.5383 | 1253056.613 | 2683557.9304 | 1253061.1643 | 2683559.6772 | 1253063.0459 | 2683560.165 | 1253063.7755 | 2683561.3939 | 1253065.4608 | 2683563.7232 | 1253068.318 | 2683549.1921 | 1253078.2428 | 2683540.1346 | 1253084.2529
60 | 2683504.4204 | 1253087.7966 | 2683500.4928 | 1253082.5351
61 | 2683554.5383 | 1253056.613 | 2683557.9304 | 1253061.1643 | 2683559.6772 | 1253063.0459 | 2683560.165 | 1253063.7755 | 2683561.3939 | 1253065.4608 | 2683575.1245 | 1253055.5803 | 2683577.2285 | 1253058.3565 | 2683580.0438 | 1253062.0657 | 2683583.6218 | 1253063.5951
62 | 2683554.5383 | 1253056.613 | 2683549.1125 | 1253049.35
63 | 2683494.6946 | 1253074.7678 | 2683500.4928 | 1253082.5351
64 | 2683583.6218 | 1253063.5951 | 2683587.6351 | 1253062.6288
65 | 2683544.379 | 1253043.0139 | 2683549.1125 | 1253049.35
66 | 2683587.6351 | 1253062.6288 | 2683588.3253 | 1253065.5852
67 | 2683440.3102 | 1253087.5154 | 2683432.0951 | 1253093.7377
68 | 2683436.7523 | 1253100.0859 | 2683432.0951 | 1253093.7377
69 | 2683436.7523 | 1253100.0859 | 2683433.5172 | 1253102.5978
70 | 2683483.6901 | 1253056.7811 | 2683488.2494 | 1253053.4762
71 | 2683483.6901 | 1253056.7811 | 2683482.1343 | 1253057.9378 | 2683493.2884 | 1253072.884 | 2683494.6946 | 1253074.7678
72 | 2683519.1464 | 1253006.265 | 2683528.9005 | 1252998.4966 | 2683541.3521 | 1252989.9435
73 | 2683513.9412 | 1252806.041 | 2683517.6899 | 1252800.8343
74 | 2683517.6899 | 1252800.8343 | 2683534.4547 | 1252812.3571 | 2683541.5617 | 1252823.1988 | 2683545.2483 | 1252822.3946 | 2683548.2226 | 1252819.6567 | 2683550.8471 | 1252816.5692 | 2683553.0515 | 1252812.7752 | 2683566.4404 | 1252821.793 | 2683571.4281 | 1252814.3578 | 2683572.7848 | 1252817.1568 | 2683572.9936 | 1252821.6075 | 2683576.2905 | 1252820.6088 | 2683583.8798 | 1252815.9902 | 2683584.8288 | 1252822.5418 | 2683583.2964 | 1252832.7279 | 2683594.5564 | 1252824.6918 | 2683598.6361 | 1252823.8376 | 2683605.6163 | 1252821.2008 | 2683612.2502 | 1252824.3857 | 2683616.8482 | 1252828.5203 | 2683596.6071 | 1252850.4846 | 2683601.1851 | 1252854.9636
75 | 2683494.6941 | 1252784.2978 | 2683517.6899 | 1252800.8343
76 | 2683589.9941 | 1252867.2038 | 2683601.1851 | 1252854.9636
77 | 2683601.1851 | 1252854.9636 | 2683614.4141 | 1252867.9284
78 | 2683494.6941 | 1252784.2978 | 2683484.0123 | 1252799.0666
79 | 2683664.5788 | 1252987.8362 | 2683662.2969 | 1252984.8351
80 | 2683664.5788 | 1252987.8362 | 2683667.2388 | 1252991.3209 | 2683669.3642 | 1252994.1864 | 2683667.5325 | 1253000.443
81 | 2683662.2969 | 1252984.8351 | 2683672.067 | 1252976.4779 | 2683679.3527 | 1252970.3762 | 2683681.9952 | 1252968.1562
82 | 2683656.1365 | 1252995.1559 | 2683658.945 | 1252998.2756 | 2683667.5325 | 1253000.443
83 | 2683571.9914 | 1252886.7313 | 2683594.2205 | 1252907.1391
84 | 2683571.9914 | 1252886.7313 | 2683566.0867 | 1252893.3752
85 | 2683571.9914 | 1252886.7313 | 2683579.0599 | 1252879.0641
86 | 2683566.0867 | 1252893.3752 | 2683575.3697 | 1252901.3455
87 | 2683566.0867 | 1252893.3752 | 2683557.5289 | 1252902.4614 | 2683548.2521 | 1252911.693 | 2683537.4133 | 1252921.4476 | 2683535.6283 | 1252922.7871
88 | 2683589.9941 | 1252867.2038 | 2683579.0599 | 1252879.0641
89 | 2683681.9952 | 1252968.1562 | 2683668.0251 | 1252950.5574
90 | 2683589.9941 | 1252867.2038 | 2683595.9375 | 1252873.1242
91 | 2683523.5239 | 1252931.8707 | 2683518.5388 | 1252935.6144
92 | 2683523.5239 | 1252931.8707 | 2683535.6283 | 1252922.7871
93 | 2683518.5388 | 1252935.6144 | 2683500.8991 | 1252948.8611
94 | 2683606.7616 | 1253028.1505 | 2683608.0819 | 1253029.7814 | 2683614.4408 | 1253024.1002 | 2683617.2978 | 1253027.5209
95 | 2683617.2978 | 1253027.5209 | 2683619.8121 | 1253030.6365 | 2683622.0214 | 1253033.4365 | 2683621.9185 | 1253038.0496
96 | 2683606.7616 | 1253028.1505 | 2683606.0301 | 1253027.0504 | 2683604.2099 | 1253024.4784 | 2683601.5916 | 1253020.7164 | 2683593.1986 | 1253009.3814
97 | 2683620.1661 | 1252987.8476 | 2683623.0841 | 1252991.7162
98 | 2683445.8523 | 1253018.2302 | 2683442.2234 | 1253013.3421
99 | 2683431.8554 | 1253020.7794 | 2683442.2234 | 1253013.3421
100 | 2683483.6931 | 1252961.7821 | 2683472.1461 | 1252970.4535 | 2683469.3027 | 1252972.6204
101 | 2683484.0123 | 1252799.0666 | 2683469.2023 | 1252819.5429
102 | 2683445.8523 | 1253018.2302 | 2683454.3263 | 1253029.656
103 | 2683432.4077 | 1253061.3733 | 2683446.2635 | 1253050.0756
104 | 2683521.1524 | 1253000.0297 | 2683516.14 | 1253003.7985 | 2683506.9002 | 1253010.7519
105 | 2683541.3521 | 1252989.9435 | 2683552.946 | 1253005.2434
106 | 2683632.8742 | 1252950.9556 | 2683629.8353 | 1252947.1022
107 | 2683617.4925 | 1252931.4513 | 2683629.8353 | 1252947.1022
108 | 2683590.1505 | 1252948.0669 | 2683592.3061 | 1252950.9328 | 2683617.4925 | 1252931.4513
109 | 2683590.1505 | 1252948.0669 | 2683586.3367 | 1252950.9375 | 2683585.9358 | 1252951.24
110 | 2683590.1505 | 1252948.0669 | 2683592.3061 | 1252950.9328 | 2683609.6408 | 1252973.8947
111 | 2683590.1505 | 1252948.0669 | 2683604.5256 | 1252937.2755
112 | 2683595.9375 | 1252873.1242 | 2683613.6597 | 1252890.7777 | 2683618.4737 | 1252886.0503
113 | 2683500.8991 | 1252948.8611 | 2683483.6931 | 1252961.7821
114 | 2683622.0789 | 1252924.0874 | 2683614.9244 | 1252929.4691 | 2683604.5256 | 1252937.2755
115 | 2683609.6408 | 1252973.8947 | 2683618.3821 | 1252985.4823 | 2683620.1661 | 1252987.8476
116 | 2683552.946 | 1253005.2434 | 2683556.3751 | 1253009.7686
117 | 2683452.7645 | 1253013.435 | 2683445.8523 | 1253018.2302
118 | 2683521.1524 | 1253000.0297 | 2683527.2302 | 1252995.4597 | 2683537.9087 | 1252987.4264 | 2683538.0594 | 1252987.3131
119 | 2683554.2866 | 1252975.1039 | 2683538.0594 | 1252987.3131
120 | 2683554.2866 | 1252975.1039 | 2683562.1642 | 1252969.1769 | 2683572.7292 | 1252961.2051
121 | 2683572.7292 | 1252961.2051 | 2683585.9358 | 1252951.24
122 | 2683591.4359 | 1252979.4309 | 2683593.0124 | 1252981.6214 | 2683594.1427 | 1252982.2712 | 2683598.3205 | 1252983.0196 | 2683599.8354 | 1252982.0847 | 2683601.0858 | 1252980.6457 | 2683609.6408 | 1252973.8947
123 | 2683591.4359 | 1252979.4309 | 2683590.607 | 1252978.2739
124 | 2683618.9803 | 1252885.5528 | 2683618.4737 | 1252886.0503

## bus_geodata
| x | y | coords
0 | 2683374.0981 | 1253044.5607
1 | 2683390.7888 | 1253032.0085
2 | 2683359.4447 | 1253054.1743
3 | 2683397.378 | 1253027.0532
4 | 2683354.9318 | 1253059.4496
5 | 2683353.721 | 1253043.697
6 | 2683411.8943 | 1253016.1362
7 | 2683373.6517 | 1253029.2503
8 | 2683412.1756 | 1253000.3203
9 | 2683394.7486 | 1252979.5816
10 | 2683404.3288 | 1253006.2127
11 | 2683427.6708 | 1252976.5984
12 | 2683426.9163 | 1252975.5203
13 | 2683434.8124 | 1252998.9046
14 | 2683432.6158 | 1253000.5527
15 | 2683439.7316 | 1253009.9798
16 | 2683384.5882 | 1253021.0365
17 | 2683369.4058 | 1253001.8599
18 | 2683391.5617 | 1253015.7998
19 | 2683455.1793 | 1252983.3835
20 | 2683435.5557 | 1252798.3531
21 | 2683431.181 | 1252806.7534
22 | 2683451.2953 | 1252806.0584
23 | 2683369.9636 | 1252828.5971
24 | 2683426.5867 | 1252840.3807
25 | 2683379.5284 | 1252809.4932
26 | 2683453.9796 | 1252867.567
27 | 2683464.1896 | 1253042.8959
28 | 2683461.2784 | 1253039.0298
29 | 2683481.3496 | 1253053.6458
30 | 2683493.835 | 1253025.5672
31 | 2683493.2559 | 1253021.0201
32 | 2683418.0451 | 1253074.3587
33 | 2683401.7527 | 1253099.646
34 | 2683419.8427 | 1253072.6296
35 | 2683452.0376 | 1253134.6049
36 | 2683456.995 | 1253143.7483
37 | 2683460.2118 | 1253125.9357
38 | 2683495.1608 | 1253111.8842
39 | 2683449.1815 | 1253112.8104
40 | 2683714.7819 | 1253063.9026
41 | 2683634.6941 | 1253007.1066
42 | 2683707.1784 | 1253105.3042
43 | 2683690.613 | 1253073.9391
44 | 2683540.1346 | 1253084.2529
45 | 2683547.2723 | 1253093.4271
46 | 2683504.4204 | 1253087.7966
47 | 2683554.5383 | 1253056.613
48 | 2683500.4928 | 1253082.5351
49 | 2683583.6218 | 1253063.5951
50 | 2683549.1125 | 1253049.35
51 | 2683587.6351 | 1253062.6288
52 | 2683588.3253 | 1253065.5852
53 | 2683432.0951 | 1253093.7377
54 | 2683440.3102 | 1253087.5154
55 | 2683436.7523 | 1253100.0859
56 | 2683501.2939 | 1253121.1332
57 | 2683472.0993 | 1253060.4873
58 | 2683483.6901 | 1253056.7811
59 | 2683519.1464 | 1253006.265
60 | 2683505.3481 | 1253040.6236
61 | 2683517.6899 | 1252800.8343
62 | 2683513.9412 | 1252806.041
63 | 2683601.1851 | 1252854.9636
64 | 2683494.6941 | 1252784.2978
65 | 2683664.5788 | 1252987.8362
66 | 2683662.2969 | 1252984.8351
67 | 2683667.5325 | 1253000.443
68 | 2683571.9914 | 1252886.7313
69 | 2683594.2205 | 1252907.1391
70 | 2683566.0867 | 1252893.3752
71 | 2683579.0599 | 1252879.0641
72 | 2683681.9952 | 1252968.1562
73 | 2683668.0251 | 1252950.5574
74 | 2683589.9941 | 1252867.2039
75 | 2683614.4141 | 1252867.9284
76 | 2683523.5239 | 1252931.8707
77 | 2683518.5388 | 1252935.6144
78 | 2683535.6283 | 1252922.7871
79 | 2683617.2978 | 1253027.5209
80 | 2683606.7616 | 1253028.1505
81 | 2683621.9185 | 1253038.0496
82 | 2683656.1365 | 1252995.1559
83 | 2683623.0841 | 1252991.7162
84 | 2683593.1986 | 1253009.3814
85 | 2683384.6619 | 1252967.5751
86 | 2683442.2234 | 1253013.3421
87 | 2683469.3027 | 1252972.6204
88 | 2683469.2023 | 1252819.5429
89 | 2683454.3263 | 1253029.656
90 | 2683446.2635 | 1253050.0756
91 | 2683506.9002 | 1253010.7519
92 | 2683432.4077 | 1253061.3733
93 | 2683676.934 | 1253117.9574
94 | 2683494.6946 | 1253074.7678
95 | 2683544.379 | 1253043.0139
96 | 2683433.5172 | 1253102.5978
97 | 2683488.2494 | 1253053.4762
98 | 2683541.3521 | 1252989.9435
99 | 2683484.0123 | 1252799.0666
100 | 2683575.3697 | 1252901.3455
101 | 2683632.8741 | 1252950.9556
102 | 2683629.8353 | 1252947.1022
103 | 2683617.4925 | 1252931.4513
104 | 2683590.1505 | 1252948.0669
105 | 2683595.9375 | 1252873.1242
106 | 2683500.8991 | 1252948.8611
107 | 2683622.0789 | 1252924.0874
108 | 2683604.5256 | 1252937.2755
109 | 2683620.1661 | 1252987.8476
110 | 2683556.3751 | 1253009.7686
111 | 2683552.946 | 1253005.2434
112 | 2683483.6931 | 1252961.7821
113 | 2683445.8523 | 1253018.2302
114 | 2683431.8554 | 1253020.7794
115 | 2683452.7645 | 1253013.435
116 | 2683521.1524 | 1253000.0297
117 | 2683538.0594 | 1252987.3131
118 | 2683554.2866 | 1252975.1039
119 | 2683572.7292 | 1252961.2051
120 | 2683585.9358 | 1252951.24
121 | 2683609.6408 | 1252973.8947
122 | 2683591.4359 | 1252979.4309
123 | 2683618.4737 | 1252886.0503
124 | 2683618.9803 | 1252885.5528
125 | 2683590.607 | 1252978.2739
126 | 2683523.5239 | 1252931.8707

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98433 | -0.29826 | 0.0032316 | 0.00080991
1 | 0.98685 | -0.24967 | 0.001989 | 0.00049848
2 | 0.98226 | -0.33833 | 0 | 0
3 | 0.98787 | -0.23027 | 0.0021721 | 0.00054439
4 | 0.98224 | -0.33871 | 0.0030322 | 0.00075993
5 | 0.98088 | -0.36498 | 0 | 0
6 | 0.99013 | -0.18695 | 0.0024826 | 0.00062219
7 | 0.97805 | -0.42019 | 0.00426 | 0.0010677
8 | 0.97337 | -0.51194 | 0 | 0
9 | 0.97202 | -0.5387 | 0 | 0
10 | 0.97387 | -0.50225 | 0.061109 | 0.015315
11 | 0.99354 | -0.12228 | 0 | 0
12 | 0.99353 | -0.12241 | 0.0058793 | 0.0014735
13 | 0.9937 | -0.11908 | 0 | 0
14 | 0.99343 | -0.12433 | 0 | 0
15 | 0.99261 | -0.13987 | 0.0036921 | 0.00092532
16 | 0.97653 | -0.44992 | 0 | 0
17 | 0.97649 | -0.45077 | 0.0018953 | 0.000475
18 | 0.97558 | -0.46863 | 0.0024335 | 0.00060989
19 | 0.99631 | -0.069523 | 0.0030637 | 0.00076784
20 | 0.97156 | -0.5473 | 0 | 0
21 | 0.97154 | -0.54774 | 0.0025056 | 0.00062796
22 | 0.97161 | -0.54649 | 0 | 0
23 | 0.97084 | -0.56156 | 0 | 0
24 | 0.9712 | -0.55451 | 0 | 0
25 | 0.97072 | -0.56402 | 0.0061285 | 0.001536
26 | 0.97104 | -0.55759 | 0.0041386 | 0.0010372
27 | 0.98955 | -0.19855 | 0 | 0
28 | 0.98994 | -0.1911 | 0 | 0
29 | 0.98702 | -0.24749 | 0 | 0
30 | 0.98862 | -0.21659 | 0 | 0
31 | 0.98812 | -0.22608 | 0.0024862 | 0.00062309
32 | 0.98893 | -0.21082 | 0 | 0
33 | 0.98869 | -0.2154 | 0.0084828 | 0.002126
34 | 0.98895 | -0.21044 | 0.008986 | 0.0022521
35 | 0.98103 | -0.36419 | 0 | 0
36 | 0.98097 | -0.36548 | 0.0068302 | 0.0017118
37 | 0.98113 | -0.36227 | 0 | 0
38 | 0.98228 | -0.33972 | 0 | 0
39 | 0.98076 | -0.36952 | 0.0068026 | 0.0017049
40 | 0.97169 | -0.54623 | 0 | 0
41 | 0.97336 | -0.51331 | 0 | 0
42 | 0.97128 | -0.55442 | 0 | 0
43 | 0.97158 | -0.54849 | 0.0046851 | 0.0011742
44 | 0.98211 | -0.34315 | 0 | 0
45 | 0.98202 | -0.34481 | 0.0078979 | 0.0019794
46 | 0.98363 | -0.31345 | 0 | 0
47 | 0.981 | -0.36487 | 0 | 0
48 | 0.98407 | -0.30488 | 0.0088314 | 0.0022134
49 | 0.98061 | -0.37249 | 0 | 0
50 | 0.98085 | -0.36769 | 0.0093697 | 0.0023483
51 | 0.98057 | -0.37328 | 0 | 0
52 | 0.98054 | -0.37385 | 0.010484 | 0.0026276
53 | 0.9804 | -0.37653 | 0 | 0
54 | 0.98033 | -0.37788 | 0.0072436 | 0.0018154
55 | 0.98045 | -0.3755 | 0 | 0
56 | 0.98221 | -0.3411 | 0.0068903 | 0.0017269
57 | 0.98694 | -0.24918 | 0.0082156 | 0.002059
58 | 0.98667 | -0.25427 | 0 | 0
59 | 0.9881 | -0.22683 | 0 | 0
60 | 0.98847 | -0.21968 | 0.0091471 | 0.0022925
61 | 0.97535 | -0.47265 | 0 | 0
62 | 0.97505 | -0.47864 | 0.050973 | 0.012775
63 | 0.99366 | -0.11959 | 0 | 0
64 | 0.97392 | -0.50074 | 0 | 0
65 | 0.97248 | -0.53073 | 0 | 0
66 | 0.97244 | -0.53149 | 0 | 0
67 | 0.97263 | -0.52781 | 0.0081383 | 0.0020396
68 | 0.99645 | -0.066869 | 0 | 0
69 | 0.99641 | -0.067559 | 0.0013039 | 0.00032678
70 | 0.9967 | -0.062046 | 0 | 0
71 | 0.99615 | -0.072476 | 0.0086244 | 0.0021615
72 | 0.97218 | -0.53671 | 0 | 0
73 | 0.97195 | -0.54125 | 0.010959 | 0.0027466
74 | 0.9953 | -0.088622 | 0 | 0
75 | 0.99364 | -0.11991 | 0.00096875 | 0.00024279
76 | 0.99841 | -0.029853 | 0 | 0
77 | 0.9986 | -0.026296 | 0.0052401 | 0.0013133
78 | 0.99795 | -0.038493 | 0.0036821 | 0.00092282
79 | 0.97292 | -0.52209 | 0 | 0
80 | 0.9728 | -0.52441 | 0 | 0
81 | 0.97284 | -0.52368 | 0.007096 | 0.0017784
82 | 0.97286 | -0.52321 | 0 | 0
83 | 0.9742 | -0.49671 | 0.011863 | 0.0029732
84 | 0.97262 | -0.52797 | 0.0083465 | 0.0020918
85 | 0.97123 | -0.55423 | 0.05369 | 0.013456
86 | 0.99233 | -0.14531 | 0 | 0
87 | 0.99814 | -0.035068 | 0.0030637 | 0.00076784
88 | 0.97187 | -0.54121 | 0.035134 | 0.0088053
89 | 0.99097 | -0.17138 | 0.0034346 | 0.0008608
90 | 0.9895 | -0.19963 | 0.0082352 | 0.0020639
91 | 0.98746 | -0.23878 | 0.0035812 | 0.00089754
92 | 0.98922 | -0.20519 | 0 | 0
93 | 0.97105 | -0.55903 | 0.0076002 | 0.0019048
94 | 0.9848 | -0.2907 | 0.0071853 | 0.0018008
95 | 0.9808 | -0.36881 | 0.0078307 | 0.0019625
96 | 0.98042 | -0.37618 | 0.009153 | 0.002294
97 | 0.98663 | -0.25511 | 0.0083415 | 0.0020906
98 | 0.98764 | -0.2357 | 0 | 0
99 | 0.973 | -0.51889 | 0.0062299 | 0.0015614
100 | 0.99667 | -0.0627 | 0.0030505 | 0.00076452
101 | 0.97639 | -0.45385 | 0.010683 | 0.0026774
102 | 0.97644 | -0.4529 | 0.01191 | 0.0029849
103 | 0.97685 | -0.44467 | 0 | 0
104 | 0.9776 | -0.43006 | 0 | 0
105 | 0.99524 | -0.089771 | 0.0021285 | 0.00053345
106 | 0.9993 | -0.013216 | 0.0050666 | 0.0012698
107 | 0.9774 | -0.43388 | 0.0038179 | 0.00095685
108 | 0.97748 | -0.43235 | 0.0031729 | 0.00079519
109 | 0.97447 | -0.49149 | 0.0039083 | 0.0009795
110 | 0.98728 | -0.24276 | 0.0084662 | 0.0021218
111 | 0.98732 | -0.2419 | 0.0095909 | 0.0024037
112 | 1 | 0 | -0.59963 | -0.15424
113 | 0.99192 | -0.15316 | 0 | 0
114 | 0.9923 | -0.14579 | 0.0021525 | 0.00053947
115 | 0.9919 | -0.15359 | 0.0028995 | 0.00072668
116 | 0.98645 | -0.25814 | 0.0041472 | 0.0010394
117 | 0.98414 | -0.30264 | 0.0046058 | 0.0011543
118 | 0.98202 | -0.34386 | 0.0041644 | 0.0010437
119 | 0.97969 | -0.38921 | 0.0044744 | 0.0011214
120 | 0.97809 | -0.42048 | 0.0043814 | 0.0010981
121 | 0.97549 | -0.47142 | 0 | 0
122 | 0.97533 | -0.47449 | 0 | 0
123 | 0.99507 | -0.092928 | 0.0021289 | 0.00053354
124 | 0.99507 | -0.092972 | 0.0035195 | 0.00088206
125 | 0.97532 | -0.47468 | 0.0073355 | 0.0018384
126 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.13098 | -0.033342 | 0.13129 | 0.033538 | 0.00030761 | 0.0001966 | 0.19819 | 0.19819 | 0.19819 | 0.98433 | -0.29826 | 0.98685 | -0.24967 | 54.4473
1 | 0.12775 | 0.032532 | -0.1275 | -0.032374 | 0.00024641 | 0.00015748 | 0.1933 | 0.1933 | 0.1933 | 0.98433 | -0.29826 | 0.98226 | -0.33833 | 53.1053
2 | -0.13328 | -0.034037 | 0.1334 | 0.034117 | 0.00012514 | 7.9984e-05 | 0.20119 | 0.20119 | 0.20119 | 0.98685 | -0.24967 | 0.98787 | -0.23027 | 55.2712
3 | 0.0030322 | 0.00075988 | -0.0030322 | -0.00075993 | 5.4931e-08 | -5.2716e-08 | 0.0045935 | 0.0045935 | 0.0045935 | 0.98226 | -0.33833 | 0.98224 | -0.33871 | 1.262
4 | 0.12447 | 0.031614 | -0.12431 | -0.031513 | 0.00015943 | 0.00010189 | 0.18871 | 0.18871 | 0.18871 | 0.98226 | -0.33833 | 0.98088 | -0.36498 | 51.8434
5 | -0.13557 | -0.034661 | 0.13586 | 0.034843 | 0.00028473 | 0.000182 | 0.20446 | 0.20446 | 0.20446 | 0.98787 | -0.23027 | 0.99013 | -0.18695 | 56.1701
6 | 0.12431 | 0.031513 | -0.12398 | -0.031302 | 0.00032886 | 0.00021016 | 0.18871 | 0.18871 | 0.18871 | 0.98088 | -0.36498 | 0.97805 | -0.42019 | 51.8434
7 | -0.13834 | -0.035465 | 0.13876 | 0.035735 | 0.00042141 | 0.00026937 | 0.20819 | 0.20819 | 0.20819 | 0.99013 | -0.18695 | 0.99343 | -0.12433 | 57.195
8 | 0.11972 | 0.030235 | -0.11955 | -0.030126 | 0.00017032 | 0.00010883 | 0.18223 | 0.18223 | 0.18223 | 0.97805 | -0.42019 | 0.97653 | -0.44992 | 50.0628
9 | 0.053798 | 0.013525 | -0.05373 | -0.013481 | 6.8651e-05 | 4.3601e-05 | 0.082257 | 0.082257 | 0.082257 | 0.97337 | -0.51194 | 0.97202 | -0.5387 | 22.5982
10 | -0.053798 | -0.013525 | 0.053823 | 0.013541 | 2.4899e-05 | 1.5813e-05 | 0.082257 | 0.082257 | 0.082257 | 0.97337 | -0.51194 | 0.97387 | -0.50225 | 22.5982
11 | 0.05373 | 0.013481 | -0.05369 | -0.013456 | 3.974e-05 | 2.524e-05 | 0.082257 | 0.082258 | 0.082258 | 0.97202 | -0.5387 | 0.97123 | -0.55423 | 22.5982
12 | -0.11493 | -0.028856 | 0.11512 | 0.028974 | 0.00018468 | 0.000118 | 0.17563 | 0.17563 | 0.17563 | 0.97387 | -0.50225 | 0.97558 | -0.46863 | 48.2497
13 | 0.0058793 | 0.0014735 | -0.0058793 | -0.0014735 | 3.8234e-08 | 7.4406e-09 | 0.0088054 | 0.0088054 | 0.0088054 | 0.99354 | -0.12228 | 0.99353 | -0.12241 | 2.4191
14 | -0.0058793 | -0.0014735 | 0.0058802 | 0.0014737 | 8.9396e-07 | 1.7389e-07 | 0.0088054 | 0.0088053 | 0.0088054 | 0.99354 | -0.12228 | 0.9937 | -0.11908 | 2.4191
15 | -0.4457 | -0.11401 | 0.44677 | 0.1147 | 0.001072 | 0.00068472 | 0.66823 | 0.66823 | 0.66823 | 0.9937 | -0.11908 | 0.99631 | -0.069523 | 45.8948
16 | 0.43982 | 0.11254 | -0.4397 | -0.11247 | 0.00011174 | 7.1372e-05 | 0.65942 | 0.65942 | 0.65942 | 0.9937 | -0.11908 | 0.99343 | -0.12433 | 45.29
17 | 0.30094 | 0.076732 | -0.30072 | -0.076588 | 0.0002255 | 0.00014371 | 0.45123 | 0.45123 | 0.45123 | 0.99343 | -0.12433 | 0.99261 | -0.13987 | 30.9913
18 | 0.29702 | 0.075663 | -0.29695 | -0.075613 | 7.7938e-05 | 4.9664e-05 | 0.4457 | 0.4457 | 0.4457 | 0.99261 | -0.13987 | 0.99233 | -0.14531 | 30.6112
19 | 0.0018953 | 0.00047474 | -0.0018953 | -0.000475 | 7.6506e-08 | -2.5703e-07 | 0.002888 | 0.0028881 | 0.0028881 | 0.97653 | -0.44992 | 0.97649 | -0.45077 | 0.79344
20 | 0.11766 | 0.029651 | -0.11755 | -0.029584 | 0.00010518 | 6.7208e-05 | 0.17934 | 0.17934 | 0.17934 | 0.97653 | -0.44992 | 0.97558 | -0.46863 | 49.2694
21 | -0.44983 | -0.11546 | 0.45058 | 0.11595 | 0.00075357 | 0.00048135 | 0.6728 | 0.6728 | 0.6728 | 0.99631 | -0.069523 | 0.99814 | -0.035068 | 46.209
22 | 0.0025056 | 0.00062787 | -0.0025056 | -0.00062796 | 5.2276e-08 | -8.3766e-08 | 0.0038375 | 0.0038375 | 0.0038375 | 0.97156 | -0.5473 | 0.97154 | -0.54774 | 1.0543
23 | -0.0025056 | -0.00062787 | 0.0025057 | 0.00062772 | 9.6783e-08 | -1.5511e-07 | 0.0038375 | 0.0038374 | 0.0038375 | 0.97156 | -0.5473 | 0.97161 | -0.54649 | 1.0543
24 | -0.01278 | -0.0032035 | 0.012783 | 0.0032053 | 3.2204e-06 | 1.7834e-06 | 0.019573 | 0.019573 | 0.019573 | 0.97161 | -0.54649 | 0.97187 | -0.54121 | 5.3772
25 | 0.010274 | 0.0025758 | -0.01027 | -0.0025738 | 3.9254e-06 | 1.9889e-06 | 0.015736 | 0.015736 | 0.015736 | 0.97161 | -0.54649 | 0.9712 | -0.55451 | 4.323
26 | -0.0061293 | -0.0015361 | 0.0061313 | 0.0015367 | 2.0586e-06 | 5.4804e-07 | 0.0093943 | 0.0093941 | 0.0093943 | 0.97084 | -0.56156 | 0.9712 | -0.55451 | 2.5809
27 | 0.0061293 | 0.0015361 | -0.0061285 | -0.001536 | 7.1747e-07 | 1.9115e-07 | 0.0093943 | 0.0093944 | 0.0093944 | 0.97084 | -0.56156 | 0.97072 | -0.56402 | 2.5809
28 | 0.0041392 | 0.0010371 | -0.0041386 | -0.0010372 | 6.0737e-07 | -1.0954e-07 | 0.0063417 | 0.0063419 | 0.0063419 | 0.9712 | -0.55451 | 0.97104 | -0.55759 | 1.7423
29 | -0.262 | -0.066563 | 0.26209 | 0.066623 | 9.3961e-05 | 5.9948e-05 | 0.39429 | 0.39429 | 0.39429 | 0.98955 | -0.19855 | 0.98994 | -0.1911 | 36.1075
30 | 0.10578 | 0.026778 | -0.10553 | -0.02662 | 0.00024792 | 0.00015833 | 0.15916 | 0.15916 | 0.15916 | 0.98955 | -0.19855 | 0.98702 | -0.24749 | 43.724
31 | 0.027251 | 0.0068463 | -0.027228 | -0.0068318 | 2.3443e-05 | 1.4526e-05 | 0.040984 | 0.040984 | 0.040984 | 0.98955 | -0.19855 | 0.98862 | -0.21659 | 11.2594
32 | 0.12897 | 0.032939 | -0.1288 | -0.032831 | 0.00017142 | 0.00010831 | 0.19415 | 0.19416 | 0.19416 | 0.98955 | -0.19855 | 0.98812 | -0.22608 | 17.7798
33 | -0.28782 | -0.073078 | 0.28809 | 0.073253 | 0.00027347 | 0.00017457 | 0.43297 | 0.43296 | 0.43297 | 0.98994 | -0.1911 | 0.99097 | -0.17138 | 39.6488
34 | 0.025726 | 0.0064547 | -0.025715 | -0.0064482 | 1.0455e-05 | 6.4515e-06 | 0.038671 | 0.038672 | 0.038672 | 0.98994 | -0.1911 | 0.9895 | -0.19963 | 10.6241
35 | 0.0082162 | 0.0020593 | -0.0082156 | -0.002059 | 6.6075e-07 | 2.7611e-07 | 0.012387 | 0.012387 | 0.012387 | 0.98702 | -0.24749 | 0.98694 | -0.24918 | 3.4029
36 | 0.097313 | 0.02456 | -0.097282 | -0.02454 | 3.1568e-05 | 2.0154e-05 | 0.14677 | 0.14677 | 0.14677 | 0.98702 | -0.24749 | 0.98667 | -0.25427 | 40.3211
37 | 0.018079 | 0.0045387 | -0.018071 | -0.0045334 | 8.8249e-06 | 5.2407e-06 | 0.027215 | 0.027215 | 0.027215 | 0.98862 | -0.21659 | 0.9881 | -0.22683 | 7.4766
38 | 0.0091485 | 0.0022931 | -0.0091471 | -0.0022925 | 1.3477e-06 | 6.1951e-07 | 0.01377 | 0.01377 | 0.01377 | 0.98862 | -0.21659 | 0.98847 | -0.21968 | 3.7829
39 | 0.12631 | 0.032208 | -0.12623 | -0.032159 | 7.7391e-05 | 4.8875e-05 | 0.19041 | 0.19041 | 0.19041 | 0.98812 | -0.22608 | 0.98746 | -0.23878 | 17.437
40 | 0.0084847 | 0.0021268 | -0.0084828 | -0.002126 | 1.8533e-06 | 7.9718e-07 | 0.012767 | 0.012767 | 0.012767 | 0.98893 | -0.21082 | 0.98869 | -0.2154 | 3.5074
41 | -0.0084847 | -0.0021268 | 0.0084848 | 0.0021269 | 1.5245e-07 | 6.5566e-08 | 0.012767 | 0.012767 | 0.012767 | 0.98893 | -0.21082 | 0.98895 | -0.21044 | 3.5074
42 | -0.017471 | -0.004379 | 0.017475 | 0.0043816 | 4.3725e-06 | 2.5818e-06 | 0.026288 | 0.026288 | 0.026288 | 0.98895 | -0.21044 | 0.98922 | -0.20519 | 7.2219
43 | 0.0068306 | 0.0017119 | -0.0068302 | -0.0017118 | 4.1843e-07 | 1.3656e-07 | 0.010361 | 0.010361 | 0.010361 | 0.98103 | -0.36419 | 0.98097 | -0.36548 | 2.8463
44 | -0.0068306 | -0.0017119 | 0.0068312 | 0.0017121 | 6.2363e-07 | 2.0349e-07 | 0.010361 | 0.010361 | 0.010361 | 0.98103 | -0.36419 | 0.98113 | -0.36227 | 2.8463
45 | -0.030044 | -0.0075345 | 0.030077 | 0.0075547 | 3.233e-05 | 2.0166e-05 | 0.045568 | 0.045568 | 0.045568 | 0.98113 | -0.36227 | 0.98228 | -0.33972 | 12.5187
46 | 0.023213 | 0.0058224 | -0.023205 | -0.0058174 | 8.0209e-06 | 4.9155e-06 | 0.035207 | 0.035207 | 0.035207 | 0.98113 | -0.36227 | 0.98076 | -0.36952 | 9.6724
47 | 0.0068908 | 0.001727 | -0.0068903 | -0.0017269 | 4.5364e-07 | 1.4981e-07 | 0.010439 | 0.010439 | 0.010439 | 0.98228 | -0.33972 | 0.98221 | -0.3411 | 2.8677
48 | -0.036967 | -0.0092817 | 0.037014 | 0.0093109 | 4.6394e-05 | 2.9192e-05 | 0.056006 | 0.056006 | 0.056006 | 0.98228 | -0.33972 | 0.98363 | -0.31345 | 15.3863
49 | 0.016402 | 0.0041125 | -0.016398 | -0.0041098 | 4.6689e-06 | 2.7345e-06 | 0.024886 | 0.024887 | 0.024887 | 0.98076 | -0.36952 | 0.98045 | -0.3755 | 6.837
50 | -0.01229 | -0.0030808 | 0.01231 | 0.0030914 | 1.9307e-05 | 1.0553e-05 | 0.018821 | 0.018821 | 0.018821 | 0.97169 | -0.54623 | 0.97336 | -0.51331 | 5.1707
51 | 0.0076048 | 0.0019066 | -0.0076019 | -0.0019054 | 2.9687e-06 | 1.1773e-06 | 0.011646 | 0.011646 | 0.011646 | 0.97169 | -0.54623 | 0.97128 | -0.55442 | 3.1995
52 | 0.0046857 | 0.0011742 | -0.0046851 | -0.0011742 | 5.0528e-07 | -7.5265e-10 | 0.0071754 | 0.0071755 | 0.0071755 | 0.97169 | -0.54623 | 0.97158 | -0.54849 | 1.9713
53 | -0.046879 | -0.011764 | 0.046916 | 0.011788 | 3.7136e-05 | 2.3527e-05 | 0.071672 | 0.071672 | 0.071672 | 0.97336 | -0.51331 | 0.9742 | -0.49671 | 19.6901
54 | 0.015452 | 0.0038752 | -0.015445 | -0.0038715 | 6.4669e-06 | 3.7549e-06 | 0.023623 | 0.023623 | 0.023623 | 0.97336 | -0.51331 | 0.97292 | -0.52209 | 6.4898
55 | 0.019118 | 0.0047979 | -0.019109 | -0.0047924 | 9.0275e-06 | 5.4275e-06 | 0.029228 | 0.029228 | 0.029228 | 0.97336 | -0.51331 | 0.97286 | -0.52321 | 8.0298
56 | 0.0076019 | 0.0019054 | -0.0076002 | -0.0019048 | 1.6676e-06 | 6.6159e-07 | 0.011646 | 0.011646 | 0.011646 | 0.97128 | -0.55442 | 0.97105 | -0.55903 | 3.1996
57 | 0.0078985 | 0.0019797 | -0.0078979 | -0.0019794 | 6.2665e-07 | 2.5342e-07 | 0.011967 | 0.011967 | 0.011967 | 0.98211 | -0.34315 | 0.98202 | -0.34481 | 3.2877
58 | -0.035619 | -0.0089396 | 0.035669 | 0.0089714 | 5.0524e-05 | 3.1749e-05 | 0.053972 | 0.053971 | 0.053972 | 0.98211 | -0.34315 | 0.98363 | -0.31345 | 14.8274
59 | 0.02772 | 0.00696 | -0.027692 | -0.0069422 | 2.8689e-05 | 1.7813e-05 | 0.042004 | 0.042005 | 0.042005 | 0.98211 | -0.34315 | 0.981 | -0.36487 | 11.5397
60 | -0.072683 | -0.018282 | 0.072713 | 0.018301 | 2.978e-05 | 1.8976e-05 | 0.10998 | 0.10998 | 0.10998 | 0.98363 | -0.31345 | 0.98407 | -0.30488 | 30.2136
61 | 0.010489 | 0.0026298 | -0.010485 | -0.0026279 | 3.8116e-06 | 1.9326e-06 | 0.01591 | 0.01591 | 0.01591 | 0.981 | -0.36487 | 0.98061 | -0.37249 | 4.3709
62 | 0.017203 | 0.0043123 | -0.017201 | -0.004311 | 2.315e-06 | 1.3671e-06 | 0.026095 | 0.026095 | 0.026095 | 0.981 | -0.36487 | 0.98085 | -0.36769 | 7.1689
63 | -0.081544 | -0.020515 | 0.0816 | 0.02055 | 5.5288e-05 | 3.5261e-05 | 0.12333 | 0.12333 | 0.12333 | 0.98407 | -0.30488 | 0.9848 | -0.2907 | 33.8823
64 | 0.010485 | 0.0026279 | -0.010484 | -0.0026277 | 3.9071e-07 | 1.9813e-07 | 0.01591 | 0.01591 | 0.01591 | 0.98061 | -0.37249 | 0.98057 | -0.37328 | 4.3709
65 | 0.0078311 | 0.0019627 | -0.0078307 | -0.0019625 | 4.1861e-07 | 1.6809e-07 | 0.01188 | 0.01188 | 0.01188 | 0.98085 | -0.36769 | 0.9808 | -0.36881 | 3.2638
66 | 0.010484 | 0.0026277 | -0.010484 | -0.0026276 | 2.8818e-07 | 1.4614e-07 | 0.01591 | 0.01591 | 0.01591 | 0.98057 | -0.37328 | 0.98054 | -0.37385 | 4.3709
67 | 0.007244 | 0.0018156 | -0.0072436 | -0.0018154 | 4.6633e-07 | 1.6874e-07 | 0.010995 | 0.010995 | 0.010995 | 0.9804 | -0.37653 | 0.98033 | -0.37788 | 3.0205
68 | -0.007244 | -0.0018156 | 0.0072444 | 0.0018157 | 3.5653e-07 | 1.29e-07 | 0.010995 | 0.010995 | 0.010995 | 0.9804 | -0.37653 | 0.98045 | -0.3755 | 3.0205
69 | 0.0091533 | 0.0022941 | -0.009153 | -0.002294 | 2.9584e-07 | 1.3779e-07 | 0.013892 | 0.013892 | 0.013892 | 0.98045 | -0.3755 | 0.98042 | -0.37618 | 3.8164
70 | 0.0083419 | 0.0020907 | -0.0083415 | -0.0020906 | 3.3361e-07 | 1.4173e-07 | 0.012581 | 0.012581 | 0.012581 | 0.98667 | -0.25427 | 0.98663 | -0.25511 | 3.4562
71 | 0.08894 | 0.02245 | -0.088785 | -0.022351 | 0.00015489 | 9.884e-05 | 0.13419 | 0.13419 | 0.13419 | 0.98667 | -0.25427 | 0.9848 | -0.2907 | 36.865
72 | 0.018071 | 0.0045334 | -0.018063 | -0.0045289 | 7.6448e-06 | 4.5403e-06 | 0.027215 | 0.027215 | 0.027215 | 0.9881 | -0.22683 | 0.98764 | -0.2357 | 7.4766
73 | 0.050988 | 0.012784 | -0.050973 | -0.012775 | 1.4546e-05 | 9.2293e-06 | 0.07779 | 0.07779 | 0.07779 | 0.97535 | -0.47265 | 0.97505 | -0.47864 | 21.3708
74 | -0.10531 | -0.026465 | 0.10711 | 0.02762 | 0.0018081 | 0.0011548 | 0.16068 | 0.16068 | 0.16068 | 0.97535 | -0.47265 | 0.99366 | -0.11959 | 44.1434
75 | 0.054318 | 0.01368 | -0.054245 | -0.013634 | 7.284e-05 | 4.6265e-05 | 0.082892 | 0.082892 | 0.082892 | 0.97535 | -0.47265 | 0.97392 | -0.50074 | 22.7727
76 | -0.10808 | -0.027862 | 0.10825 | 0.027966 | 0.00016328 | 0.00010428 | 0.16213 | 0.16213 | 0.16213 | 0.99366 | -0.11959 | 0.9953 | -0.088622 | 44.5417
77 | 0.00096876 | 0.00024256 | -0.00096875 | -0.00024279 | 1.4618e-08 | -2.3057e-07 | 0.0014507 | 0.0014507 | 0.0014507 | 0.99366 | -0.11959 | 0.99364 | -0.11991 | 0.39855
78 | 0.054245 | 0.013634 | -0.054198 | -0.013604 | 4.6965e-05 | 2.9831e-05 | 0.082892 | 0.082893 | 0.082893 | 0.97392 | -0.50074 | 0.973 | -0.51889 | 22.7727
79 | 0.010965 | 0.0027495 | -0.010964 | -0.0027493 | 3.9754e-07 | 2.077e-07 | 0.016778 | 0.016778 | 0.016778 | 0.97248 | -0.53073 | 0.97244 | -0.53149 | 4.6093
80 | -0.010965 | -0.0027495 | 0.010966 | 0.0027503 | 1.5275e-06 | 7.9806e-07 | 0.016778 | 0.016778 | 0.016778 | 0.97248 | -0.53073 | 0.97263 | -0.52781 | 4.6093
81 | 0.010964 | 0.0027493 | -0.010962 | -0.0027479 | 2.7247e-06 | 1.4237e-06 | 0.016778 | 0.016778 | 0.016778 | 0.97244 | -0.53149 | 0.97218 | -0.53671 | 4.6093
82 | -0.019104 | -0.0047899 | 0.019109 | 0.0047924 | 4.1822e-06 | 2.5145e-06 | 0.029228 | 0.029228 | 0.029228 | 0.97263 | -0.52781 | 0.97286 | -0.52321 | 8.0298
83 | 0.0013039 | 0.00032642 | -0.0013039 | -0.00032678 | 4.2903e-08 | -3.6561e-07 | 0.001947 | 0.0019472 | 0.0019472 | 0.99645 | -0.066869 | 0.99641 | -0.067559 | 0.53494
84 | -0.12608 | -0.032483 | 0.12611 | 0.032501 | 2.9602e-05 | 1.8483e-05 | 0.18859 | 0.18859 | 0.18859 | 0.99645 | -0.066869 | 0.9967 | -0.062046 | 12.9526
85 | 0.12477 | 0.032156 | -0.12474 | -0.032135 | 3.4057e-05 | 2.1253e-05 | 0.18664 | 0.18664 | 0.18664 | 0.99645 | -0.066869 | 0.99615 | -0.072476 | 12.8189
86 | 0.0030506 | 0.00076442 | -0.0030505 | -0.00076452 | 9.5e-08 | -9.8379e-08 | 0.0045542 | 0.0045543 | 0.0045543 | 0.9967 | -0.062046 | 0.99667 | -0.0627 | 1.2512
87 | -0.12916 | -0.033266 | 0.12931 | 0.033358 | 0.00014822 | 9.2651e-05 | 0.19314 | 0.19314 | 0.19314 | 0.9967 | -0.062046 | 0.99795 | -0.038493 | 13.2653
88 | 0.11611 | 0.029974 | -0.11602 | -0.029916 | 9.1321e-05 | 5.8026e-05 | 0.17376 | 0.17376 | 0.17376 | 0.99615 | -0.072476 | 0.9953 | -0.088622 | 23.8681
89 | 0.010962 | 0.0027479 | -0.010959 | -0.0027466 | 2.372e-06 | 1.2395e-06 | 0.016778 | 0.016778 | 0.016778 | 0.97218 | -0.53671 | 0.97195 | -0.54125 | 4.6094
90 | 0.0077781 | 0.0019493 | -0.0077777 | -0.0019492 | 4.254e-07 | 1.6324e-07 | 0.011629 | 0.011629 | 0.011629 | 0.9953 | -0.088622 | 0.99524 | -0.089771 | 3.1947
91 | -0.13304 | -0.034316 | 0.13307 | 0.034331 | 2.306e-05 | 1.4432e-05 | 0.19863 | 0.19863 | 0.19863 | 0.99841 | -0.029853 | 0.9986 | -0.026296 | 13.6423
92 | 0.13304 | 0.034316 | -0.13299 | -0.034281 | 5.5978e-05 | 3.5035e-05 | 0.19863 | 0.19863 | 0.19863 | 0.99841 | -0.029853 | 0.99795 | -0.038493 | 13.6423
93 | -0.13831 | -0.035644 | 0.13839 | 0.035699 | 8.8138e-05 | 5.5253e-05 | 0.20644 | 0.20644 | 0.20644 | 0.9986 | -0.026296 | 0.9993 | -0.013216 | 14.1786
94 | 0.0083488 | 0.0020928 | -0.0083479 | -0.0020924 | 9.2221e-07 | 4.0294e-07 | 0.012769 | 0.012769 | 0.012769 | 0.97292 | -0.52209 | 0.9728 | -0.52441 | 3.508
95 | 0.0070965 | 0.0017786 | -0.007096 | -0.0017784 | 5.3827e-07 | 1.932e-07 | 0.010854 | 0.010854 | 0.010854 | 0.97292 | -0.52209 | 0.97284 | -0.52368 | 2.9818
96 | 0.0083479 | 0.0020924 | -0.0083465 | -0.0020918 | 1.4161e-06 | 6.1882e-07 | 0.012769 | 0.012769 | 0.012769 | 0.9728 | -0.52441 | 0.97262 | -0.52797 | 3.5081
97 | -0.05878 | -0.014761 | 0.058794 | 0.014771 | 1.4651e-05 | 9.3162e-06 | 0.089792 | 0.089792 | 0.089792 | 0.9742 | -0.49671 | 0.97447 | -0.49149 | 24.6681
98 | 0.29479 | 0.075074 | -0.29468 | -0.075003 | 0.00011163 | 7.113e-05 | 0.44247 | 0.44247 | 0.44247 | 0.99233 | -0.14531 | 0.99192 | -0.15316 | 30.3895
99 | 0.0021526 | 0.00053934 | -0.0021525 | -0.00053947 | 4.9759e-08 | -1.3268e-07 | 0.0032278 | 0.0032278 | 0.0032278 | 0.99233 | -0.14531 | 0.9923 | -0.14579 | 0.88676
100 | -0.45365 | -0.11671 | 0.45442 | 0.11721 | 0.00077494 | 0.00049502 | 0.67737 | 0.67737 | 0.67737 | 0.99814 | -0.035068 | 1 | 0 | 46.5227
101 | -0.047917 | -0.012011 | 0.047968 | 0.012043 | 5.1007e-05 | 3.2331e-05 | 0.073365 | 0.073365 | 0.073365 | 0.97187 | -0.54121 | 0.973 | -0.51889 | 20.1553
102 | -0.29153 | -0.074113 | 0.29178 | 0.074276 | 0.00025599 | 0.0001631 | 0.43812 | 0.43812 | 0.43812 | 0.99097 | -0.17138 | 0.99192 | -0.15316 | 30.0908
103 | 0.01748 | 0.0043843 | -0.017475 | -0.0043816 | 4.6328e-06 | 2.7354e-06 | 0.026287 | 0.026288 | 0.026288 | 0.9895 | -0.19963 | 0.98922 | -0.20519 | 7.2219
104 | 0.12265 | 0.031261 | -0.12254 | -0.031188 | 0.00011447 | 7.2805e-05 | 0.18501 | 0.18502 | 0.18502 | 0.98746 | -0.23878 | 0.98645 | -0.25814 | 25.4142
105 | 0.018063 | 0.0045289 | -0.018058 | -0.0045257 | 5.3317e-06 | 3.1667e-06 | 0.027215 | 0.027215 | 0.027215 | 0.98764 | -0.2357 | 0.98732 | -0.2419 | 7.4766
106 | -0.010683 | -0.0026774 | 0.010684 | 0.0026777 | 4.8781e-07 | 2.5082e-07 | 0.016281 | 0.016281 | 0.016281 | 0.97639 | -0.45385 | 0.97644 | -0.4529 | 4.4728
107 | -0.022594 | -0.0056626 | 0.022603 | 0.0056681 | 8.8612e-06 | 5.4217e-06 | 0.034431 | 0.034431 | 0.034431 | 0.97644 | -0.4529 | 0.97685 | -0.44467 | 9.4591
108 | -0.022603 | -0.0056681 | 0.022618 | 0.0056777 | 1.575e-05 | 9.6359e-06 | 0.034431 | 0.034431 | 0.034431 | 0.97685 | -0.44467 | 0.9776 | -0.43006 | 9.4591
109 | -0.099848 | -0.025145 | 0.099894 | 0.025175 | 4.5722e-05 | 2.9196e-05 | 0.15202 | 0.15202 | 0.15202 | 0.9776 | -0.43006 | 0.97809 | -0.42048 | 41.7649
110 | 0.070238 | 0.017716 | -0.070099 | -0.017627 | 0.00013879 | 8.8422e-05 | 0.10695 | 0.10695 | 0.10695 | 0.9776 | -0.43006 | 0.97549 | -0.47142 | 29.3822
111 | 0.0069918 | 0.0017522 | -0.006991 | -0.0017519 | 7.6343e-07 | 2.6325e-07 | 0.010642 | 0.010642 | 0.010642 | 0.9776 | -0.43006 | 0.97748 | -0.43235 | 2.9237
112 | 0.0056492 | 0.0014157 | -0.0056483 | -0.0014156 | 8.4971e-07 | 1.3115e-07 | 0.0084463 | 0.0084464 | 0.0084464 | 0.99524 | -0.089771 | 0.99507 | -0.092928 | 2.3204
113 | -0.14346 | -0.036969 | 0.14355 | 0.037027 | 9.2368e-05 | 5.7987e-05 | 0.21398 | 0.21398 | 0.21398 | 0.9993 | -0.013216 | 1 | 0 | 14.6967
114 | -0.0038179 | -0.00095685 | 0.0038181 | 0.00095675 | 2.7815e-07 | -9.7177e-08 | 0.0058124 | 0.0058123 | 0.0058124 | 0.9774 | -0.43388 | 0.97748 | -0.43235 | 1.5968
115 | -0.062703 | -0.01575 | 0.062763 | 0.015788 | 6.0101e-05 | 3.8247e-05 | 0.09576 | 0.09576 | 0.09576 | 0.97447 | -0.49149 | 0.97549 | -0.47142 | 26.3076
116 | -0.0084662 | -0.0021218 | 0.0084666 | 0.002122 | 3.4668e-07 | 1.4927e-07 | 0.01276 | 0.01276 | 0.01276 | 0.98728 | -0.24276 | 0.98732 | -0.2419 | 3.5056
117 | 0.0028996 | 0.00072661 | -0.0028995 | -0.00072668 | 5.957e-08 | -7.0249e-08 | 0.0043497 | 0.0043497 | 0.0043497 | 0.99192 | -0.15316 | 0.9919 | -0.15359 | 1.195
118 | 0.11839 | 0.030149 | -0.11814 | -0.029987 | 0.00025351 | 0.00016198 | 0.17876 | 0.17876 | 0.17876 | 0.98645 | -0.25814 | 0.98414 | -0.30264 | 49.1097
119 | 0.11353 | 0.028833 | -0.11331 | -0.028689 | 0.00022475 | 0.00014359 | 0.1718 | 0.1718 | 0.1718 | 0.98414 | -0.30264 | 0.98202 | -0.34386 | 47.1966
120 | 0.10914 | 0.027645 | -0.10891 | -0.027494 | 0.00023716 | 0.00015149 | 0.16549 | 0.16549 | 0.16549 | 0.98202 | -0.34386 | 0.97969 | -0.38921 | 45.4631
121 | 0.10443 | 0.026373 | -0.10428 | -0.026273 | 0.00015624 | 9.9783e-05 | 0.15869 | 0.15869 | 0.15869 | 0.97969 | -0.38921 | 0.97809 | -0.42048 | 43.5961
122 | 0.0073366 | 0.0018389 | -0.0073355 | -0.0018385 | 1.0703e-06 | 4.0056e-07 | 0.011191 | 0.011191 | 0.011191 | 0.97549 | -0.47142 | 0.97533 | -0.47449 | 3.0746
123 | 0.0073355 | 0.0018385 | -0.0073355 | -0.0018384 | 6.6789e-08 | 2.4999e-08 | 0.011191 | 0.011191 | 0.011191 | 0.97533 | -0.47449 | 0.97532 | -0.47468 | 3.0746
124 | 0.0035195 | 0.00088206 | -0.0035195 | -0.00088206 | 7.375e-09 | -4.5035e-09 | 0.005263 | 0.005263 | 0.005263 | 0.99507 | -0.092928 | 0.99507 | -0.092972 | 1.4459

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.60402 | 0.15534

## res_load
| p_mw | q_mvar
0 | 0.0032316 | 0.00080991
1 | 0.001989 | 0.00049848
2 | 0.0021721 | 0.00054439
3 | 0.0030322 | 0.00075993
4 | 0.0024826 | 0.00062219
5 | 0.00426 | 0.0010677
6 | 0.061109 | 0.015315
7 | 0.0058793 | 0.0014735
8 | 0.0036921 | 0.00092532
9 | 0.0018953 | 0.000475
10 | 0.0024335 | 0.00060989
11 | 0.0030637 | 0.00076784
12 | 0.0025056 | 0.00062796
13 | 0.0061285 | 0.001536
14 | 0.0041386 | 0.0010372
15 | 0.0024862 | 0.00062309
16 | 0.0084828 | 0.002126
17 | 0.008986 | 0.0022521
18 | 0.0068302 | 0.0017118
19 | 0.0068026 | 0.0017049
20 | 0.0046851 | 0.0011742
21 | 0.0078979 | 0.0019794
22 | 0.0088314 | 0.0022134
23 | 0.0093697 | 0.0023483
24 | 0.010484 | 0.0026276
25 | 0.0072436 | 0.0018154
26 | 0.0068903 | 0.0017269
27 | 0.0082156 | 0.002059
28 | 0.0091471 | 0.0022925
29 | 0.050973 | 0.012775
30 | 0.0081383 | 0.0020396
31 | 0.0013039 | 0.00032678
32 | 0.0086244 | 0.0021615
33 | 0.010959 | 0.0027466
34 | 0.00096875 | 0.00024279
35 | 0.0052401 | 0.0013133
36 | 0.0036821 | 0.00092282
37 | 0.007096 | 0.0017784
38 | 0.011863 | 0.0029732
39 | 0.0083465 | 0.0020918
40 | 0.05369 | 0.013456
41 | 0.0030637 | 0.00076784
42 | 0.035134 | 0.0088053
43 | 0.0034346 | 0.0008608
44 | 0.0082352 | 0.0020639
45 | 0.0035812 | 0.00089754
46 | 0.0076002 | 0.0019048
47 | 0.0071853 | 0.0018008
48 | 0.0078307 | 0.0019625
49 | 0.009153 | 0.002294
50 | 0.0083415 | 0.0020906
51 | 0.0062299 | 0.0015614
52 | 0.0030505 | 0.00076452
53 | 0.010683 | 0.0026774
54 | 0.01191 | 0.0029849
55 | 0.0021285 | 0.00053345
56 | 0.0050666 | 0.0012698
57 | 0.0038179 | 0.00095685
58 | 0.0031729 | 0.00079519
59 | 0.0039083 | 0.0009795
60 | 0.0084662 | 0.0021218
61 | 0.0095909 | 0.0024037
62 | 0.0043892 | 0.0011
63 | 0.0021525 | 0.00053947
64 | 0.0028995 | 0.00072668
65 | 0.0041472 | 0.0010394
66 | 0.0046058 | 0.0011543
67 | 0.0041644 | 0.0010437
68 | 0.0044744 | 0.0011214
69 | 0.0043814 | 0.0010981
70 | 0.0021289 | 0.00053354
71 | 0.0035195 | 0.00088206
72 | 0.0073355 | 0.0018384

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1