## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-534_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-534_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-534_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_261-534_0_4_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_261-534_0_4_node_7 | 0.4 | n |  | TRUE
5 | bus_LV_261-534_0_4_node_19 | 0.4 | n |  | TRUE
6 | bus_LV_261-534_0_4_node_3 | 0.4 | n |  | TRUE
7 | bus_LV_261-534_0_4_node_34 | 0.4 | n |  | TRUE
8 | bus_LV_261-534_0_4_node_16 | 0.4 | n |  | TRUE
9 | bus_LV_261-534_0_4_node_20 | 0.4 | n |  | TRUE
10 | bus_LV_261-534_0_4_node_5 | 0.4 | n |  | TRUE
11 | bus_LV_261-534_0_4_node_12 | 0.4 | n |  | TRUE
12 | bus_LV_261-534_0_4_node_9 | 0.4 | n |  | TRUE
13 | bus_LV_261-534_0_4_node_27 | 0.4 | n |  | TRUE
14 | bus_LV_261-534_0_4_node_6 | 0.4 | n |  | TRUE
15 | bus_LV_261-534_0_4_node_11 | 0.4 | n |  | TRUE
16 | bus_LV_261-534_0_4_node_15 | 0.4 | n |  | TRUE
17 | bus_LV_261-534_0_4_node_30 | 0.4 | n |  | TRUE
18 | bus_LV_261-534_0_4_node_31 | 0.4 | n |  | TRUE
19 | bus_LV_261-534_0_4_node_28 | 0.4 | n |  | TRUE
20 | bus_LV_261-534_0_4_node_32 | 0.4 | n |  | TRUE
21 | bus_LV_261-534_0_4_node_13 | 0.4 | n |  | TRUE
22 | bus_LV_261-534_0_4_node_23 | 0.4 | n |  | TRUE
23 | bus_LV_261-534_0_4_node_14 | 0.4 | n |  | TRUE
24 | bus_LV_261-534_0_4_node_33 | 0.4 | n |  | TRUE
25 | bus_LV_261-534_0_4_node_26 | 0.4 | n |  | TRUE
26 | bus_LV_261-534_0_4_node_17 | 0.4 | n |  | TRUE
27 | bus_LV_261-534_0_4_node_18 | 0.4 | n |  | TRUE
28 | bus_LV_261-534_0_4_node_25 | 0.4 | n |  | TRUE
29 | bus_LV_261-534_0_4_node_29 | 0.4 | n |  | TRUE
30 | bus_LV_261-534_0_4_node_24 | 0.4 | n |  | TRUE
31 | bus_LV_261-534_0_4_node_22 | 0.4 | n |  | TRUE
32 | bus_MV_524_0_node_69 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-534_0_4_load_0 | 0 | 0.070166 | 0.017585 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-534_0_4_load_19 | 5 | 0.0044473 | 0.0011146 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-534_0_4_load_34 | 7 | 0.0075268 | 0.0018864 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-534_0_4_load_20 | 9 | 0.018887 | 0.0047336 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-534_0_4_load_27 | 13 | 0.011682 | 0.0029278 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-534_0_4_load_30 | 17 | 0.034639 | 0.0086813 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-534_0_4_load_31 | 18 | 0.059083 | 0.014808 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-534_0_4_load_28 | 19 | 0.092535 | 0.023192 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-534_0_4_load_32 | 20 | 0.02368 | 0.0059349 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-534_0_4_load_23 | 22 | 0.01465 | 0.0036717 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-534_0_4_load_33 | 24 | 0.018982 | 0.0047573 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-534_0_4_load_26 | 25 | 0.0053572 | 0.0013427 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-534_0_4_load_25 | 28 | 0.0074381 | 0.0018642 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-534_0_4_load_29 | 29 | 0.03353 | 0.0084034 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-534_0_4_load_24 | 30 | 0.02708 | 0.0067868 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-534_0_4_load_22 | 31 | 0.0060815 | 0.0015242 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 19 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-534_0_4_line_0 |  | 0 | 1 | 0.016378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-534_0_4_line_1 |  | 0 | 2 | 0.0026201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-534_0_4_line_2 |  | 1 | 3 | 0.015695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-534_0_4_line_3 |  | 1 | 4 | 0.011402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-534_0_4_line_4 |  | 2 | 5 | 0.016963 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_261-534_0_4_line_5 |  | 3 | 9 | 0.034764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_261-534_0_4_line_6 |  | 4 | 17 | 0.014931 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_261-534_0_4_line_7 |  | 5 | 27 | 0.029499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_261-534_0_4_line_8 |  | 6 | 7 | 0.017435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_261-534_0_4_line_9 |  | 6 | 8 | 0.051898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_261-534_0_4_line_10 |  | 8 | 9 | 0.033628 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_261-534_0_4_line_11 |  | 10 | 11 | 0.007878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_261-534_0_4_line_12 |  | 10 | 12 | 0.01243 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-534_0_4_line_13 |  | 10 | 13 | 0.027707 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_261-534_0_4_line_14 |  | 11 | 20 | 0.012666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_261-534_0_4_line_15 |  | 12 | 18 | 0.014998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_261-534_0_4_line_16 |  | 13 | 25 | 0.00022675 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_261-534_0_4_line_17 |  | 14 | 15 | 0.007082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
18 | LV_261-534_0_4_line_18 |  | 14 | 16 | 0.0077183 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
19 | LV_261-534_0_4_line_19 |  | 15 | 19 | 0.015597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
20 | LV_261-534_0_4_line_20 |  | 16 | 25 | 0.027367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_261-534_0_4_line_21 |  | 16 | 21 | 0.007275 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_261-534_0_4_line_22 |  | 17 | 29 | 0.020682 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
23 | LV_261-534_0_4_line_23 |  | 19 | 29 | 0.034167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
24 | LV_261-534_0_4_line_24 |  | 20 | 23 | 0.037525 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_261-534_0_4_line_25 |  | 21 | 22 | 0.012721 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_261-534_0_4_line_26 |  | 22 | 31 | 0.023525 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_261-534_0_4_line_27 |  | 23 | 24 | 0.025085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_261-534_0_4_line_28 |  | 26 | 27 | 0.023653 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_261-534_0_4_line_29 |  | 26 | 28 | 0.037366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_261-534_0_4_line_30 |  | 30 | 31 | 0.033561 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-534_0_4_trafo_28 | 0.63 MVA 20/0.4 kV | 32 | 19 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2683441.9237 | 1252201.3166 | 2683453.541 | 1252206.5508 | 2683457.0176 | 1252207.6144
1 | 2683459.5231 | 1252208.3809 | 2683457.0176 | 1252207.6144
2 | 2683429.7172 | 1252195.0401 | 2683434.3398 | 1252195.3276 | 2683438.7436 | 1252195.612 | 2683439.2657 | 1252197.6542 | 2683440.5124 | 1252199.7067 | 2683441.9237 | 1252201.3166
3 | 2683441.9237 | 1252201.3166 | 2683441.7551 | 1252202.037 | 2683440.9506 | 1252205.5617 | 2683440.1226 | 1252209.1527 | 2683439.8089 | 1252210.5271 | 2683438.4086 | 1252211.8862
4 | 2683459.5231 | 1252208.3809 | 2683471.0709 | 1252213.1916 | 2683475.1268 | 1252215.0311
5 | 2683429.7172 | 1252195.0401 | 2683429.9008 | 1252191.6512 | 2683431.7484 | 1252160.3357
6 | 2683438.4086 | 1252211.8862 | 2683437.4923 | 1252214.2417 | 2683436.7717 | 1252226.6246
7 | 2683501.9915 | 1252227.2155 | 2683475.1268 | 1252215.0311
8 | 2683466.0243 | 1252161.5929 | 2683473.3197 | 1252145.7504
9 | 2683431.4209 | 1252127.1576 | 2683438.3869 | 1252127.189 | 2683445.505 | 1252129.8134 | 2683475.5318 | 1252140.8891 | 2683473.3197 | 1252145.7504
10 | 2683431.4209 | 1252127.1576 | 2683431.1972 | 1252131.2464 | 2683432.4673 | 1252133.7773 | 2683433.173 | 1252136.189 | 2683431.7484 | 1252160.3357
11 | 2683492.0849 | 1252312.6289 | 2683492.2659 | 1252315.3113 | 2683493.0691 | 1252320.4375
12 | 2683487.5444 | 1252303.8472 | 2683491.4423 | 1252304.1357 | 2683491.6898 | 1252309.0651 | 2683492.0849 | 1252312.6289
13 | 2683492.0849 | 1252312.6289 | 2683471.5783 | 1252311.5837 | 2683464.4134 | 1252311.2188
14 | 2683493.0691 | 1252320.4375 | 2683495.3471 | 1252330.1658 | 2683496.1255 | 1252332.7251
15 | 2683487.5444 | 1252303.8472 | 2683472.5552 | 1252303.3301
16 | 2683464.4134 | 1252311.2188 | 2683464.1869 | 1252311.2073
17 | 2683437.4164 | 1252302.1177 | 2683436.2763 | 1252301.6124 | 2683435.1106 | 1252300.7842 | 2683433.756 | 1252298.8971 | 2683432.9909 | 1252296.9515
18 | 2683436.8551 | 1252309.8156 | 2683437.0805 | 1252306.6719 | 2683437.4164 | 1252302.1177
19 | 2683432.9909 | 1252296.9515 | 2683432.8317 | 1252294.3251 | 2683433.585 | 1252281.3809
20 | 2683436.8551 | 1252309.8156 | 2683464.1869 | 1252311.2073
21 | 2683436.8551 | 1252309.8156 | 2683434.3771 | 1252311.0594 | 2683432.826 | 1252312.4052 | 2683432.0627 | 1252313.5509 | 2683431.8063 | 1252314.6036
22 | 2683436.7717 | 1252226.6246 | 2683435.5701 | 1252247.2712
23 | 2683433.585 | 1252281.3809 | 2683435.5701 | 1252247.2712
24 | 2683508.4722 | 1252368.1459 | 2683504.2533 | 1252355.8328 | 2683498.7877 | 1252341.4783 | 2683496.1255 | 1252332.7251
25 | 2683431.8063 | 1252314.6036 | 2683431.6009 | 1252315.2568 | 2683430.964 | 1252327.2767
26 | 2683429.6622 | 1252350.7655 | 2683430.0746 | 1252343.2341 | 2683430.2232 | 1252341.2569 | 2683430.964 | 1252327.2767
27 | 2683484.0864 | 1252368.1801 | 2683490.5454 | 1252370.4284 | 2683492.8684 | 1252370.539 | 2683497.0763 | 1252370.7873 | 2683501.1332 | 1252370.4998 | 2683508.4722 | 1252368.1459
28 | 2683514.1366 | 1252210.0071 | 2683511.9295 | 1252209.698 | 2683508.5294 | 1252210.4951 | 2683501.9915 | 1252227.2155
29 | 2683514.1366 | 1252210.0071 | 2683516.8779 | 1252203.4741 | 2683522.7834 | 1252183.9761 | 2683524.777 | 1252174.2707
30 | 2683429.6622 | 1252350.7655 | 2683429.1905 | 1252359.3782 | 2683429.0225 | 1252362.7339 | 2683427.9648 | 1252384.2836

## bus_geodata
| x | y | coords
0 | 2683457.0176 | 1252207.6144
1 | 2683441.9237 | 1252201.3166
2 | 2683459.5231 | 1252208.3809
3 | 2683429.7172 | 1252195.0401
4 | 2683438.4086 | 1252211.8862
5 | 2683475.1268 | 1252215.0311
6 | 2683473.3197 | 1252145.7504
7 | 2683466.0243 | 1252161.5929
8 | 2683431.4209 | 1252127.1576
9 | 2683431.7484 | 1252160.3357
10 | 2683492.0849 | 1252312.6289
11 | 2683493.0691 | 1252320.4375
12 | 2683487.5444 | 1252303.8472
13 | 2683464.4134 | 1252311.2188
14 | 2683437.4164 | 1252302.1177
15 | 2683432.9909 | 1252296.9515
16 | 2683436.8551 | 1252309.8156
17 | 2683436.7717 | 1252226.6246
18 | 2683472.5552 | 1252303.3301
19 | 2683433.585 | 1252281.3809
20 | 2683496.1255 | 1252332.7251
21 | 2683431.8063 | 1252314.6036
22 | 2683430.964 | 1252327.2767
23 | 2683508.4722 | 1252368.1459
24 | 2683484.0864 | 1252368.1801
25 | 2683464.1869 | 1252311.2073
26 | 2683514.1366 | 1252210.0071
27 | 2683501.9915 | 1252227.2155
28 | 2683524.777 | 1252174.2707
29 | 2683435.5701 | 1252247.2712
30 | 2683427.9648 | 1252384.2836
31 | 2683429.6622 | 1252350.7655
32 | 2683432.9909 | 1252296.9515

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99205 | -0.15282 | 0.070166 | 0.017585
1 | 0.99328 | -0.12905 | 0 | 0
2 | 0.99203 | -0.15337 | 0 | 0
3 | 0.9929 | -0.13637 | 0 | 0
4 | 0.99441 | -0.10722 | 0 | 0
5 | 0.99184 | -0.15694 | 0.0044473 | 0.0011146
6 | 0.99148 | -0.16403 | 0 | 0
7 | 0.99136 | -0.16636 | 0.0075268 | 0.0018864
8 | 0.99183 | -0.15711 | 0 | 0
9 | 0.99206 | -0.15262 | 0.018887 | 0.0047336
10 | 0.99211 | -0.15158 | 0 | 0
11 | 0.9918 | -0.15753 | 0 | 0
12 | 0.99144 | -0.16459 | 0 | 0
13 | 0.99469 | -0.10179 | 0.011682 | 0.0029278
14 | 0.99827 | -0.032985 | 0 | 0
15 | 0.99881 | -0.022673 | 0 | 0
16 | 0.99769 | -0.044237 | 0 | 0
17 | 0.99589 | -0.078715 | 0.034639 | 0.0086813
18 | 0.99062 | -0.18032 | 0.059083 | 0.014808
19 | 1 | 0 | -0.34704 | -0.087396
20 | 0.99131 | -0.16711 | 0.02368 | 0.0059349
21 | 0.99737 | -0.05033 | 0 | 0
22 | 0.99682 | -0.060993 | 0.01465 | 0.0036717
23 | 0.99065 | -0.17976 | 0 | 0
24 | 0.99022 | -0.18822 | 0.018982 | 0.0047573
25 | 0.99471 | -0.10133 | 0.0053572 | 0.0013427
26 | 0.99148 | -0.16395 | 0 | 0
27 | 0.99164 | -0.16083 | 0 | 0
28 | 0.99123 | -0.16888 | 0.0074381 | 0.0018642
29 | 0.99725 | -0.052743 | 0.03353 | 0.0084034
30 | 0.99528 | -0.090666 | 0.02708 | 0.0067868
31 | 0.9961 | -0.074688 | 0.0060815 | 0.0015242
32 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.082058 | -0.020567 | 0.082151 | 0.020626 | 9.304e-05 | 5.9334e-05 | 0.12308 | 0.12308 | 0.12308 | 0.99205 | -0.15282 | 0.99328 | -0.12905 | 33.8136
1 | 0.011892 | 0.0029815 | -0.011892 | -0.0029814 | 3.1262e-07 | 1.6625e-07 | 0.017838 | 0.017838 | 0.017838 | 0.99205 | -0.15282 | 0.99203 | -0.15337 | 4.9004
2 | 0.026449 | 0.0066402 | -0.02644 | -0.0066345 | 9.2419e-06 | 5.7117e-06 | 0.039627 | 0.039627 | 0.039627 | 0.99328 | -0.12905 | 0.9929 | -0.13637 | 10.8864
3 | -0.1086 | -0.027266 | 0.10871 | 0.027339 | 0.00011319 | 7.2295e-05 | 0.16271 | 0.16271 | 0.16271 | 0.99328 | -0.12905 | 0.99441 | -0.10722 | 44.7
4 | 0.011892 | 0.0029814 | -0.01189 | -0.0029803 | 2.024e-06 | 1.0764e-06 | 0.017838 | 0.017838 | 0.017838 | 0.99203 | -0.15337 | 0.99184 | -0.15694 | 4.9005
5 | 0.02644 | 0.0066345 | -0.026419 | -0.0066219 | 2.0471e-05 | 1.2652e-05 | 0.039627 | 0.039627 | 0.039627 | 0.9929 | -0.13637 | 0.99206 | -0.15262 | 10.8865
6 | -0.10871 | -0.027339 | 0.10886 | 0.027433 | 0.00014823 | 9.4676e-05 | 0.16271 | 0.16271 | 0.16271 | 0.99441 | -0.10722 | 0.99589 | -0.078715 | 44.7
7 | 0.0074423 | 0.0018657 | -0.0074409 | -0.0018652 | 1.3791e-06 | 5.0199e-07 | 0.011166 | 0.011166 | 0.011166 | 0.99184 | -0.15694 | 0.99164 | -0.16083 | 3.0675
8 | 0.0075277 | 0.0018867 | -0.0075268 | -0.0018864 | 8.3451e-07 | 3.0926e-07 | 0.011298 | 0.011298 | 0.011298 | 0.99148 | -0.16403 | 0.99136 | -0.16636 | 3.1038
9 | -0.0075277 | -0.0018867 | 0.0075302 | 0.0018876 | 2.484e-06 | 9.202e-07 | 0.011298 | 0.011297 | 0.011298 | 0.99148 | -0.16403 | 0.99183 | -0.15711 | 3.1037
10 | -0.0075302 | -0.0018876 | 0.0075318 | 0.0018882 | 1.6095e-06 | 5.9596e-07 | 0.011297 | 0.011297 | 0.011297 | 0.99183 | -0.15711 | 0.99206 | -0.15262 | 3.1037
11 | 0.042713 | 0.010724 | -0.042701 | -0.010716 | 1.2127e-05 | 7.6597e-06 | 0.06407 | 0.06407 | 0.06407 | 0.99211 | -0.15158 | 0.9918 | -0.15753 | 17.6017
12 | 0.059164 | 0.014859 | -0.059127 | -0.014836 | 3.6713e-05 | 2.3336e-05 | 0.088749 | 0.088749 | 0.088749 | 0.99211 | -0.15158 | 0.99144 | -0.16459 | 24.3815
13 | -0.10188 | -0.025583 | 0.10212 | 0.025738 | 0.00024265 | 0.00015494 | 0.15282 | 0.15282 | 0.15282 | 0.99211 | -0.15158 | 0.99469 | -0.10179 | 41.9831
14 | 0.042701 | 0.010716 | -0.042681 | -0.010704 | 1.9498e-05 | 1.2316e-05 | 0.06407 | 0.06407 | 0.06407 | 0.9918 | -0.15753 | 0.99131 | -0.16711 | 17.6017
15 | 0.059127 | 0.014836 | -0.059083 | -0.014808 | 4.4299e-05 | 2.8158e-05 | 0.088749 | 0.088749 | 0.088749 | 0.99144 | -0.16459 | 0.99062 | -0.18032 | 24.3815
16 | -0.1138 | -0.028665 | 0.1138 | 0.028667 | 2.4659e-06 | 1.5753e-06 | 0.17029 | 0.17029 | 0.17029 | 0.99469 | -0.10179 | 0.99471 | -0.10133 | 46.7842
17 | -0.16747 | -0.042309 | 0.16755 | 0.042362 | 8.2825e-05 | 5.2823e-05 | 0.24975 | 0.24975 | 0.24975 | 0.99827 | -0.032985 | 0.99881 | -0.022673 | 34.3061
18 | 0.16747 | 0.042309 | -0.16738 | -0.042251 | 9.0267e-05 | 5.7569e-05 | 0.24975 | 0.24975 | 0.24975 | 0.99827 | -0.032985 | 0.99769 | -0.044237 | 34.3061
19 | -0.16755 | -0.042362 | 0.16774 | 0.042478 | 0.00018241 | 0.00011634 | 0.24975 | 0.24975 | 0.24975 | 0.99881 | -0.022673 | 1 | 0 | 34.3061
20 | 0.11949 | 0.030218 | -0.11916 | -0.03001 | 0.00032629 | 0.00020847 | 0.17831 | 0.17831 | 0.17831 | 0.99769 | -0.044237 | 0.99471 | -0.10133 | 48.9858
21 | 0.047892 | 0.012033 | -0.047878 | -0.012024 | 1.3923e-05 | 8.8161e-06 | 0.07144 | 0.07144 | 0.07144 | 0.99769 | -0.044237 | 0.99737 | -0.05033 | 19.6264
22 | -0.1435 | -0.036115 | 0.14368 | 0.036228 | 0.00017836 | 0.00011361 | 0.21446 | 0.21446 | 0.21446 | 0.99589 | -0.078715 | 0.99725 | -0.052743 | 29.4593
23 | 0.17766 | 0.044917 | -0.17721 | -0.044632 | 0.00044817 | 0.00028594 | 0.26449 | 0.26449 | 0.26449 | 1 | 0 | 0.99725 | -0.052743 | 36.3316
24 | 0.019001 | 0.0047688 | -0.01899 | -0.0047619 | 1.1449e-05 | 6.8441e-06 | 0.028524 | 0.028524 | 0.028524 | 0.99131 | -0.16711 | 0.99065 | -0.17976 | 7.8364
25 | 0.047878 | 0.012024 | -0.047854 | -0.012009 | 2.4347e-05 | 1.5416e-05 | 0.07144 | 0.07144 | 0.07144 | 0.99737 | -0.05033 | 0.99682 | -0.060993 | 19.6264
26 | 0.033204 | 0.0083373 | -0.033182 | -0.0083238 | 2.1678e-05 | 1.3567e-05 | 0.049571 | 0.049571 | 0.049571 | 0.99682 | -0.060993 | 0.9961 | -0.074688 | 13.6184
27 | 0.01899 | 0.0047619 | -0.018982 | -0.0047573 | 7.6539e-06 | 4.5757e-06 | 0.028524 | 0.028525 | 0.028525 | 0.99065 | -0.17976 | 0.99022 | -0.18822 | 7.8364
28 | -0.0074398 | -0.0018648 | 0.0074409 | 0.0018652 | 1.1058e-06 | 4.0264e-07 | 0.011166 | 0.011166 | 0.011166 | 0.99148 | -0.16395 | 0.99164 | -0.16083 | 3.0675
29 | 0.0074398 | 0.0018648 | -0.0074381 | -0.0018642 | 1.747e-06 | 6.363e-07 | 0.011166 | 0.011166 | 0.011166 | 0.99148 | -0.16395 | 0.99123 | -0.16888 | 3.0676
30 | -0.02708 | -0.0067868 | 0.0271 | 0.0067996 | 2.0629e-05 | 1.2766e-05 | 0.040486 | 0.040486 | 0.040486 | 0.99528 | -0.090666 | 0.9961 | -0.074688 | 11.1226

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.43958 | 0.11059

## res_load
| p_mw | q_mvar
0 | 0.070166 | 0.017585
1 | 0.0044473 | 0.0011146
2 | 0.0075268 | 0.0018864
3 | 0.018887 | 0.0047336
4 | 0.011682 | 0.0029278
5 | 0.034639 | 0.0086813
6 | 0.059083 | 0.014808
7 | 0.092535 | 0.023192
8 | 0.02368 | 0.0059349
9 | 0.01465 | 0.0036717
10 | 0.018982 | 0.0047573
11 | 0.0053572 | 0.0013427
12 | 0.0074381 | 0.0018642
13 | 0.03353 | 0.0084034
14 | 0.02708 | 0.0067868
15 | 0.0060815 | 0.0015242

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1