## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-543_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-543_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-543_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_261-543_0_3_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_261-543_0_3_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_261-543_0_3_node_6 | 0.4 | n |  | TRUE
6 | bus_LV_261-543_0_3_node_33 | 0.4 | n |  | TRUE
7 | bus_LV_261-543_0_3_node_7 | 0.4 | n |  | TRUE
8 | bus_LV_261-543_0_3_node_19 | 0.4 | n |  | TRUE
9 | bus_LV_261-543_0_3_node_34 | 0.4 | n |  | TRUE
10 | bus_LV_261-543_0_3_node_9 | 0.4 | n |  | TRUE
11 | bus_LV_261-543_0_3_node_26 | 0.4 | n |  | TRUE
12 | bus_LV_261-543_0_3_node_31 | 0.4 | n |  | TRUE
13 | bus_LV_261-543_0_3_node_10 | 0.4 | n |  | TRUE
14 | bus_LV_261-543_0_3_node_20 | 0.4 | n |  | TRUE
15 | bus_LV_261-543_0_3_node_18 | 0.4 | n |  | TRUE
16 | bus_LV_261-543_0_3_node_11 | 0.4 | n |  | TRUE
17 | bus_LV_261-543_0_3_node_15 | 0.4 | n |  | TRUE
18 | bus_LV_261-543_0_3_node_30 | 0.4 | n |  | TRUE
19 | bus_LV_261-543_0_3_node_12 | 0.4 | n |  | TRUE
20 | bus_LV_261-543_0_3_node_29 | 0.4 | n |  | TRUE
21 | bus_LV_261-543_0_3_node_27 | 0.4 | n |  | TRUE
22 | bus_LV_261-543_0_3_node_14 | 0.4 | n |  | TRUE
23 | bus_LV_261-543_0_3_node_35 | 0.4 | n |  | TRUE
24 | bus_LV_261-543_0_3_node_16 | 0.4 | n |  | TRUE
25 | bus_LV_261-543_0_3_node_28 | 0.4 | n |  | TRUE
26 | bus_LV_261-543_0_3_node_24 | 0.4 | n |  | TRUE
27 | bus_LV_261-543_0_3_node_25 | 0.4 | n |  | TRUE
28 | bus_LV_261-543_0_3_node_23 | 0.4 | n |  | TRUE
29 | bus_LV_261-543_0_3_node_32 | 0.4 | n |  | TRUE
30 | bus_LV_261-543_0_3_node_21 | 0.4 | n |  | TRUE
31 | bus_LV_261-543_0_3_node_22 | 0.4 | n |  | TRUE
32 | bus_MV_469_0_node_151 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-543_0_3_load_0 | 0 | 0.0067929 | 0.0017025 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-543_0_3_load_1 | 1 | 0.0068144 | 0.0017079 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-543_0_3_load_2 | 2 | 0.0081424 | 0.0020407 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-543_0_3_load_4 | 3 | 0.0088468 | 0.0022172 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-543_0_3_load_33 | 6 | 0.030625 | 0.0076755 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-543_0_3_load_34 | 9 | 0.03155 | 0.0079071 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-543_0_3_load_26 | 11 | 0.0051461 | 0.0012897 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-543_0_3_load_20 | 14 | 0.032302 | 0.0080956 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-543_0_3_load_18 | 15 | 0.042269 | 0.010594 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-543_0_3_load_30 | 18 | 0.016882 | 0.0042311 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-543_0_3_load_29 | 20 | 0.0065903 | 0.0016517 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-543_0_3_load_27 | 21 | 0.019684 | 0.0049332 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-543_0_3_load_35 | 23 | 0.0023455 | 0.00058784 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-543_0_3_load_24 | 26 | 0.019462 | 0.0048776 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-543_0_3_load_32 | 29 | 0.0045089 | 0.00113 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-543_0_3_load_21 | 30 | 0.011038 | 0.0027664 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-543_0_3_load_22 | 31 | 0.023798 | 0.0059643 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 13 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-543_0_3_line_0 |  | 0 | 1 | 0.01588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-543_0_3_line_1 |  | 0 | 2 | 0.017783 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-543_0_3_line_2 |  | 2 | 3 | 0.012171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-543_0_3_line_3 |  | 3 | 4 | 0.0096091 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-543_0_3_line_4 |  | 4 | 5 | 0.033929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_261-543_0_3_line_5 |  | 4 | 22 | 0.036791 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_261-543_0_3_line_6 |  | 5 | 6 | 0.035102 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_261-543_0_3_line_7 |  | 6 | 9 | 0.028568 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_261-543_0_3_line_8 |  | 7 | 8 | 0.054994 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_261-543_0_3_line_9 |  | 7 | 9 | 0.034615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_261-543_0_3_line_10 |  | 8 | 15 | 0.019021 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_261-543_0_3_line_11 |  | 10 | 11 | 0.03737 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_261-543_0_3_line_12 |  | 10 | 12 | 0.015376 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-543_0_3_line_13 |  | 11 | 27 | 0.023538 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_261-543_0_3_line_14 |  | 12 | 29 | 0.036856 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_261-543_0_3_line_15 |  | 12 | 14 | 0.033469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_261-543_0_3_line_16 |  | 13 | 14 | 0.042302 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_261-543_0_3_line_17 |  | 13 | 15 | 0.036677 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
18 | LV_261-543_0_3_line_18 |  | 16 | 17 | 0.025264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_261-543_0_3_line_19 |  | 16 | 18 | 0.030935 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_261-543_0_3_line_20 |  | 17 | 23 | 0.0095391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_261-543_0_3_line_21 |  | 18 | 24 | 0.015344 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_261-543_0_3_line_22 |  | 19 | 20 | 0.01849 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_261-543_0_3_line_23 |  | 19 | 21 | 0.015387 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_261-543_0_3_line_24 |  | 20 | 22 | 0.012663 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_261-543_0_3_line_25 |  | 21 | 25 | 0.030019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_261-543_0_3_line_26 |  | 24 | 25 | 0.008305 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_261-543_0_3_line_27 |  | 26 | 27 | 0.041863 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_261-543_0_3_line_28 |  | 27 | 28 | 0.048779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_261-543_0_3_line_29 |  | 28 | 31 | 0.01406 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_261-543_0_3_line_30 |  | 30 | 31 | 0.091582 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-543_0_3_trafo_10 | 0.63 MVA 20/0.4 kV | 32 | 13 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2684040.5853 | 1253209.2797 | 2684031.7481 | 1253196.0855
1 | 2684040.5853 | 1253209.2797 | 2684050.4815 | 1253224.0548
2 | 2684057.2544 | 1253234.1668 | 2684050.4815 | 1253224.0548
3 | 2684062.6018 | 1253242.1505 | 2684057.2544 | 1253234.1668
4 | 2684062.6018 | 1253242.1505 | 2684068.4245 | 1253238.6416 | 2684075.138 | 1253234.5783 | 2684076.792 | 1253237.137 | 2684078.4475 | 1253238.5282 | 2684080.443 | 1253239.3572 | 2684082.5909 | 1253239.5544 | 2684084.7029 | 1253239.0841 | 2684086.582 | 1253238.021 | 2684089.7033 | 1253242.4687
5 | 2684044.3111 | 1253267.5769 | 2684064.6819 | 1253254.0335 | 2684064.3873 | 1253245.5451 | 2684062.6018 | 1253242.1505
6 | 2684089.7033 | 1253242.4687 | 2684092.9502 | 1253247.1072 | 2684090.5339 | 1253249.3412 | 2684089.1934 | 1253252.3356 | 2684089.4332 | 1253255.6415 | 2684100.3581 | 1253271.8585
7 | 2684100.3581 | 1253271.8585 | 2684116.3195 | 1253295.5521
8 | 2684181.8613 | 1253294.2276 | 2684135.6595 | 1253324.2606
9 | 2684135.6595 | 1253324.2606 | 2684116.3195 | 1253295.5521
10 | 2684181.8613 | 1253294.2276 | 2684175.5897 | 1253284.7202 | 2684171.3848 | 1253278.352
11 | 2684206.1025 | 1253193.2069 | 2684237.181 | 1253172.3218
12 | 2684214.484 | 1253206.1135 | 2684206.1025 | 1253193.2069
13 | 2684223.9961 | 1253152.7974 | 2684237.181 | 1253172.3218
14 | 2684214.484 | 1253206.1135 | 2684223.8255 | 1253220.4905 | 2684240.3634 | 1253209.766
15 | 2684214.484 | 1253206.1135 | 2684186.5197 | 1253224.5029
16 | 2684151.1752 | 1253247.7455 | 2684186.5197 | 1253224.5029
17 | 2684151.1752 | 1253247.7455 | 2684171.3848 | 1253278.352
18 | 2684097.4845 | 1253390.0795 | 2684108.3124 | 1253382.6831 | 2684118.3479 | 1253375.8316
19 | 2684118.3479 | 1253375.8316 | 2684100.8844 | 1253350.2967
20 | 2684097.4845 | 1253390.0795 | 2684091.2797 | 1253382.8342
21 | 2684092.2228 | 1253337.6319 | 2684100.8844 | 1253350.2967
22 | 2684061.8983 | 1253293.2903 | 2684051.4598 | 1253278.0287
23 | 2684061.8983 | 1253293.2903 | 2684070.5837 | 1253305.9916
24 | 2684044.3111 | 1253267.5769 | 2684051.4598 | 1253278.0287
25 | 2684087.5285 | 1253330.7712 | 2684070.5837 | 1253305.9916
26 | 2684087.5285 | 1253330.7712 | 2684092.2228 | 1253337.6319
27 | 2684223.9961 | 1253152.7974 | 2684222.2776 | 1253150.0042 | 2684218.2685 | 1253143.7758 | 2684200.4841 | 1253118.1693
28 | 2684264.6421 | 1253125.6548 | 2684223.9961 | 1253152.7974
29 | 2684264.6421 | 1253125.6548 | 2684272.5579 | 1253137.2752
30 | 2684272.5579 | 1253137.2752 | 2684324.1173 | 1253212.9644

## bus_geodata
| x | y | coords
0 | 2684040.5853 | 1253209.2797
1 | 2684031.7481 | 1253196.0855
2 | 2684050.4815 | 1253224.0548
3 | 2684057.2544 | 1253234.1668
4 | 2684062.6018 | 1253242.1505
5 | 2684089.7033 | 1253242.4687
6 | 2684100.3581 | 1253271.8585
7 | 2684135.6595 | 1253324.2606
8 | 2684181.8613 | 1253294.2276
9 | 2684116.3195 | 1253295.5521
10 | 2684206.1025 | 1253193.2069
11 | 2684237.181 | 1253172.3218
12 | 2684214.484 | 1253206.1135
13 | 2684151.1752 | 1253247.7455
14 | 2684186.5197 | 1253224.5029
15 | 2684171.3848 | 1253278.352
16 | 2684118.3479 | 1253375.8316
17 | 2684097.4845 | 1253390.0795
18 | 2684100.8844 | 1253350.2967
19 | 2684061.8983 | 1253293.2903
20 | 2684051.4598 | 1253278.0287
21 | 2684070.5837 | 1253305.9916
22 | 2684044.3111 | 1253267.5769
23 | 2684091.2797 | 1253382.8342
24 | 2684092.2228 | 1253337.6318
25 | 2684087.5285 | 1253330.7712
26 | 2684200.4841 | 1253118.1693
27 | 2684223.9961 | 1253152.7974
28 | 2684264.6421 | 1253125.6548
29 | 2684240.3634 | 1253209.766
30 | 2684324.1173 | 1253212.9644
31 | 2684272.5579 | 1253137.2752
32 | 2684129.9518 | 1253215.5976

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97449 | -0.49071 | 0.0067929 | 0.0017025
1 | 0.97439 | -0.4927 | 0.0068144 | 0.0017079
2 | 0.97472 | -0.48627 | 0.0081424 | 0.0020407
3 | 0.97497 | -0.48142 | 0.0088468 | 0.0022172
4 | 0.97524 | -0.47603 | 0 | 0
5 | 0.97765 | -0.42882 | 0 | 0
6 | 0.98014 | -0.38023 | 0.030625 | 0.0076755
7 | 0.98742 | -0.23911 | 0 | 0
8 | 0.99449 | -0.10413 | 0 | 0
9 | 0.98297 | -0.32507 | 0.03155 | 0.0079071
10 | 0.99347 | -0.12504 | 0 | 0
11 | 0.99144 | -0.16435 | 0.0051461 | 0.0012897
12 | 0.99431 | -0.10891 | 0 | 0
13 | 1 | 0 | -0.28233 | -0.071843
14 | 0.99627 | -0.071242 | 0.032302 | 0.0080956
15 | 0.99694 | -0.057889 | 0.042269 | 0.010594
16 | 0.97088 | -0.56206 | 0 | 0
17 | 0.97082 | -0.56316 | 0 | 0
18 | 0.97095 | -0.56072 | 0.016882 | 0.0042311
19 | 0.97247 | -0.53061 | 0 | 0
20 | 0.97314 | -0.51736 | 0.0065903 | 0.0016517
21 | 0.97191 | -0.54165 | 0.019684 | 0.0049332
22 | 0.97368 | -0.50676 | 0 | 0
23 | 0.9708 | -0.56357 | 0.0023455 | 0.00058784
24 | 0.97122 | -0.55526 | 0 | 0
25 | 0.97137 | -0.55231 | 0 | 0
26 | 0.98952 | -0.20154 | 0.019462 | 0.0048776
27 | 0.99026 | -0.18704 | 0 | 0
28 | 0.9887 | -0.2173 | 0 | 0
29 | 0.99416 | -0.11184 | 0.0045089 | 0.00113
30 | 0.98733 | -0.24409 | 0.011038 | 0.0027664
31 | 0.98825 | -0.22604 | 0.023798 | 0.0059643
32 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0068151 | 0.0017081 | -0.0068144 | -0.0017079 | 6.4489e-07 | 2.1491e-07 | 0.010406 | 0.010406 | 0.010406 | 0.97449 | -0.49071 | 0.97439 | -0.4927 | 2.8589
1 | -0.013608 | -0.0034105 | 0.013611 | 0.0034122 | 2.8793e-06 | 1.6211e-06 | 0.020779 | 0.020779 | 0.020779 | 0.97449 | -0.49071 | 0.97472 | -0.48627 | 5.7085
2 | -0.021753 | -0.0054528 | 0.021758 | 0.0054559 | 5.0333e-06 | 3.0696e-06 | 0.033209 | 0.033209 | 0.033209 | 0.97472 | -0.48627 | 0.97497 | -0.48142 | 9.1234
3 | -0.030605 | -0.0076731 | 0.030613 | 0.007678 | 7.8625e-06 | 4.9121e-06 | 0.046711 | 0.046711 | 0.046711 | 0.97497 | -0.48142 | 0.97524 | -0.47603 | 12.8328
4 | -0.076268 | -0.019177 | 0.07644 | 0.019287 | 0.00017236 | 0.00010989 | 0.11639 | 0.11639 | 0.11639 | 0.97524 | -0.47603 | 0.97765 | -0.42882 | 31.9756
5 | 0.045655 | 0.011499 | -0.045588 | -0.011457 | 6.6987e-05 | 4.2414e-05 | 0.06968 | 0.06968 | 0.06968 | 0.97524 | -0.47603 | 0.97368 | -0.50676 | 19.1429
6 | -0.07644 | -0.019287 | 0.076618 | 0.019401 | 0.00017832 | 0.00011368 | 0.11639 | 0.11639 | 0.11639 | 0.97765 | -0.42882 | 0.98014 | -0.38023 | 31.9756
7 | -0.10724 | -0.027076 | 0.10753 | 0.027258 | 0.00028424 | 0.00018155 | 0.16289 | 0.16289 | 0.16289 | 0.98014 | -0.38023 | 0.98297 | -0.32507 | 44.7488
8 | -0.13965 | -0.035533 | 0.14057 | 0.036118 | 0.00091506 | 0.00058493 | 0.21064 | 0.21064 | 0.21064 | 0.98742 | -0.23911 | 0.99449 | -0.10413 | 57.8694
9 | 0.13965 | 0.035533 | -0.13908 | -0.035165 | 0.00057597 | 0.00036818 | 0.21064 | 0.21064 | 0.21064 | 0.98742 | -0.23911 | 0.98297 | -0.32507 | 57.8695
10 | -0.14057 | -0.036118 | 0.14089 | 0.03632 | 0.00031649 | 0.00020231 | 0.21064 | 0.21064 | 0.21064 | 0.99449 | -0.10413 | 0.99694 | -0.057889 | 57.8694
11 | 0.059703 | 0.01506 | -0.05959 | -0.014989 | 0.00011214 | 7.129e-05 | 0.089456 | 0.089457 | 0.089457 | 0.99347 | -0.12504 | 0.99144 | -0.16435 | 24.576
12 | -0.059703 | -0.01506 | 0.059749 | 0.01509 | 4.6142e-05 | 2.9332e-05 | 0.089456 | 0.089456 | 0.089456 | 0.99347 | -0.12504 | 0.99431 | -0.10891 | 24.576
13 | 0.054444 | 0.013699 | -0.054385 | -0.013662 | 5.8965e-05 | 3.7435e-05 | 0.081733 | 0.081733 | 0.081733 | 0.99144 | -0.16435 | 0.99026 | -0.18704 | 22.4542
14 | 0.0045095 | 0.00113 | -0.0045089 | -0.00113 | 6.2946e-07 | -7.5114e-08 | 0.0067485 | 0.0067487 | 0.0067487 | 0.99431 | -0.10891 | 0.99416 | -0.11184 | 1.854
15 | -0.064258 | -0.01622 | 0.064374 | 0.016294 | 0.00011616 | 7.3909e-05 | 0.096205 | 0.096205 | 0.096205 | 0.99431 | -0.10891 | 0.99627 | -0.071242 | 26.4299
16 | 0.097007 | 0.0246 | -0.096676 | -0.024389 | 0.000331 | 0.00021129 | 0.14445 | 0.14445 | 0.14445 | 1 | 0 | 0.99627 | -0.071242 | 39.6841
17 | 0.18367 | 0.047243 | -0.18315 | -0.046914 | 0.00051529 | 0.00032883 | 0.27373 | 0.27373 | 0.27373 | 1 | 0 | 0.99694 | -0.057889 | 37.6009
18 | 0.0023457 | 0.00058751 | -0.0023455 | -0.00058775 | 1.2244e-07 | -2.3404e-07 | 0.003595 | 0.0035951 | 0.0035951 | 0.97088 | -0.56206 | 0.97082 | -0.56316 | 0.98766
19 | -0.0023457 | -0.00058751 | 0.0023458 | 0.00058723 | 1.4992e-07 | -2.8664e-07 | 0.003595 | 0.0035948 | 0.003595 | 0.97088 | -0.56206 | 0.97095 | -0.56072 | 0.98762
20 | 0.0023455 | 0.00058775 | -0.0023455 | -0.00058784 | 4.6233e-08 | -8.8358e-08 | 0.0035951 | 0.0035951 | 0.0035951 | 0.97082 | -0.56316 | 0.9708 | -0.56357 | 0.98767
21 | -0.019228 | -0.0048183 | 0.019233 | 0.0048213 | 4.9962e-06 | 3.0077e-06 | 0.029467 | 0.029467 | 0.029467 | 0.97095 | -0.56072 | 0.97122 | -0.55526 | 8.0955
22 | -0.03895 | -0.0097749 | 0.038974 | 0.0097905 | 2.4632e-05 | 1.5535e-05 | 0.059603 | 0.059603 | 0.059603 | 0.97247 | -0.53061 | 0.97314 | -0.51736 | 16.3745
23 | 0.03895 | 0.0097749 | -0.038929 | -0.009762 | 2.0499e-05 | 1.2928e-05 | 0.059603 | 0.059603 | 0.059603 | 0.97247 | -0.53061 | 0.97191 | -0.54165 | 16.3745
24 | -0.045565 | -0.011442 | 0.045588 | 0.011457 | 2.3056e-05 | 1.4598e-05 | 0.06968 | 0.06968 | 0.06968 | 0.97314 | -0.51736 | 0.97368 | -0.50676 | 19.143
25 | 0.019245 | 0.0048288 | -0.019236 | -0.0048229 | 9.7749e-06 | 5.8841e-06 | 0.029467 | 0.029467 | 0.029467 | 0.97191 | -0.54165 | 0.97137 | -0.55231 | 8.0954
26 | -0.019233 | -0.0048213 | 0.019236 | 0.0048229 | 2.7043e-06 | 1.628e-06 | 0.029467 | 0.029467 | 0.029467 | 0.97122 | -0.55526 | 0.97137 | -0.55231 | 8.0954
27 | -0.019462 | -0.0048776 | 0.019475 | 0.0048856 | 1.3446e-05 | 8.0673e-06 | 0.029266 | 0.029266 | 0.029266 | 0.98952 | -0.20154 | 0.99026 | -0.18704 | 8.0402
28 | 0.03491 | 0.0087763 | -0.03486 | -0.0087447 | 5.0355e-05 | 3.1601e-05 | 0.052467 | 0.052467 | 0.052467 | 0.99026 | -0.18704 | 0.9887 | -0.2173 | 14.4141
29 | 0.03486 | 0.0087447 | -0.034845 | -0.0087356 | 1.4515e-05 | 9.1091e-06 | 0.052467 | 0.052467 | 0.052467 | 0.9887 | -0.2173 | 0.98825 | -0.22604 | 14.4141
30 | -0.011038 | -0.0027664 | 0.011047 | 0.0027713 | 9.5039e-06 | 4.9101e-06 | 0.016635 | 0.016635 | 0.016635 | 0.98733 | -0.24409 | 0.98825 | -0.22604 | 4.5702

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.28233 | 0.071843

## res_load
| p_mw | q_mvar
0 | 0.0067929 | 0.0017025
1 | 0.0068144 | 0.0017079
2 | 0.0081424 | 0.0020407
3 | 0.0088468 | 0.0022172
4 | 0.030625 | 0.0076755
5 | 0.03155 | 0.0079071
6 | 0.0051461 | 0.0012897
7 | 0.032302 | 0.0080956
8 | 0.042269 | 0.010594
9 | 0.016882 | 0.0042311
10 | 0.0065903 | 0.0016517
11 | 0.019684 | 0.0049332
12 | 0.0023455 | 0.00058784
13 | 0.019462 | 0.0048776
14 | 0.0045089 | 0.00113
15 | 0.011038 | 0.0027664
16 | 0.023798 | 0.0059643

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1