## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-545_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-545_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-545_0_5_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_261-545_0_5_node_5 | 0.4 | n |  | TRUE
4 | bus_LV_261-545_0_5_node_25 | 0.4 | n |  | TRUE
5 | bus_LV_261-545_0_5_node_4 | 0.4 | n |  | TRUE
6 | bus_LV_261-545_0_5_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_261-545_0_5_node_26 | 0.4 | n |  | TRUE
8 | bus_LV_261-545_0_5_node_9 | 0.4 | n |  | TRUE
9 | bus_LV_261-545_0_5_node_27 | 0.4 | n |  | TRUE
10 | bus_LV_261-545_0_5_node_12 | 0.4 | n |  | TRUE
11 | bus_LV_261-545_0_5_node_28 | 0.4 | n |  | TRUE
12 | bus_LV_261-545_0_5_node_7 | 0.4 | n |  | TRUE
13 | bus_LV_261-545_0_5_node_11 | 0.4 | n |  | TRUE
14 | bus_LV_261-545_0_5_node_18 | 0.4 | n |  | TRUE
15 | bus_LV_261-545_0_5_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_261-545_0_5_node_29 | 0.4 | n |  | TRUE
17 | bus_LV_261-545_0_5_node_19 | 0.4 | n |  | TRUE
18 | bus_LV_261-545_0_5_node_20 | 0.4 | n |  | TRUE
19 | bus_LV_261-545_0_5_node_13 | 0.4 | n |  | TRUE
20 | bus_LV_261-545_0_5_node_17 | 0.4 | n |  | TRUE
21 | bus_LV_261-545_0_5_node_24 | 0.4 | n |  | TRUE
22 | bus_LV_261-545_0_5_node_15 | 0.4 | n |  | TRUE
23 | bus_LV_261-545_0_5_node_14 | 0.4 | n |  | TRUE
24 | bus_LV_261-545_0_5_node_16 | 0.4 | n |  | TRUE
25 | bus_LV_261-545_0_5_node_22 | 0.4 | n |  | TRUE
26 | bus_LV_261-545_0_5_node_21 | 0.4 | n |  | TRUE
27 | bus_LV_261-545_0_5_node_23 | 0.4 | n |  | TRUE
28 | bus_MV_469_0_node_174 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-545_0_5_load_0 | 0 | 0.058485 | 0.014658 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-545_0_5_load_25 | 4 | 0.077434 | 0.019407 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-545_0_5_load_26 | 7 | 0.036392 | 0.0091206 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-545_0_5_load_27 | 9 | 0.021891 | 0.0054863 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-545_0_5_load_28 | 11 | 0.076821 | 0.019253 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-545_0_5_load_18 | 14 | 0.0017949 | 0.00044984 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-545_0_5_load_29 | 16 | 0.038748 | 0.0097112 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-545_0_5_load_19 | 17 | 0.037325 | 0.0093546 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-545_0_5_load_20 | 18 | 0.091609 | 0.022959 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-545_0_5_load_24 | 21 | 0.0016086 | 0.00040316 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-545_0_5_load_14 | 23 | 0.007445 | 0.0018659 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-545_0_5_load_16 | 24 | 0.020249 | 0.0050748 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-545_0_5_load_21 | 26 | 0.0045898 | 0.0011503 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-545_0_5_load_23 | 27 | 0.0051972 | 0.0013025 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 2 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-545_0_5_line_0 |  | 0 | 1 | 0.013687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-545_0_5_line_1 |  | 1 | 2 | 0.060242 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-545_0_5_line_2 |  | 1 | 3 | 0.093473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-545_0_5_line_3 |  | 2 | 4 | 0.015471 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-545_0_5_line_4 |  | 2 | 5 | 0.035906 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_261-545_0_5_line_5 |  | 2 | 6 | 0.084325 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
6 | LV_261-545_0_5_line_6 |  | 3 | 9 | 0.007944 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_261-545_0_5_line_7 |  | 5 | 7 | 0.008208 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_261-545_0_5_line_8 |  | 5 | 8 | 0.14528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_261-545_0_5_line_9 |  | 6 | 10 | 0.011631 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
10 | LV_261-545_0_5_line_10 |  | 6 | 11 | 0.008549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_261-545_0_5_line_11 |  | 8 | 15 | 0.10913 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_261-545_0_5_line_12 |  | 8 | 16 | 0.005673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-545_0_5_line_13 |  | 10 | 18 | 0.0023588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
14 | LV_261-545_0_5_line_14 |  | 12 | 13 | 0.072561 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_261-545_0_5_line_15 |  | 12 | 14 | 0.17574 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_261-545_0_5_line_16 |  | 13 | 18 | 0.05927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_261-545_0_5_line_17 |  | 14 | 19 | 0.080375 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_261-545_0_5_line_18 |  | 15 | 17 | 0.04845 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_261-545_0_5_line_19 |  | 19 | 20 | 0.1223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_261-545_0_5_line_20 |  | 20 | 21 | 0.013067 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_261-545_0_5_line_21 |  | 20 | 22 | 0.037382 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_261-545_0_5_line_22 |  | 21 | 25 | 0.014581 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_261-545_0_5_line_23 |  | 22 | 24 | 0.040852 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_261-545_0_5_line_24 |  | 22 | 23 | 0.025807 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_261-545_0_5_line_25 |  | 25 | 27 | 0.032657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_261-545_0_5_line_26 |  | 25 | 26 | 0.00051365 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-545_0_5_trafo_3 | 0.63 MVA 20/0.4 kV | 28 | 2 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19
0 | 2684124.7323 | 1253589.2724 | 2684116.4867 | 1253578.3481
1 | 2684124.7323 | 1253589.2724 | 2684135.3458 | 1253603.3226 | 2684163.2124 | 1253582.0801 | 2684167.8201 | 1253588.1168
2 | 2684082.6949 | 1253591.922 | 2684096.7747 | 1253610.5582 | 2684107.2399 | 1253624.4172 | 2684135.3458 | 1253603.3226 | 2684124.7323 | 1253589.2724
3 | 2684161.8548 | 1253601.1419 | 2684162.9911 | 1253591.8065 | 2684167.8201 | 1253588.1168
4 | 2684146.1938 | 1253559.4546 | 2684154.2071 | 1253570.0987 | 2684163.2124 | 1253582.0801 | 2684167.8201 | 1253588.1168
5 | 2684167.8201 | 1253588.1168 | 2684163.2124 | 1253582.0801 | 2684195.2814 | 1253557.7173 | 2684204.6718 | 1253550.5787 | 2684219.0664 | 1253539.6417 | 2684224.3071 | 1253535.6577
6 | 2684089.1005 | 1253587.1983 | 2684082.6949 | 1253591.922
7 | 2684152.6425 | 1253554.3534 | 2684146.1938 | 1253559.4546
8 | 2684123.4537 | 1253496.0504 | 2684125.5429 | 1253495.5908 | 2684142.8754 | 1253492.4346 | 2684144.4081 | 1253495.5587 | 2684147.6611 | 1253505.0677 | 2684153.252 | 1253503.5126 | 2684153.6395 | 1253505.4529 | 2684157.4891 | 1253526.0676 | 2684164.8224 | 1253525.0932 | 2684167.2436 | 1253528.3523 | 2684155.6054 | 1253530.1217 | 2684127.3162 | 1253534.3564 | 2684146.1938 | 1253559.4546
9 | 2684233.5831 | 1253528.6064 | 2684231.1725 | 1253530.4402 | 2684229.4333 | 1253531.7609 | 2684224.3071 | 1253535.6577
10 | 2684218.9997 | 1253528.9438 | 2684224.3071 | 1253535.6577
11 | 2684123.4537 | 1253496.0504 | 2684125.5429 | 1253495.5908 | 2684142.8754 | 1253492.4346 | 2684144.4081 | 1253495.5587 | 2684147.6611 | 1253505.0677 | 2684153.252 | 1253503.5126 | 2684153.6395 | 1253505.4529 | 2684157.8173 | 1253504.0445 | 2684160.2616 | 1253515.2321 | 2684162.4371 | 1253518.2542 | 2684165.1779 | 1253520.2613 | 2684169.0402 | 1253520.8722 | 2684176.6644 | 1253519.0792 | 2684181.9876 | 1253516.7197 | 2684187.9592 | 1253513.3353 | 2684203.0999 | 1253499.2843
12 | 2684117.8977 | 1253497.2725 | 2684123.4537 | 1253496.0504
13 | 2684233.5831 | 1253528.6064 | 2684235.0686 | 1253530.4388
14 | 2684277.9124 | 1253530.3827 | 2684296.8732 | 1253546.9427 | 2684325.881 | 1253572.2636 | 2684332.6633 | 1253578.1868
15 | 2684332.6633 | 1253578.1868 | 2684331.1083 | 1253579.8103 | 2684328.7378 | 1253582.0116 | 2684328.3469 | 1253583.496 | 2684328.6184 | 1253585.6237 | 2684328.8697 | 1253587.5844 | 2684328.5824 | 1253591.3275 | 2684326.8893 | 1253594.706 | 2684319.892 | 1253599.6435 | 2684301.7575 | 1253611.4388 | 2684292.3965 | 1253617.0431 | 2684279.4241 | 1253620.8392 | 2684271.469 | 1253624.6845 | 2684256.8138 | 1253640.6882 | 2684250.3653 | 1253646.3007 | 2684233.7567 | 1253658.0068 | 2684225.2757 | 1253664.3465 | 2684217.6219 | 1253669.8196 | 2684204.945 | 1253680.9701 | 2684199.9405 | 1253684.5516
16 | 2684277.9124 | 1253530.3827 | 2684251.403 | 1253550.5876 | 2684235.0686 | 1253530.4388
17 | 2684135.4273 | 1253732.4436 | 2684154.426 | 1253717.1241 | 2684199.9405 | 1253684.5516
18 | 2684203.0999 | 1253499.2843 | 2684176.3779 | 1253458.8697
19 | 2684135.4273 | 1253732.4436 | 2684145.0132 | 1253743.3769 | 2684151.2705 | 1253750.1375 | 2684156.824 | 1253754.92 | 2684174.0253 | 1253766.2396 | 2684202.2052 | 1253778.1046 | 2684240.1933 | 1253791.6216
20 | 2684240.1933 | 1253791.6216 | 2684252.688 | 1253795.4465
21 | 2684240.1933 | 1253791.6216 | 2684242.2276 | 1253828.9454
22 | 2684266.6308 | 1253799.7148 | 2684252.688 | 1253795.4465
23 | 2684242.2276 | 1253828.9454 | 2684254.7181 | 1253831.9364 | 2684256.3792 | 1253844.5807 | 2684253.5363 | 1253845.5188 | 2684253.4717 | 1253850.0546 | 2684245.7938 | 1253850.9087
24 | 2684242.2276 | 1253828.9454 | 2684227.3665 | 1253837.1848 | 2684229.6818 | 1253845.6904
25 | 2684266.6308 | 1253799.7148 | 2684282.6255 | 1253771.2208
26 | 2684267.1165 | 1253799.8818 | 2684266.6308 | 1253799.7148

## bus_geodata
| x | y | coords
0 | 2684116.4867 | 1253578.3481
1 | 2684124.7323 | 1253589.2724
2 | 2684167.8201 | 1253588.1168
3 | 2684082.6949 | 1253591.922
4 | 2684161.8548 | 1253601.1419
5 | 2684146.1938 | 1253559.4546
6 | 2684224.3071 | 1253535.6577
7 | 2684152.6425 | 1253554.3534
8 | 2684123.4537 | 1253496.0504
9 | 2684089.1005 | 1253587.1983
10 | 2684233.5831 | 1253528.6064
11 | 2684218.9997 | 1253528.9438
12 | 2684332.6633 | 1253578.1868
13 | 2684277.9124 | 1253530.3827
14 | 2684199.9405 | 1253684.5516
15 | 2684203.0999 | 1253499.2843
16 | 2684117.8977 | 1253497.2725
17 | 2684176.3779 | 1253458.8697
18 | 2684235.0686 | 1253530.4388
19 | 2684135.4273 | 1253732.4436
20 | 2684240.1933 | 1253791.6216
21 | 2684252.688 | 1253795.4465
22 | 2684242.2276 | 1253828.9454
23 | 2684229.6818 | 1253845.6904
24 | 2684245.7938 | 1253850.9087
25 | 2684266.6308 | 1253799.7148
26 | 2684267.1165 | 1253799.8818
27 | 2684282.6255 | 1253771.2208
28 | 2684163.2124 | 1253582.0801

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99486 | -0.098859 | 0.058485 | 0.014658
1 | 0.99558 | -0.084773 | 0 | 0
2 | 1 | 0 | -0.48553 | -0.12292
3 | 0.99372 | -0.12082 | 0 | 0
4 | 0.99891 | -0.020903 | 0.077434 | 0.019407
5 | 0.99629 | -0.070652 | 0 | 0
6 | 0.99189 | -0.1551 | 0 | 0
7 | 0.99602 | -0.075898 | 0.036392 | 0.0091206
8 | 0.98609 | -0.26674 | 0 | 0
9 | 0.99356 | -0.12389 | 0.021891 | 0.0054863
10 | 0.99118 | -0.16876 | 0 | 0
11 | 0.99129 | -0.16674 | 0.076821 | 0.019253
12 | 0.98599 | -0.26771 | 0 | 0
13 | 0.98877 | -0.21465 | 0 | 0
14 | 0.97928 | -0.39745 | 0.0017949 | 0.00044984
15 | 0.98232 | -0.34004 | 0 | 0
16 | 0.98589 | -0.27068 | 0.038748 | 0.0097112
17 | 0.98065 | -0.37277 | 0.037325 | 0.0093546
18 | 0.99103 | -0.17153 | 0.091609 | 0.022959
19 | 0.97634 | -0.45474 | 0 | 0
20 | 0.97187 | -0.54257 | 0 | 0
21 | 0.97173 | -0.54532 | 0.0016086 | 0.00040316
22 | 0.97091 | -0.56169 | 0 | 0
23 | 0.97073 | -0.56525 | 0.007445 | 0.0018659
24 | 0.97013 | -0.577 | 0.020249 | 0.0050748
25 | 0.9716 | -0.54795 | 0 | 0
26 | 0.9716 | -0.548 | 0.0045898 | 0.0011503
27 | 0.97144 | -0.55109 | 0.0051972 | 0.0013025
28 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.058485 | -0.014658 | 0.058524 | 0.014683 | 3.9275e-05 | 2.4958e-05 | 0.087476 | 0.087476 | 0.087476 | 0.99486 | -0.098859 | 0.99558 | -0.084773 | 24.0319
1 | -0.080455 | -0.020194 | 0.080782 | 0.020402 | 0.00032672 | 0.00020832 | 0.12026 | 0.12026 | 0.12026 | 0.99558 | -0.084773 | 1 | 0 | 33.0386
2 | 0.021932 | 0.0055112 | -0.021894 | -0.0054883 | 3.7675e-05 | 2.2899e-05 | 0.032784 | 0.032785 | 0.032785 | 0.99558 | -0.084773 | 0.99372 | -0.12082 | 9.0068
3 | 0.077511 | 0.019456 | -0.077434 | -0.019407 | 7.7192e-05 | 4.92e-05 | 0.11535 | 0.11535 | 0.11535 | 1 | 0 | 0.99891 | -0.020903 | 31.6891
4 | 0.11378 | 0.029023 | -0.11339 | -0.028776 | 0.00038678 | 0.00024707 | 0.16949 | 0.16949 | 0.16949 | 1 | 0 | 0.99629 | -0.070652 | 46.562
5 | 0.21181 | 0.054043 | -0.21023 | -0.053038 | 0.0015739 | 0.0010051 | 0.31551 | 0.31551 | 0.31551 | 1 | 0 | 0.99189 | -0.1551 | 43.3395
6 | 0.021894 | 0.0054883 | -0.021891 | -0.0054863 | 3.202e-06 | 1.9464e-06 | 0.032785 | 0.032785 | 0.032785 | 0.99372 | -0.12082 | 0.99356 | -0.12389 | 9.0068
7 | 0.036401 | 0.0091264 | -0.036392 | -0.0091206 | 9.0982e-06 | 5.716e-06 | 0.054368 | 0.054368 | 0.054368 | 0.99629 | -0.070652 | 0.99602 | -0.075898 | 14.9363
8 | 0.076992 | 0.01965 | -0.07627 | -0.01919 | 0.00072197 | 0.00046019 | 0.11512 | 0.11512 | 0.11512 | 0.99629 | -0.070652 | 0.98609 | -0.26674 | 31.6259
9 | 0.13337 | 0.033757 | -0.13328 | -0.033702 | 8.7403e-05 | 5.5638e-05 | 0.2002 | 0.2002 | 0.2002 | 0.99189 | -0.1551 | 0.99118 | -0.16876 | 27.4994
10 | 0.076864 | 0.01928 | -0.076821 | -0.019253 | 4.2631e-05 | 2.7174e-05 | 0.11532 | 0.11532 | 0.11532 | 0.99189 | -0.1551 | 0.99129 | -0.16674 | 31.6803
11 | 0.037515 | 0.0094739 | -0.037383 | -0.0093913 | 0.00013127 | 8.2628e-05 | 0.056636 | 0.056636 | 0.056636 | 0.98609 | -0.26674 | 0.98232 | -0.34004 | 15.5594
12 | 0.038755 | 0.0097157 | -0.038748 | -0.0097112 | 7.2761e-06 | 4.5844e-06 | 0.058483 | 0.058483 | 0.058483 | 0.98609 | -0.26674 | 0.98589 | -0.27068 | 16.0667
13 | 0.13328 | 0.033702 | -0.13326 | -0.03369 | 1.7726e-05 | 1.1284e-05 | 0.2002 | 0.2002 | 0.2002 | 0.99118 | -0.16876 | 0.99103 | -0.17153 | 27.4994
14 | -0.04146 | -0.010609 | 0.041567 | 0.010676 | 0.0001068 | 6.7421e-05 | 0.062648 | 0.062648 | 0.062648 | 0.98599 | -0.26771 | 0.98877 | -0.21465 | 17.2111
15 | 0.04146 | 0.010609 | -0.041202 | -0.010445 | 0.00025865 | 0.00016331 | 0.062648 | 0.062649 | 0.062649 | 0.98599 | -0.26771 | 0.97928 | -0.39745 | 17.2113
16 | -0.041567 | -0.010676 | 0.041654 | 0.010731 | 8.7232e-05 | 5.5067e-05 | 0.062648 | 0.062648 | 0.062648 | 0.98877 | -0.21465 | 0.99103 | -0.17153 | 17.211
17 | 0.039407 | 0.0099954 | -0.039299 | -0.0099272 | 0.00010822 | 6.8255e-05 | 0.059922 | 0.059922 | 0.059922 | 0.97928 | -0.39745 | 0.97634 | -0.45474 | 16.4622
18 | 0.037383 | 0.0093913 | -0.037325 | -0.0093546 | 5.8279e-05 | 3.6686e-05 | 0.056636 | 0.056636 | 0.056636 | 0.98232 | -0.34004 | 0.98065 | -0.37277 | 15.5594
19 | 0.039299 | 0.0099272 | -0.039134 | -0.0098233 | 0.00016468 | 0.00010387 | 0.059922 | 0.059923 | 0.059923 | 0.97634 | -0.45474 | 0.97187 | -0.54257 | 16.4623
20 | 0.011399 | 0.0028575 | -0.011398 | -0.0028567 | 1.4927e-06 | 7.934e-07 | 0.017453 | 0.017453 | 0.017453 | 0.97187 | -0.54257 | 0.97173 | -0.54532 | 4.7948
21 | 0.027735 | 0.0069658 | -0.02771 | -0.0069501 | 2.5284e-05 | 1.5719e-05 | 0.04247 | 0.04247 | 0.04247 | 0.97187 | -0.54257 | 0.97091 | -0.56169 | 11.6675
22 | 0.009789 | 0.0024535 | -0.0097878 | -0.0024529 | 1.2287e-06 | 6.0574e-07 | 0.01499 | 0.01499 | 0.01499 | 0.97173 | -0.54532 | 0.9716 | -0.54795 | 4.1181
23 | 0.020263 | 0.0050837 | -0.020249 | -0.0050748 | 1.4777e-05 | 8.9523e-06 | 0.031058 | 0.031058 | 0.031058 | 0.97091 | -0.56169 | 0.97013 | -0.577 | 8.5324
24 | 0.0074463 | 0.0018664 | -0.007445 | -0.0018659 | 1.2604e-06 | 4.8758e-07 | 0.011412 | 0.011412 | 0.011412 | 0.97091 | -0.56169 | 0.97073 | -0.56525 | 3.1353
25 | 0.0051979 | 0.0013026 | -0.0051972 | -0.0013025 | 7.7609e-07 | 9.2318e-08 | 0.0079607 | 0.0079608 | 0.0079608 | 0.9716 | -0.54795 | 0.97144 | -0.55109 | 2.187
26 | 0.0045898 | 0.0011503 | -0.0045898 | -0.0011503 | 9.5176e-09 | -2.7049e-10 | 0.0070294 | 0.0070294 | 0.0070294 | 0.9716 | -0.54795 | 0.9716 | -0.548 | 1.9311

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.48553 | 0.12292

## res_load
| p_mw | q_mvar
0 | 0.058485 | 0.014658
1 | 0.077434 | 0.019407
2 | 0.036392 | 0.0091206
3 | 0.021891 | 0.0054863
4 | 0.076821 | 0.019253
5 | 0.0017949 | 0.00044984
6 | 0.038748 | 0.0097112
7 | 0.037325 | 0.0093546
8 | 0.091609 | 0.022959
9 | 0.0016086 | 0.00040316
10 | 0.007445 | 0.0018659
11 | 0.020249 | 0.0050748
12 | 0.0045898 | 0.0011503
13 | 0.0051972 | 0.0013025

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1