## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-572_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-572_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-572_0_6_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_261-572_0_6_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_261-572_0_6_node_115 | 0.4 | n |  | TRUE
5 | bus_LV_261-572_0_6_node_46 | 0.4 | n |  | TRUE
6 | bus_LV_261-572_0_6_node_120 | 0.4 | n |  | TRUE
7 | bus_LV_261-572_0_6_node_114 | 0.4 | n |  | TRUE
8 | bus_LV_261-572_0_6_node_44 | 0.4 | n |  | TRUE
9 | bus_LV_261-572_0_6_node_8 | 0.4 | n |  | TRUE
10 | bus_LV_261-572_0_6_node_30 | 0.4 | n |  | TRUE
11 | bus_LV_261-572_0_6_node_57 | 0.4 | n |  | TRUE
12 | bus_LV_261-572_0_6_node_9 | 0.4 | n |  | TRUE
13 | bus_LV_261-572_0_6_node_119 | 0.4 | n |  | TRUE
14 | bus_LV_261-572_0_6_node_7 | 0.4 | n |  | TRUE
15 | bus_LV_261-572_0_6_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_261-572_0_6_node_32 | 0.4 | n |  | TRUE
17 | bus_LV_261-572_0_6_node_106 | 0.4 | n |  | TRUE
18 | bus_LV_261-572_0_6_node_11 | 0.4 | n |  | TRUE
19 | bus_LV_261-572_0_6_node_14 | 0.4 | n |  | TRUE
20 | bus_LV_261-572_0_6_node_16 | 0.4 | n |  | TRUE
21 | bus_LV_261-572_0_6_node_81 | 0.4 | n |  | TRUE
22 | bus_LV_261-572_0_6_node_13 | 0.4 | n |  | TRUE
23 | bus_LV_261-572_0_6_node_17 | 0.4 | n |  | TRUE
24 | bus_LV_261-572_0_6_node_23 | 0.4 | n |  | TRUE
25 | bus_LV_261-572_0_6_node_25 | 0.4 | n |  | TRUE
26 | bus_LV_261-572_0_6_node_90 | 0.4 | n |  | TRUE
27 | bus_LV_261-572_0_6_node_20 | 0.4 | n |  | TRUE
28 | bus_LV_261-572_0_6_node_100 | 0.4 | n |  | TRUE
29 | bus_LV_261-572_0_6_node_43 | 0.4 | n |  | TRUE
30 | bus_LV_261-572_0_6_node_18 | 0.4 | n |  | TRUE
31 | bus_LV_261-572_0_6_node_45 | 0.4 | n |  | TRUE
32 | bus_LV_261-572_0_6_node_49 | 0.4 | n |  | TRUE
33 | bus_LV_261-572_0_6_node_60 | 0.4 | n |  | TRUE
34 | bus_LV_261-572_0_6_node_19 | 0.4 | n |  | TRUE
35 | bus_LV_261-572_0_6_node_21 | 0.4 | n |  | TRUE
36 | bus_LV_261-572_0_6_node_109 | 0.4 | n |  | TRUE
37 | bus_LV_261-572_0_6_node_42 | 0.4 | n |  | TRUE
38 | bus_LV_261-572_0_6_node_6 | 0.4 | n |  | TRUE
39 | bus_LV_261-572_0_6_node_58 | 0.4 | n |  | TRUE
40 | bus_LV_261-572_0_6_node_53 | 0.4 | n |  | TRUE
41 | bus_LV_261-572_0_6_node_111 | 0.4 | n |  | TRUE
42 | bus_LV_261-572_0_6_node_24 | 0.4 | n |  | TRUE
43 | bus_LV_261-572_0_6_node_26 | 0.4 | n |  | TRUE
44 | bus_LV_261-572_0_6_node_105 | 0.4 | n |  | TRUE
45 | bus_LV_261-572_0_6_node_62 | 0.4 | n |  | TRUE
46 | bus_LV_261-572_0_6_node_118 | 0.4 | n |  | TRUE
47 | bus_LV_261-572_0_6_node_117 | 0.4 | n |  | TRUE
48 | bus_LV_261-572_0_6_node_27 | 0.4 | n |  | TRUE
49 | bus_LV_261-572_0_6_node_28 | 0.4 | n |  | TRUE
50 | bus_LV_261-572_0_6_node_116 | 0.4 | n |  | TRUE
51 | bus_LV_261-572_0_6_node_67 | 0.4 | n |  | TRUE
52 | bus_LV_261-572_0_6_node_31 | 0.4 | n |  | TRUE
53 | bus_LV_261-572_0_6_node_65 | 0.4 | n |  | TRUE
54 | bus_LV_261-572_0_6_node_61 | 0.4 | n |  | TRUE
55 | bus_LV_261-572_0_6_node_110 | 0.4 | n |  | TRUE
56 | bus_LV_261-572_0_6_node_107 | 0.4 | n |  | TRUE
57 | bus_LV_261-572_0_6_node_33 | 0.4 | n |  | TRUE
58 | bus_LV_261-572_0_6_node_98 | 0.4 | n |  | TRUE
59 | bus_LV_261-572_0_6_node_34 | 0.4 | n |  | TRUE
60 | bus_LV_261-572_0_6_node_93 | 0.4 | n |  | TRUE
61 | bus_LV_261-572_0_6_node_82 | 0.4 | n |  | TRUE
62 | bus_LV_261-572_0_6_node_37 | 0.4 | n |  | TRUE
63 | bus_LV_261-572_0_6_node_79 | 0.4 | n |  | TRUE
64 | bus_LV_261-572_0_6_node_36 | 0.4 | n |  | TRUE
65 | bus_LV_261-572_0_6_node_104 | 0.4 | n |  | TRUE
66 | bus_LV_261-572_0_6_node_103 | 0.4 | n |  | TRUE
67 | bus_LV_261-572_0_6_node_101 | 0.4 | n |  | TRUE
68 | bus_LV_261-572_0_6_node_99 | 0.4 | n |  | TRUE
69 | bus_LV_261-572_0_6_node_38 | 0.4 | n |  | TRUE
70 | bus_LV_261-572_0_6_node_95 | 0.4 | n |  | TRUE
71 | bus_LV_261-572_0_6_node_121 | 0.4 | n |  | TRUE
72 | bus_LV_261-572_0_6_node_5 | 0.4 | n |  | TRUE
73 | bus_LV_261-572_0_6_node_40 | 0.4 | n |  | TRUE
74 | bus_LV_261-572_0_6_node_55 | 0.4 | n |  | TRUE
75 | bus_LV_261-572_0_6_node_50 | 0.4 | n |  | TRUE
76 | bus_LV_261-572_0_6_node_52 | 0.4 | n |  | TRUE
77 | bus_LV_261-572_0_6_node_51 | 0.4 | n |  | TRUE
78 | bus_LV_261-572_0_6_node_80 | 0.4 | n |  | TRUE
79 | bus_LV_261-572_0_6_node_83 | 0.4 | n |  | TRUE
80 | bus_LV_261-572_0_6_node_84 | 0.4 | n |  | TRUE
81 | bus_LV_261-572_0_6_node_113 | 0.4 | n |  | TRUE
82 | bus_LV_261-572_0_6_node_89 | 0.4 | n |  | TRUE
83 | bus_LV_261-572_0_6_node_47 | 0.4 | n |  | TRUE
84 | bus_LV_261-572_0_6_node_59 | 0.4 | n |  | TRUE
85 | bus_LV_261-572_0_6_node_108 | 0.4 | n |  | TRUE
86 | bus_LV_261-572_0_6_node_112 | 0.4 | n |  | TRUE
87 | bus_LV_261-572_0_6_node_56 | 0.4 | n |  | TRUE
88 | bus_LV_261-572_0_6_node_70 | 0.4 | n |  | TRUE
89 | bus_LV_261-572_0_6_node_72 | 0.4 | n |  | TRUE
90 | bus_LV_261-572_0_6_node_68 | 0.4 | n |  | TRUE
91 | bus_LV_261-572_0_6_node_77 | 0.4 | n |  | TRUE
92 | bus_LV_261-572_0_6_node_92 | 0.4 | n |  | TRUE
93 | bus_LV_261-572_0_6_node_91 | 0.4 | n |  | TRUE
94 | bus_LV_261-572_0_6_node_63 | 0.4 | n |  | TRUE
95 | bus_LV_261-572_0_6_node_127 | 0.4 | n |  | TRUE
96 | bus_LV_261-572_0_6_node_66 | 0.4 | n |  | TRUE
97 | bus_LV_261-572_0_6_node_102 | 0.4 | n |  | TRUE
98 | bus_LV_261-572_0_6_node_74 | 0.4 | n |  | TRUE
99 | bus_LV_261-572_0_6_node_88 | 0.4 | n |  | TRUE
100 | bus_LV_261-572_0_6_node_97 | 0.4 | n |  | TRUE
101 | bus_LV_261-572_0_6_node_96 | 0.4 | n |  | TRUE
102 | bus_LV_261-572_0_6_node_125 | 0.4 | n |  | TRUE
103 | bus_LV_261-572_0_6_node_122 | 0.4 | n |  | TRUE
104 | bus_LV_261-572_0_6_node_94 | 0.4 | n |  | TRUE
105 | bus_LV_261-572_0_6_node_39 | 0.4 | n |  | TRUE
106 | bus_LV_261-572_0_6_node_41 | 0.4 | n |  | TRUE
107 | bus_LV_261-572_0_6_node_48 | 0.4 | n |  | TRUE
108 | bus_LV_261-572_0_6_node_54 | 0.4 | n |  | TRUE
109 | bus_LV_261-572_0_6_node_126 | 0.4 | n |  | TRUE
110 | bus_LV_261-572_0_6_node_124 | 0.4 | n |  | TRUE
111 | bus_LV_261-572_0_6_node_69 | 0.4 | n |  | TRUE
112 | bus_LV_261-572_0_6_node_71 | 0.4 | n |  | TRUE
113 | bus_LV_261-572_0_6_node_73 | 0.4 | n |  | TRUE
114 | bus_LV_261-572_0_6_node_78 | 0.4 | n |  | TRUE
115 | bus_LV_261-572_0_6_node_75 | 0.4 | n |  | TRUE
116 | bus_LV_261-572_0_6_node_87 | 0.4 | n |  | TRUE
117 | bus_LV_261-572_0_6_node_86 | 0.4 | n |  | TRUE
118 | bus_LV_261-572_0_6_node_76 | 0.4 | n |  | TRUE
119 | bus_LV_261-572_0_6_node_85 | 0.4 | n |  | TRUE
120 | bus_LV_261-572_0_6_node_123 | 0.4 | n |  | TRUE
121 | bus_MV_533_0_node_101 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-572_0_6_load_0 | 0 | 0.0039625 | 0.00099309 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-572_0_6_load_1 | 1 | 0.0040227 | 0.0010082 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-572_0_6_load_2 | 2 | 0.0039421 | 0.00098798 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-572_0_6_load_46 | 5 | 0.0040267 | 0.0010092 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-572_0_6_load_114 | 7 | 0.0058953 | 0.0014775 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-572_0_6_load_44 | 8 | 0.0039236 | 0.00098334 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-572_0_6_load_57 | 11 | 0.0043444 | 0.0010888 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-572_0_6_load_119 | 13 | 0.003259 | 0.00081679 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-572_0_6_load_106 | 17 | 0.0062309 | 0.0015616 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-572_0_6_load_81 | 21 | 0.0042276 | 0.0010595 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-572_0_6_load_90 | 26 | 0.0038337 | 0.00096081 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-572_0_6_load_100 | 28 | 0.016359 | 0.0040999 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-572_0_6_load_43 | 29 | 0.0032537 | 0.00081545 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-572_0_6_load_45 | 31 | 0.004029 | 0.0010098 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-572_0_6_load_49 | 32 | 0.0043571 | 0.001092 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-572_0_6_load_60 | 33 | 0.0043064 | 0.0010793 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-572_0_6_load_109 | 36 | 0.0076694 | 0.0019221 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_261-572_0_6_load_42 | 37 | 0.0032895 | 0.00082444 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_261-572_0_6_load_6 | 38 | 0.0032933 | 0.00082537 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_261-572_0_6_load_58 | 39 | 0.0062976 | 0.0015783 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_261-572_0_6_load_53 | 40 | 0.0062584 | 0.0015685 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_261-572_0_6_load_111 | 41 | 0.0031817 | 0.00079741 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_261-572_0_6_load_105 | 44 | 0.0046946 | 0.0011766 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_261-572_0_6_load_62 | 45 | 0.052158 | 0.013072 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_261-572_0_6_load_117 | 47 | 0.070494 | 0.017668 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_261-572_0_6_load_116 | 50 | 0.030342 | 0.0076044 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_261-572_0_6_load_67 | 51 | 0.0076581 | 0.0019193 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_261-572_0_6_load_65 | 53 | 0.0061235 | 0.0015347 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_261-572_0_6_load_61 | 54 | 0.0043213 | 0.001083 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_261-572_0_6_load_110 | 55 | 0.0021389 | 0.00053606 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_261-572_0_6_load_107 | 56 | 0.0068488 | 0.0017165 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_261-572_0_6_load_98 | 58 | 0.0024377 | 0.00061095 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_261-572_0_6_load_93 | 60 | 0.0022625 | 0.00056704 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_261-572_0_6_load_82 | 61 | 0.0037 | 0.00092732 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_261-572_0_6_load_79 | 63 | 0.0032533 | 0.00081537 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_261-572_0_6_load_104 | 65 | 0.0016326 | 0.00040916 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_261-572_0_6_load_103 | 66 | 0.0016291 | 0.00040828 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_261-572_0_6_load_99 | 68 | 0.0050391 | 0.0012629 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_261-572_0_6_load_121 | 71 | 0.0040349 | 0.0010113 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_261-572_0_6_load_5 | 72 | 0.0040887 | 0.0010247 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_261-572_0_6_load_40 | 73 | 0.0031647 | 0.00079315 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_261-572_0_6_load_55 | 74 | 0.0046248 | 0.0011591 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_261-572_0_6_load_50 | 75 | 0.0031613 | 0.00079231 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_261-572_0_6_load_52 | 76 | 0.0032513 | 0.00081485 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_261-572_0_6_load_51 | 77 | 0.0037615 | 0.00094273 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_261-572_0_6_load_80 | 78 | 0.0050256 | 0.0012595 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_261-572_0_6_load_83 | 79 | 0.0016323 | 0.0004091 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_261-572_0_6_load_84 | 80 | 0.0015611 | 0.00039126 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_261-572_0_6_load_113 | 81 | 0.0031768 | 0.00079618 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_261-572_0_6_load_89 | 82 | 0.0040313 | 0.0010104 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_261-572_0_6_load_47 | 83 | 0.0031851 | 0.00079825 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_261-572_0_6_load_59 | 84 | 0.004276 | 0.0010717 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_261-572_0_6_load_108 | 85 | 0.0068426 | 0.0017149 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_261-572_0_6_load_112 | 86 | 0.0025267 | 0.00063325 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_261-572_0_6_load_56 | 87 | 0.0060974 | 0.0015281 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_261-572_0_6_load_68 | 90 | 0.0025099 | 0.00062904 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_261-572_0_6_load_92 | 92 | 0.0063259 | 0.0015854 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_261-572_0_6_load_91 | 93 | 0.0040847 | 0.0010237 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_261-572_0_6_load_63 | 94 | 0.018747 | 0.0046984 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_261-572_0_6_load_127 | 95 | 0.001394 | 0.00034937 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_261-572_0_6_load_66 | 96 | 0.013209 | 0.0033106 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_261-572_0_6_load_102 | 97 | 0.0016157 | 0.00040493 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_261-572_0_6_load_74 | 98 | 0.0029355 | 0.0007357 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_261-572_0_6_load_88 | 99 | 0.0071432 | 0.0017903 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_261-572_0_6_load_97 | 100 | 0.0043523 | 0.0010908 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_261-572_0_6_load_125 | 102 | 0.0016202 | 0.00040605 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_261-572_0_6_load_122 | 103 | 0.0033003 | 0.00082714 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_261-572_0_6_load_94 | 104 | 0.0027329 | 0.00068492 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_261-572_0_6_load_39 | 105 | 0.0032038 | 0.00080295 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_261-572_0_6_load_41 | 106 | 0.003207 | 0.00080376 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_261-572_0_6_load_48 | 107 | 0.0032016 | 0.00080239 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_261-572_0_6_load_54 | 108 | 0.0046245 | 0.001159 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_261-572_0_6_load_126 | 109 | 0.0016264 | 0.00040762 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_261-572_0_6_load_124 | 110 | 0.00164 | 0.00041104 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_261-572_0_6_load_69 | 111 | 0.0025231 | 0.00063235 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_261-572_0_6_load_71 | 112 | 0.0017446 | 0.00043724 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_261-572_0_6_load_73 | 113 | 0.0017672 | 0.00044291 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_261-572_0_6_load_78 | 114 | 0.0076081 | 0.0019068 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_261-572_0_6_load_75 | 115 | 0.0074774 | 0.001874 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_261-572_0_6_load_87 | 116 | 0.0062058 | 0.0015553 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_261-572_0_6_load_86 | 117 | 0.0036857 | 0.00092372 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_261-572_0_6_load_76 | 118 | 0.017248 | 0.0043228 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_261-572_0_6_load_85 | 119 | 0.0016428 | 0.00041172 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_261-572_0_6_load_123 | 120 | 0.0016196 | 0.0004059 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 27 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-572_0_6_line_0 |  | 0 | 1 | 0.014362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-572_0_6_line_1 |  | 0 | 2 | 0.014215 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-572_0_6_line_2 |  | 1 | 3 | 0.011041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-572_0_6_line_3 |  | 3 | 4 | 0.003167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
4 | LV_261-572_0_6_line_4 |  | 3 | 5 | 0.027989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
5 | LV_261-572_0_6_line_5 |  | 4 | 6 | 0.00409 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
6 | LV_261-572_0_6_line_6 |  | 4 | 7 | 0.016164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_261-572_0_6_line_7 |  | 5 | 8 | 0.014314 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
8 | LV_261-572_0_6_line_8 |  | 6 | 71 | 0.018742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
9 | LV_261-572_0_6_line_9 |  | 6 | 119 | 0.00030729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_261-572_0_6_line_10 |  | 7 | 81 | 0.024628 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_261-572_0_6_line_11 |  | 8 | 31 | 0.014329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
12 | LV_261-572_0_6_line_12 |  | 9 | 10 | 0.013899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
13 | LV_261-572_0_6_line_13 |  | 9 | 11 | 0.0072298 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
14 | LV_261-572_0_6_line_14 |  | 10 | 52 | 0.01806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
15 | LV_261-572_0_6_line_15 |  | 10 | 53 | 0.016151 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_261-572_0_6_line_16 |  | 11 | 74 | 0.014346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
17 | LV_261-572_0_6_line_17 |  | 12 | 13 | 0.011502 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_261-572_0_6_line_18 |  | 12 | 14 | 0.0075759 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_261-572_0_6_line_19 |  | 13 | 75 | 0.014346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_261-572_0_6_line_20 |  | 14 | 37 | 0.011514 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_261-572_0_6_line_21 |  | 14 | 38 | 0.034559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_261-572_0_6_line_22 |  | 15 | 16 | 0.0094063 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
23 | LV_261-572_0_6_line_23 |  | 15 | 17 | 0.033016 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
24 | LV_261-572_0_6_line_24 |  | 16 | 55 | 0.0059671 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_261-572_0_6_line_25 |  | 16 | 56 | 0.015256 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
26 | LV_261-572_0_6_line_26 |  | 17 | 44 | 0.025334 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
27 | LV_261-572_0_6_line_27 |  | 18 | 19 | 0.006805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_261-572_0_6_line_28 |  | 18 | 20 | 0.012056 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
29 | LV_261-572_0_6_line_29 |  | 18 | 21 | 0.021029 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
30 | LV_261-572_0_6_line_30 |  | 19 | 25 | 0.037454 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_261-572_0_6_line_31 |  | 19 | 26 | 0.010747 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_261-572_0_6_line_32 |  | 20 | 27 | 0.005586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
33 | LV_261-572_0_6_line_33 |  | 20 | 28 | 0.026611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_261-572_0_6_line_34 |  | 21 | 78 | 0.021015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
35 | LV_261-572_0_6_line_35 |  | 22 | 23 | 0.003777 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_261-572_0_6_line_36 |  | 22 | 24 | 0.004234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_261-572_0_6_line_37 |  | 23 | 29 | 0.010038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_261-572_0_6_line_38 |  | 23 | 30 | 0.0087497 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
39 | LV_261-572_0_6_line_39 |  | 23 | 31 | 0.027537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
40 | LV_261-572_0_6_line_40 |  | 24 | 41 | 0.011844 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_261-572_0_6_line_41 |  | 25 | 45 | 0.022574 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_261-572_0_6_line_42 |  | 26 | 82 | 0.028099 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_261-572_0_6_line_43 |  | 30 | 32 | 0.010203 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_261-572_0_6_line_44 |  | 30 | 33 | 0.02697 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
45 | LV_261-572_0_6_line_45 |  | 32 | 83 | 0.014338 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_261-572_0_6_line_46 |  | 33 | 84 | 0.014328 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
47 | LV_261-572_0_6_line_47 |  | 34 | 35 | 0.037511 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
48 | LV_261-572_0_6_line_48 |  | 34 | 36 | 0.035372 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
49 | LV_261-572_0_6_line_49 |  | 35 | 39 | 0.011198 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
50 | LV_261-572_0_6_line_50 |  | 35 | 40 | 0.02944 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_261-572_0_6_line_51 |  | 36 | 85 | 0.022486 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
52 | LV_261-572_0_6_line_52 |  | 37 | 73 | 0.014345 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_261-572_0_6_line_53 |  | 38 | 72 | 0.014476 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_261-572_0_6_line_54 |  | 39 | 87 | 0.014348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
55 | LV_261-572_0_6_line_55 |  | 40 | 77 | 0.015599 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_261-572_0_6_line_56 |  | 41 | 86 | 0.021336 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_261-572_0_6_line_57 |  | 42 | 43 | 0.098795 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
58 | LV_261-572_0_6_line_58 |  | 42 | 44 | 0.024582 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
59 | LV_261-572_0_6_line_59 |  | 43 | 46 | 0.011519 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_261-572_0_6_line_60 |  | 43 | 47 | 0.0025186 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_261-572_0_6_line_61 |  | 45 | 94 | 0.03647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_261-572_0_6_line_62 |  | 46 | 95 | 0.002243 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_261-572_0_6_line_63 |  | 48 | 49 | 0.003796 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_261-572_0_6_line_64 |  | 48 | 50 | 0.018554 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_261-572_0_6_line_65 |  | 49 | 51 | 0.025838 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_261-572_0_6_line_66 |  | 51 | 96 | 0.0079665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_261-572_0_6_line_67 |  | 52 | 54 | 0.0093382 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
68 | LV_261-572_0_6_line_68 |  | 53 | 96 | 0.012997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_261-572_0_6_line_69 |  | 54 | 84 | 0.014352 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
70 | LV_261-572_0_6_line_70 |  | 56 | 85 | 0.013696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
71 | LV_261-572_0_6_line_71 |  | 57 | 58 | 0.012714 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_261-572_0_6_line_72 |  | 57 | 59 | 0.008341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_261-572_0_6_line_73 |  | 57 | 60 | 0.028269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_261-572_0_6_line_74 |  | 58 | 97 | 0.021909 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_261-572_0_6_line_75 |  | 59 | 61 | 0.039726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_261-572_0_6_line_76 |  | 59 | 62 | 0.0081343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
77 | LV_261-572_0_6_line_77 |  | 59 | 63 | 0.01294 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
78 | LV_261-572_0_6_line_78 |  | 60 | 98 | 0.017843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_261-572_0_6_line_79 |  | 61 | 99 | 0.013497 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_261-572_0_6_line_80 |  | 62 | 67 | 0.018198 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
81 | LV_261-572_0_6_line_81 |  | 62 | 68 | 0.0053614 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_261-572_0_6_line_82 |  | 63 | 78 | 0.028539 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
83 | LV_261-572_0_6_line_83 |  | 64 | 65 | 0.035721 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_261-572_0_6_line_84 |  | 64 | 66 | 0.015834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_261-572_0_6_line_85 |  | 65 | 102 | 0.0079788 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_261-572_0_6_line_86 |  | 66 | 97 | 0.0080083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_261-572_0_6_line_87 |  | 67 | 103 | 0.004612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_261-572_0_6_line_88 |  | 67 | 69 | 0.004074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
89 | LV_261-572_0_6_line_89 |  | 69 | 70 | 0.00372 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_261-572_0_6_line_90 |  | 69 | 71 | 0.01743 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
91 | LV_261-572_0_6_line_91 |  | 70 | 104 | 0.014131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_261-572_0_6_line_92 |  | 73 | 105 | 0.014154 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_261-572_0_6_line_93 |  | 74 | 108 | 0.01422 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
94 | LV_261-572_0_6_line_94 |  | 75 | 107 | 0.01419 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_261-572_0_6_line_95 |  | 76 | 77 | 0.015784 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_261-572_0_6_line_96 |  | 79 | 80 | 0.00564 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_261-572_0_6_line_97 |  | 80 | 119 | 0.0056556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_261-572_0_6_line_98 |  | 82 | 93 | 0.026952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_261-572_0_6_line_99 |  | 83 | 107 | 0.014226 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_261-572_0_6_line_100 |  | 87 | 108 | 0.014165 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
101 | LV_261-572_0_6_line_101 |  | 88 | 89 | 0.003995 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_261-572_0_6_line_102 |  | 88 | 90 | 0.024862 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_261-572_0_6_line_103 |  | 89 | 91 | 0.016299 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_261-572_0_6_line_104 |  | 90 | 111 | 0.010009 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_261-572_0_6_line_105 |  | 91 | 114 | 0.017808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_261-572_0_6_line_106 |  | 91 | 115 | 0.012715 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_261-572_0_6_line_107 |  | 92 | 93 | 0.029533 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_261-572_0_6_line_108 |  | 98 | 113 | 0.016353 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_261-572_0_6_line_109 |  | 99 | 117 | 0.0023963 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_261-572_0_6_line_110 |  | 100 | 101 | 0.021937 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_261-572_0_6_line_111 |  | 101 | 104 | 0.0053353 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_261-572_0_6_line_112 |  | 102 | 120 | 0.014679 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_261-572_0_6_line_113 |  | 105 | 106 | 0.014241 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_261-572_0_6_line_114 |  | 109 | 110 | 0.014688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_261-572_0_6_line_115 |  | 110 | 120 | 0.0079935 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_261-572_0_6_line_116 |  | 111 | 112 | 0.016143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_261-572_0_6_line_117 |  | 112 | 113 | 0.0080923 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_261-572_0_6_line_118 |  | 115 | 118 | 0.016976 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_261-572_0_6_line_119 |  | 116 | 117 | 0.024726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-572_0_6_trafo_20 | 0.63 MVA 20/0.4 kV | 121 | 27 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21
0 | 2681345.8653 | 1246753.7833 | 2681340.3669 | 1246767.0507
1 | 2681345.8653 | 1246753.7833 | 2681351.3074 | 1246740.6516
2 | 2681336.1399 | 1246777.2501 | 2681340.3669 | 1246767.0507
3 | 2681334.9363 | 1246780.1802 | 2681336.1399 | 1246777.2501
4 | 2681336.1399 | 1246777.2501 | 2681362.1347 | 1246787.6252
5 | 2681331.1193 | 1246778.6823 | 2681334.9363 | 1246780.1802
6 | 2681334.9363 | 1246780.1802 | 2681349.983 | 1246786.0851
7 | 2681375.4288 | 1246792.9313 | 2681362.1347 | 1246787.6252
8 | 2681331.1193 | 1246778.6823 | 2681323.9964 | 1246796.0181
9 | 2681331.2377 | 1246778.3988 | 2681331.1193 | 1246778.6823
10 | 2681372.9088 | 1246795.0821 | 2681349.983 | 1246786.0851
11 | 2681375.4288 | 1246792.9313 | 2681388.7372 | 1246798.243
12 | 2681491.4398 | 1246851.625 | 2681494.6061 | 1246853.1918 | 2681499.7459 | 1246844.1892
13 | 2681499.7459 | 1246844.1892 | 2681497.8407 | 1246843.2068 | 2681500.2064 | 1246838.7044
14 | 2681491.4398 | 1246851.625 | 2681477.8569 | 1246844.4998 | 2681479.1064 | 1246842.0819
15 | 2681491.4398 | 1246851.625 | 2681483.0378 | 1246865.4181
16 | 2681506.8794 | 1246826.0044 | 2681500.2064 | 1246838.7044
17 | 2681451.0766 | 1246737.3315 | 2681446.8118 | 1246748.0137
18 | 2681444.0366 | 1246734.5328 | 2681447.5454 | 1246735.9265 | 2681451.0766 | 1246737.3315
19 | 2681446.8118 | 1246748.0137 | 2681441.4922 | 1246761.3375
20 | 2681444.0366 | 1246734.5328 | 2681439.7986 | 1246745.2388
21 | 2681444.0366 | 1246734.5328 | 2681411.9172 | 1246721.7794
22 | 2681525.9718 | 1246871.2917 | 2681526.8572 | 1246871.7264 | 2681528.628 | 1246872.5958 | 2681530.3169 | 1246873.3863 | 2681534.4599 | 1246875.3446
23 | 2681534.4599 | 1246875.3446 | 2681530.0824 | 1246881.6446 | 2681515.5361 | 1246902.3988
24 | 2681525.9718 | 1246871.2917 | 2681522.5899 | 1246876.2079
25 | 2681525.9718 | 1246871.2917 | 2681532.8975 | 1246857.6988
26 | 2681500.9958 | 1246923.1445 | 2681515.5361 | 1246902.3988
27 | 2681373.8179 | 1246894.13 | 2681375.9025 | 1246895.8043 | 2681376.4454 | 1246896.9793 | 2681376.6168 | 1246898.2492 | 2681376.3163 | 1246899.7795
28 | 2681373.8179 | 1246894.13 | 2681376.9493 | 1246889.4362 | 2681380.5126 | 1246884.1035
29 | 2681373.8179 | 1246894.13 | 2681361.594 | 1246884.3107 | 2681357.5624 | 1246880.7938
30 | 2681376.3163 | 1246899.7795 | 2681379.3108 | 1246901.2106 | 2681383.4008 | 1246903.1792 | 2681363.6536 | 1246925.2244
31 | 2681376.3163 | 1246899.7795 | 2681375.4974 | 1246901.1026 | 2681369.4969 | 1246908.0639
32 | 2681380.5126 | 1246884.1035 | 2681382.2636 | 1246883.6716 | 2681383.9231 | 1246882.7493 | 2681385.256 | 1246881.3999
33 | 2681380.5126 | 1246884.1035 | 2681378.7001 | 1246884.0674 | 2681376.9697 | 1246883.5544 | 2681375.0056 | 1246882.4489 | 2681359.5853 | 1246871.5961 | 2681358.2528 | 1246870.2662
34 | 2681342.449 | 1246866.211 | 2681342.6292 | 1246866.4153 | 2681352.4122 | 1246876.3012 | 2681357.5624 | 1246880.7938
35 | 2681413.0654 | 1246810.8411 | 2681414.5034 | 1246807.3472
36 | 2681413.0654 | 1246810.8411 | 2681411.4479 | 1246814.7551
37 | 2681414.5034 | 1246807.3472 | 2681414.9662 | 1246806.653 | 2681415.7902 | 1246805.508 | 2681416.5048 | 1246804.0834 | 2681418.7866 | 1246798.319
38 | 2681414.5034 | 1246807.3472 | 2681418.1242 | 1246808.8313 | 2681422.6014 | 1246810.6608
39 | 2681414.5034 | 1246807.3472 | 2681413.2401 | 1246807.4744 | 2681412.2727 | 1246807.5056 | 2681411.2115 | 1246807.213 | 2681388.7372 | 1246798.243
40 | 2681411.4479 | 1246814.7551 | 2681407.1558 | 1246825.7936
41 | 2681363.6536 | 1246925.2244 | 2681367.7232 | 1246928.6828 | 2681380.8501 | 1246939.8488
42 | 2681350.2548 | 1246928.3312 | 2681359.7449 | 1246917.7542 | 2681362.5012 | 1246916.1798 | 2681369.4969 | 1246908.0639
43 | 2681422.6014 | 1246810.6608 | 2681422.4884 | 1246809.5362 | 2681422.8021 | 1246808.1506 | 2681425.6394 | 1246801.044
44 | 2681422.6014 | 1246810.6608 | 2681423.5294 | 1246812.397 | 2681424.9287 | 1246813.3725 | 2681445.5131 | 1246824.2804
45 | 2681430.9557 | 1246787.7282 | 2681425.6394 | 1246801.044
46 | 2681445.5131 | 1246824.2804 | 2681458.1735 | 1246830.9893
47 | 2681531.9653 | 1246778.2616 | 2681534.7304 | 1246777.6992 | 2681565.3816 | 1246793.9436
48 | 2681565.3816 | 1246793.9436 | 2681549.3232 | 1246825.4607
49 | 2681531.9653 | 1246778.2616 | 2681526.7565 | 1246788.1749
50 | 2681531.9653 | 1246778.2616 | 2681522.7905 | 1246773.5988 | 2681522.4178 | 1246771.5811 | 2681507.2649 | 1246763.6643
51 | 2681549.3232 | 1246825.4607 | 2681539.1151 | 1246845.4958
52 | 2681439.7986 | 1246745.2388 | 2681434.5189 | 1246758.5763
53 | 2681398.4631 | 1246716.4372 | 2681411.9172 | 1246721.7794
54 | 2681526.7565 | 1246788.1749 | 2681520.0827 | 1246800.8764
55 | 2681507.2649 | 1246763.6643 | 2681493.439 | 1246756.4408
56 | 2681407.1558 | 1246825.7936 | 2681399.4236 | 1246845.679
57 | 2681414.4357 | 1246969.0088 | 2681415.7455 | 1246967.6925 | 2681416.7053 | 1246966.5604 | 2681418.5826 | 1246964.0843 | 2681423.0586 | 1246958.842 | 2681428.207 | 1246953.0529 | 2681430.7032 | 1246950.0627 | 2681435.0812 | 1246944.8079 | 2681438.2544 | 1246946.9753 | 2681442.3423 | 1246941.9499 | 2681447.7524 | 1246950.0968 | 2681458.6822 | 1246952.3708 | 2681461.2442 | 1246952.8397 | 2681463.8562 | 1246952.9645 | 2681466.6342 | 1246952.558 | 2681470.2365 | 1246951.5289 | 2681476.8898 | 1246950.0192 | 2681477.4929 | 1246947.3589 | 2681478.3789 | 1246945.0027 | 2681480.4466 | 1246941.3173 | 2681481.4942 | 1246939.8417 | 2681486.4297 | 1246942.9451
58 | 2681486.4297 | 1246942.9451 | 2681499.1529 | 1246925.774 | 2681500.9958 | 1246923.1445
59 | 2681405.6702 | 1246961.5052 | 2681414.4357 | 1246969.0088
60 | 2681414.4357 | 1246969.0088 | 2681414.5868 | 1246970.6565 | 2681415.2208 | 1246971.2434
61 | 2681358.5256 | 1246968.4161 | 2681362.2419 | 1246964.2335 | 2681362.708 | 1246962.194 | 2681377.7058 | 1246943.8308 | 2681380.8501 | 1246939.8488 | 2681380.8501 | 1246939.8488
62 | 2681405.6702 | 1246961.5052 | 2681404.0294 | 1246959.9705
63 | 2681459.5795 | 1246904.6705 | 2681462.5843 | 1246907.0024
64 | 2681459.5795 | 1246904.6705 | 2681458.9148 | 1246902.4709 | 2681457.7781 | 1246900.5316 | 2681447.26 | 1246891.2794
65 | 2681462.5843 | 1246907.0024 | 2681467.8232 | 1246895.1768 | 2681468.5552 | 1246889.1936 | 2681472.1322 | 1246883.3214
66 | 2681476.2765 | 1246876.5178 | 2681472.1322 | 1246883.3214
67 | 2681479.1064 | 1246842.0819 | 2681470.8551 | 1246837.7094
68 | 2681476.2765 | 1246876.5178 | 2681483.0378 | 1246865.4181
69 | 2681470.8551 | 1246837.7094 | 2681458.1735 | 1246830.9893
70 | 2681532.8975 | 1246857.6988 | 2681539.1151 | 1246845.4958
71 | 2681309.0316 | 1246829.2497 | 2681303.4037 | 1246823.1904 | 2681300.3709 | 1246819.9422
72 | 2681309.0316 | 1246829.2497 | 2681314.6962 | 1246835.3874
73 | 2681309.0316 | 1246829.2497 | 2681292.0725 | 1246851.8667
74 | 2681300.3709 | 1246819.9422 | 2681288.5436 | 1246807.2751 | 2681285.3793 | 1246803.9663
75 | 2681314.6962 | 1246835.3874 | 2681308.5111 | 1246836.9037 | 2681288.4356 | 1246863.5446
76 | 2681314.6962 | 1246835.3874 | 2681317.8387 | 1246832.6396 | 2681320.8207 | 1246830.0341
77 | 2681314.6962 | 1246835.3874 | 2681323.4748 | 1246844.8947
78 | 2681281.3678 | 1246866.1426 | 2681292.0725 | 1246851.8667
79 | 2681280.313 | 1246874.3236 | 2681288.4356 | 1246863.5446
80 | 2681321.1585 | 1246813.6713 | 2681318.0327 | 1246821.2562 | 2681317.466 | 1246822.9163 | 2681317.4045 | 1246824.6501 | 2681317.8275 | 1246826.3015 | 2681318.7065 | 1246827.7591 | 2681320.8207 | 1246830.0341
81 | 2681320.8207 | 1246830.0341 | 2681324.471 | 1246833.9609
82 | 2681323.4748 | 1246844.8947 | 2681326.4051 | 1246848.0683 | 2681336.842 | 1246859.8534 | 2681342.449 | 1246866.211
83 | 2681269.2563 | 1246786.4178 | 2681245.5902 | 1246813.174
84 | 2681269.2563 | 1246786.4178 | 2681273.7602 | 1246791.8168 | 2681279.8443 | 1246798.1786
85 | 2681245.5902 | 1246813.174 | 2681240.304 | 1246819.1504
86 | 2681279.8443 | 1246798.1786 | 2681285.3793 | 1246803.9663
87 | 2681321.1585 | 1246813.6713 | 2681322.9131 | 1246809.4061
88 | 2681317.3721 | 1246812.1405 | 2681321.1585 | 1246813.6713
89 | 2681317.3721 | 1246812.1405 | 2681313.9164 | 1246810.7365
90 | 2681317.3721 | 1246812.1405 | 2681323.9964 | 1246796.0181
91 | 2681313.9164 | 1246810.7365 | 2681312.7111 | 1246811.5873 | 2681311.3073 | 1246812.0461 | 2681309.834 | 1246812.0593 | 2681308.2845 | 1246811.571 | 2681306.9834 | 1246810.5969 | 2681302.4152 | 1246806.0356
92 | 2681429.3093 | 1246771.7367 | 2681434.5189 | 1246758.5763
93 | 2681513.4938 | 1246813.4161 | 2681506.8794 | 1246826.0044
94 | 2681441.4922 | 1246761.3375 | 2681436.2307 | 1246774.5161
95 | 2681479.4257 | 1246749.1772 | 2681481.4126 | 1246750.1575 | 2681493.439 | 1246756.4408
96 | 2681335.5909 | 1246767.9756 | 2681333.4173 | 1246773.18
97 | 2681333.4173 | 1246773.18 | 2681331.2377 | 1246778.3988
98 | 2681350.2548 | 1246928.3312 | 2681332.2556 | 1246948.3918
99 | 2681430.9557 | 1246787.7282 | 2681436.2307 | 1246774.5161
100 | 2681520.0827 | 1246800.8764 | 2681513.4938 | 1246813.4161
101 | 2681236.0615 | 1246926.4875 | 2681239.1234 | 1246929.0647
102 | 2681236.0615 | 1246926.4875 | 2681251.0115 | 1246906.6221
103 | 2681251.6251 | 1246939.5658 | 2681239.1234 | 1246929.0647
104 | 2681251.0115 | 1246906.6221 | 2681251.881 | 1246905.4667 | 2681257.0181 | 1246898.6158
105 | 2681251.6251 | 1246939.5658 | 2681258.9332 | 1246946.4932 | 2681262.5509 | 1246947.0988 | 2681265.5722 | 1246949.8755
106 | 2681251.6251 | 1246939.5658 | 2681256.7557 | 1246931.7526 | 2681258.7688 | 1246929.0524
107 | 2681312.5323 | 1246970.374 | 2681332.2556 | 1246948.3918
108 | 2681281.3678 | 1246866.1426 | 2681271.5575 | 1246879.2258
109 | 2681278.8709 | 1246876.2374 | 2681280.313 | 1246874.3236
110 | 2681298.5651 | 1246806.9455 | 2681295.5202 | 1246803.6792 | 2681283.6557 | 1246790.8545
111 | 2681298.5651 | 1246806.9455 | 2681301.0216 | 1246804.6442 | 2681302.4152 | 1246806.0356
112 | 2681230.5785 | 1246830.1458 | 2681240.304 | 1246819.1504
113 | 2681429.3093 | 1246771.7367 | 2681424.0678 | 1246784.9777
114 | 2681225.2826 | 1246836.1332 | 2681215.5515 | 1246847.1349
115 | 2681230.5785 | 1246830.1458 | 2681225.2826 | 1246836.1332
116 | 2681266.7028 | 1246885.7001 | 2681257.0181 | 1246898.6158
117 | 2681266.7028 | 1246885.7001 | 2681271.5575 | 1246879.2258
118 | 2681269.19 | 1246915.7669 | 2681266.6286 | 1246920.2128 | 2681260.719 | 1246926.4364 | 2681258.7688 | 1246929.0524
119 | 2681278.8709 | 1246876.2374 | 2681263.9903 | 1246895.9844

## bus_geodata
| x | y | coords
0 | 2681345.8653 | 1246753.7833
1 | 2681340.3669 | 1246767.0507
2 | 2681351.3074 | 1246740.6516
3 | 2681336.1399 | 1246777.2501
4 | 2681334.9363 | 1246780.1802
5 | 2681362.1347 | 1246787.6252
6 | 2681331.1193 | 1246778.6823
7 | 2681349.983 | 1246786.0851
8 | 2681375.4288 | 1246792.9313
9 | 2681499.7459 | 1246844.1892
10 | 2681491.4398 | 1246851.625
11 | 2681500.2064 | 1246838.7044
12 | 2681451.0766 | 1246737.3315
13 | 2681446.8118 | 1246748.0137
14 | 2681444.0366 | 1246734.5328
15 | 2681534.4599 | 1246875.3446
16 | 2681525.9718 | 1246871.2917
17 | 2681515.5361 | 1246902.3988
18 | 2681373.8179 | 1246894.13
19 | 2681376.3163 | 1246899.7795
20 | 2681380.5126 | 1246884.1035
21 | 2681357.5624 | 1246880.7938
22 | 2681413.0654 | 1246810.8411
23 | 2681414.5034 | 1246807.3472
24 | 2681411.4479 | 1246814.7551
25 | 2681363.6536 | 1246925.2244
26 | 2681369.4969 | 1246908.0639
27 | 2681385.256 | 1246881.3999
28 | 2681358.2528 | 1246870.2662
29 | 2681418.7866 | 1246798.319
30 | 2681422.6014 | 1246810.6608
31 | 2681388.7372 | 1246798.243
32 | 2681425.6394 | 1246801.044
33 | 2681445.5131 | 1246824.2804
34 | 2681565.3816 | 1246793.9436
35 | 2681531.9653 | 1246778.2616
36 | 2681549.3232 | 1246825.4607
37 | 2681439.7986 | 1246745.2388
38 | 2681411.9172 | 1246721.7794
39 | 2681526.7565 | 1246788.1749
40 | 2681507.2649 | 1246763.6643
41 | 2681407.1558 | 1246825.7936
42 | 2681486.4297 | 1246942.9451
43 | 2681414.4357 | 1246969.0088
44 | 2681500.9958 | 1246923.1445
45 | 2681380.8501 | 1246939.8488
46 | 2681405.6702 | 1246961.5052
47 | 2681415.2208 | 1246971.2434
48 | 2681459.5795 | 1246904.6705
49 | 2681462.5843 | 1246907.0024
50 | 2681447.26 | 1246891.2794
51 | 2681472.1322 | 1246883.3214
52 | 2681479.1064 | 1246842.0819
53 | 2681483.0378 | 1246865.4181
54 | 2681470.8551 | 1246837.7094
55 | 2681522.5899 | 1246876.2079
56 | 2681532.8975 | 1246857.6988
57 | 2681309.0316 | 1246829.2497
58 | 2681300.3709 | 1246819.9422
59 | 2681314.6962 | 1246835.3874
60 | 2681292.0725 | 1246851.8667
61 | 2681288.4356 | 1246863.5446
62 | 2681320.8207 | 1246830.0342
63 | 2681323.4748 | 1246844.8947
64 | 2681269.2563 | 1246786.4178
65 | 2681245.5902 | 1246813.174
66 | 2681279.8443 | 1246798.1786
67 | 2681321.1585 | 1246813.6713
68 | 2681324.471 | 1246833.9609
69 | 2681317.3721 | 1246812.1405
70 | 2681313.9164 | 1246810.7365
71 | 2681323.9964 | 1246796.0181
72 | 2681398.4631 | 1246716.4372
73 | 2681434.5189 | 1246758.5763
74 | 2681506.8794 | 1246826.0044
75 | 2681441.4922 | 1246761.3375
76 | 2681479.4257 | 1246749.1772
77 | 2681493.439 | 1246756.4408
78 | 2681342.449 | 1246866.211
79 | 2681335.5909 | 1246767.9756
80 | 2681333.4173 | 1246773.18
81 | 2681372.9088 | 1246795.0821
82 | 2681350.2548 | 1246928.3312
83 | 2681430.9557 | 1246787.7282
84 | 2681458.1735 | 1246830.9893
85 | 2681539.1151 | 1246845.4958
86 | 2681399.4236 | 1246845.6791
87 | 2681520.0827 | 1246800.8764
88 | 2681236.0615 | 1246926.4875
89 | 2681239.1234 | 1246929.0647
90 | 2681251.0115 | 1246906.6221
91 | 2681251.6251 | 1246939.5658
92 | 2681312.5323 | 1246970.374
93 | 2681332.2556 | 1246948.3918
94 | 2681358.5256 | 1246968.4161
95 | 2681404.0294 | 1246959.9705
96 | 2681476.2765 | 1246876.5178
97 | 2681285.3793 | 1246803.9663
98 | 2681281.3678 | 1246866.1426
99 | 2681280.313 | 1246874.3236
100 | 2681283.6557 | 1246790.8545
101 | 2681298.5651 | 1246806.9455
102 | 2681240.304 | 1246819.1504
103 | 2681322.9131 | 1246809.4061
104 | 2681302.4152 | 1246806.0356
105 | 2681429.3093 | 1246771.7367
106 | 2681424.0678 | 1246784.9777
107 | 2681436.2307 | 1246774.5161
108 | 2681513.4938 | 1246813.4161
109 | 2681215.5515 | 1246847.1349
110 | 2681225.2826 | 1246836.1332
111 | 2681257.0181 | 1246898.6158
112 | 2681266.7028 | 1246885.7001
113 | 2681271.5575 | 1246879.2258
114 | 2681265.5722 | 1246949.8755
115 | 2681258.7688 | 1246929.0524
116 | 2681263.9903 | 1246895.9844
117 | 2681278.8709 | 1246876.2374
118 | 2681269.19 | 1246915.7669
119 | 2681331.2377 | 1246778.3988
120 | 2681230.5785 | 1246830.1458
121 | 2681388.9179 | 1246882.6399

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98764 | -0.23563 | 0.0039625 | 0.00099309
1 | 0.98775 | -0.23361 | 0.0040227 | 0.0010082
2 | 0.98759 | -0.23664 | 0.0039421 | 0.00098798
3 | 0.98787 | -0.23125 | 0 | 0
4 | 0.98804 | -0.22802 | 0 | 0
5 | 0.98644 | -0.25871 | 0.0040267 | 0.0010092
6 | 0.98826 | -0.22371 | 0 | 0
7 | 0.9879 | -0.23064 | 0.0058953 | 0.0014775
8 | 0.98572 | -0.27258 | 0.0039236 | 0.00098334
9 | 0.97965 | -0.39051 | 0 | 0
10 | 0.98003 | -0.38316 | 0 | 0
11 | 0.97946 | -0.39433 | 0.0043444 | 0.0010888
12 | 0.9812 | -0.36053 | 0 | 0
13 | 0.98142 | -0.35631 | 0.003259 | 0.00081679
14 | 0.98106 | -0.36331 | 0 | 0
15 | 0.9753 | -0.47567 | 0 | 0
16 | 0.97545 | -0.47282 | 0 | 0
17 | 0.97479 | -0.4857 | 0.0062309 | 0.0015616
18 | 0.99835 | -0.031238 | 0 | 0
19 | 0.9978 | -0.041857 | 0 | 0
20 | 0.99947 | -0.010098 | 0 | 0
21 | 0.99674 | -0.061644 | 0.0042276 | 0.0010595
22 | 0.98365 | -0.31265 | 0 | 0
23 | 0.98367 | -0.31226 | 0 | 0
24 | 0.98363 | -0.31309 | 0 | 0
25 | 0.99537 | -0.088464 | 0 | 0
26 | 0.99762 | -0.045297 | 0.0038337 | 0.00096081
27 | 1 | 0 | -0.52748 | -0.13472
28 | 0.99907 | -0.017696 | 0.016359 | 0.0040999
29 | 0.98364 | -0.31285 | 0.0032537 | 0.00081545
30 | 0.98326 | -0.32025 | 0 | 0
31 | 0.98501 | -0.28628 | 0.004029 | 0.0010098
32 | 0.98291 | -0.32714 | 0.0043571 | 0.001092
33 | 0.98218 | -0.34127 | 0.0043064 | 0.0010793
34 | 0.97704 | -0.4416 | 0 | 0
35 | 0.97778 | -0.42705 | 0 | 0
36 | 0.97634 | -0.45535 | 0.0076694 | 0.0019221
37 | 0.98092 | -0.36599 | 0.0032895 | 0.00082444
38 | 0.98082 | -0.36793 | 0.0032933 | 0.00082537
39 | 0.97803 | -0.42216 | 0.0062976 | 0.0015783
40 | 0.97742 | -0.43417 | 0.0062584 | 0.0015685
41 | 0.98357 | -0.3143 | 0.0031817 | 0.00079741
42 | 0.9741 | -0.49931 | 0 | 0
43 | 0.97189 | -0.5429 | 0 | 0
44 | 0.97443 | -0.49282 | 0.0046946 | 0.0011766
45 | 0.99391 | -0.11666 | 0.052158 | 0.013072
46 | 0.97188 | -0.5432 | 0 | 0
47 | 0.97173 | -0.54618 | 0.070494 | 0.017668
48 | 0.97744 | -0.43399 | 0 | 0
49 | 0.97754 | -0.43189 | 0 | 0
50 | 0.97692 | -0.44426 | 0.030342 | 0.0076044
51 | 0.97827 | -0.4176 | 0.0076581 | 0.0019193
52 | 0.98071 | -0.36986 | 0 | 0
53 | 0.97917 | -0.39998 | 0.0061235 | 0.0015347
54 | 0.98106 | -0.363 | 0.0043213 | 0.001083
55 | 0.97544 | -0.47305 | 0.0021389 | 0.00053606
56 | 0.97569 | -0.46807 | 0.0068488 | 0.0017165
57 | 0.99161 | -0.15961 | 0 | 0
58 | 0.99145 | -0.16273 | 0.0024377 | 0.00061095
59 | 0.99207 | -0.15076 | 0 | 0
60 | 0.99041 | -0.18273 | 0.0022625 | 0.00056704
61 | 0.99131 | -0.16536 | 0.0037 | 0.00092732
62 | 0.99158 | -0.15997 | 0 | 0
63 | 0.99302 | -0.13243 | 0.0032533 | 0.00081537
64 | 0.99103 | -0.17083 | 0 | 0
65 | 0.99076 | -0.17599 | 0.0016326 | 0.00040916
66 | 0.99115 | -0.16854 | 0.0016291 | 0.00040828
67 | 0.99052 | -0.18028 | 0 | 0
68 | 0.99156 | -0.16045 | 0.0050391 | 0.0012629
69 | 0.99029 | -0.18479 | 0 | 0
70 | 0.99026 | -0.18526 | 0 | 0
71 | 0.9893 | -0.20365 | 0.0040349 | 0.0010113
72 | 0.98077 | -0.369 | 0.0040887 | 0.0010247
73 | 0.9808 | -0.36848 | 0.0031647 | 0.00079315
74 | 0.97908 | -0.4017 | 0.0046248 | 0.0011591
75 | 0.98173 | -0.35021 | 0.0031613 | 0.00079231
76 | 0.97727 | -0.4371 | 0.0032513 | 0.00081485
77 | 0.97732 | -0.43617 | 0.0037615 | 0.00094273
78 | 0.99515 | -0.091813 | 0.0050256 | 0.0012595
79 | 0.98823 | -0.22422 | 0.0016323 | 0.0004091
80 | 0.98824 | -0.22405 | 0.0015611 | 0.00039126
81 | 0.98783 | -0.23203 | 0.0031768 | 0.00079618
82 | 0.99725 | -0.052407 | 0.0040313 | 0.0010104
83 | 0.98247 | -0.33569 | 0.0031851 | 0.00079825
84 | 0.98162 | -0.35223 | 0.004276 | 0.0010717
85 | 0.97592 | -0.46347 | 0.0068426 | 0.0017149
86 | 0.98352 | -0.31528 | 0.0025267 | 0.00063325
87 | 0.97837 | -0.41558 | 0.0060974 | 0.0015281
88 | 0.98717 | -0.24553 | 0 | 0
89 | 0.98705 | -0.24784 | 0 | 0
90 | 0.98791 | -0.23117 | 0.0025099 | 0.00062904
91 | 0.98657 | -0.25728 | 0 | 0
92 | 0.99682 | -0.060603 | 0.0063259 | 0.0015854
93 | 0.99699 | -0.057327 | 0.0040847 | 0.0010237
94 | 0.99329 | -0.12873 | 0.018747 | 0.0046984
95 | 0.97187 | -0.54326 | 0.001394 | 0.00034937
96 | 0.97855 | -0.41209 | 0.013209 | 0.0033106
97 | 0.99122 | -0.16715 | 0.0016157 | 0.00040493
98 | 0.98969 | -0.19663 | 0.0029355 | 0.0007357
99 | 0.9911 | -0.16944 | 0.0071432 | 0.0017903
100 | 0.99006 | -0.18915 | 0.0043523 | 0.0010908
101 | 0.99015 | -0.18745 | 0 | 0
102 | 0.99071 | -0.17691 | 0.0016202 | 0.00040605
103 | 0.99051 | -0.18055 | 0.0033003 | 0.00082714
104 | 0.99017 | -0.18704 | 0.0027329 | 0.00068492
105 | 0.98071 | -0.37012 | 0.0032038 | 0.00080295
106 | 0.98067 | -0.37095 | 0.003207 | 0.00080376
107 | 0.98208 | -0.34337 | 0.0032016 | 0.00080239
108 | 0.97872 | -0.40877 | 0.0046245 | 0.001159
109 | 0.9906 | -0.17907 | 0.0016264 | 0.00040762
110 | 0.99062 | -0.17865 | 0.00164 | 0.00041104
111 | 0.98823 | -0.22494 | 0.0025231 | 0.00063235
112 | 0.98879 | -0.21418 | 0.0017446 | 0.00043724
113 | 0.98908 | -0.20854 | 0.0017672 | 0.00044291
114 | 0.98644 | -0.2597 | 0.0076081 | 0.0019068
115 | 0.98628 | -0.26291 | 0.0074774 | 0.001874
116 | 0.99094 | -0.17258 | 0.0062058 | 0.0015553
117 | 0.99108 | -0.16986 | 0.0036857 | 0.00092372
118 | 0.98601 | -0.26816 | 0.017248 | 0.0043228
119 | 0.98826 | -0.22373 | 0.0016428 | 0.00041172
120 | 0.99065 | -0.17818 | 0.0016196 | 0.0004059
121 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0079048 | -0.001981 | 0.0079055 | 0.0019813 | 7.6388e-07 | 3.0508e-07 | 0.01191 | 0.011909 | 0.01191 | 0.98764 | -0.23563 | 0.98775 | -0.23361 | 3.2719
1 | 0.0039423 | 0.00098792 | -0.0039421 | -0.00098798 | 1.8805e-07 | -6.1542e-08 | 0.0059396 | 0.0059396 | 0.0059396 | 0.98764 | -0.23563 | 0.98759 | -0.23664 | 1.6318
2 | -0.011928 | -0.0029895 | 0.01193 | 0.0029902 | 1.3369e-06 | 7.1429e-07 | 0.01797 | 0.01797 | 0.01797 | 0.98775 | -0.23361 | 0.98787 | -0.23125 | 4.9367
3 | -0.28884 | -0.073423 | 0.28889 | 0.073452 | 4.5039e-05 | 2.8622e-05 | 0.43545 | 0.43545 | 0.43545 | 0.98787 | -0.23125 | 0.98804 | -0.22802 | 23.9259
4 | 0.27691 | 0.070433 | -0.27655 | -0.0702 | 0.00036586 | 0.00023236 | 0.41748 | 0.41748 | 0.41748 | 0.98787 | -0.23125 | 0.98644 | -0.25871 | 22.9386
5 | -0.29796 | -0.075726 | 0.29802 | 0.075765 | 6.1873e-05 | 3.9337e-05 | 0.44912 | 0.44912 | 0.44912 | 0.98804 | -0.22802 | 0.98826 | -0.22371 | 24.6767
6 | 0.0090734 | 0.002274 | -0.0090723 | -0.0022735 | 1.1319e-06 | 5.1741e-07 | 0.013665 | 0.013665 | 0.013665 | 0.98804 | -0.22802 | 0.9879 | -0.23064 | 3.7541
7 | 0.27252 | 0.069191 | -0.27234 | -0.069076 | 0.0001817 | 0.00011538 | 0.41141 | 0.41141 | 0.41141 | 0.98644 | -0.25871 | 0.98572 | -0.27258 | 22.6048
8 | -0.30286 | -0.076977 | 0.30315 | 0.077163 | 0.0002928 | 0.00018619 | 0.4564 | 0.4564 | 0.4564 | 0.98826 | -0.22371 | 0.9893 | -0.20365 | 25.0768
9 | 0.0048363 | 0.001212 | -0.0048363 | -0.001212 | 6.1104e-09 | -2.6576e-11 | 0.007282 | 0.007282 | 0.007282 | 0.98826 | -0.22371 | 0.98826 | -0.22373 | 2.0005
10 | 0.003177 | 0.000796 | -0.0031768 | -0.00079618 | 2.1148e-07 | -1.7996e-07 | 0.0047853 | 0.0047854 | 0.0047854 | 0.9879 | -0.23064 | 0.98783 | -0.23203 | 1.3147
11 | 0.26842 | 0.068092 | -0.26824 | -0.06798 | 0.0001767 | 0.00011217 | 0.40549 | 0.40549 | 0.40549 | 0.98572 | -0.27258 | 0.98501 | -0.28628 | 22.2794
12 | -0.1463 | -0.036924 | 0.14635 | 0.036956 | 5.1518e-05 | 3.2096e-05 | 0.22231 | 0.22231 | 0.22231 | 0.97965 | -0.39051 | 0.98003 | -0.38316 | 12.2146
13 | 0.1463 | 0.036924 | -0.14627 | -0.036907 | 2.6797e-05 | 1.6695e-05 | 0.22231 | 0.22231 | 0.22231 | 0.97965 | -0.39051 | 0.97946 | -0.39433 | 12.2146
14 | -0.20381 | -0.051403 | 0.20393 | 0.051485 | 0.0001298 | 8.1933e-05 | 0.30956 | 0.30956 | 0.30956 | 0.98003 | -0.38316 | 0.98071 | -0.36986 | 17.0089
15 | 0.057457 | 0.014448 | -0.057411 | -0.014418 | 4.6113e-05 | 2.9309e-05 | 0.087257 | 0.087257 | 0.087257 | 0.98003 | -0.38316 | 0.97917 | -0.39998 | 23.9716
16 | 0.14193 | 0.035818 | -0.14187 | -0.035787 | 5.0064e-05 | 3.1139e-05 | 0.21571 | 0.21571 | 0.21571 | 0.97946 | -0.39433 | 0.97908 | -0.4017 | 11.852
17 | -0.020255 | -0.0050781 | 0.020259 | 0.0050805 | 4.07e-06 | 2.4595e-06 | 0.030718 | 0.030718 | 0.030718 | 0.9812 | -0.36053 | 0.98142 | -0.35631 | 8.439
18 | 0.020255 | 0.0050781 | -0.020252 | -0.0050765 | 2.6807e-06 | 1.62e-06 | 0.030718 | 0.030718 | 0.030718 | 0.9812 | -0.36053 | 0.98106 | -0.36331 | 8.439
19 | -0.023518 | -0.0058973 | 0.023525 | 0.0059015 | 6.8409e-06 | 4.1969e-06 | 0.035659 | 0.035659 | 0.035659 | 0.98142 | -0.35631 | 0.98173 | -0.35021 | 9.7965
20 | 0.012869 | 0.0032258 | -0.012867 | -0.0032249 | 1.645e-06 | 9.0742e-07 | 0.019518 | 0.019519 | 0.019519 | 0.98106 | -0.36331 | 0.98092 | -0.36599 | 5.3622
21 | 0.0073838 | 0.0018507 | -0.0073822 | -0.00185 | 1.6255e-06 | 6.0404e-07 | 0.011199 | 0.0112 | 0.0112 | 0.98106 | -0.36331 | 0.98082 | -0.36793 | 3.0768
22 | -0.083063 | -0.020905 | 0.083074 | 0.020912 | 1.1336e-05 | 6.6679e-06 | 0.12676 | 0.12676 | 0.12676 | 0.9753 | -0.47567 | 0.97545 | -0.47282 | 6.9649
23 | 0.083063 | 0.020905 | -0.083023 | -0.020882 | 3.9788e-05 | 2.3405e-05 | 0.12676 | 0.12676 | 0.12676 | 0.9753 | -0.47567 | 0.97479 | -0.4857 | 6.9649
24 | 0.0021389 | 0.000536 | -0.0021389 | -0.00053606 | 2.3822e-08 | -5.924e-08 | 0.0032628 | 0.0032628 | 0.0032628 | 0.97545 | -0.47282 | 0.97544 | -0.47305 | 0.89639
25 | -0.085213 | -0.021448 | 0.085233 | 0.02146 | 1.9343e-05 | 1.1427e-05 | 0.13002 | 0.13002 | 0.13002 | 0.97545 | -0.47282 | 0.97569 | -0.46807 | 7.1441
26 | 0.076792 | 0.01932 | -0.076766 | -0.019305 | 2.6121e-05 | 1.5139e-05 | 0.11725 | 0.11725 | 0.11725 | 0.97479 | -0.4857 | 0.97443 | -0.49282 | 6.4423
27 | 0.089501 | 0.022554 | -0.089456 | -0.022525 | 4.5441e-05 | 2.8993e-05 | 0.13344 | 0.13344 | 0.13344 | 0.99835 | -0.031238 | 0.9978 | -0.041857 | 36.6601
28 | -0.50869 | -0.13012 | 0.50921 | 0.13045 | 0.00052107 | 0.00033269 | 0.75912 | 0.75912 | 0.75912 | 0.99835 | -0.031238 | 0.99947 | -0.010098 | 41.7099
29 | 0.41919 | 0.10757 | -0.41857 | -0.10717 | 0.00061744 | 0.00039379 | 0.62568 | 0.62568 | 0.62568 | 0.99835 | -0.031238 | 0.99674 | -0.061644 | 34.378
30 | 0.071169 | 0.017938 | -0.071011 | -0.017838 | 0.00015832 | 0.00010084 | 0.10617 | 0.10617 | 0.10617 | 0.9978 | -0.041857 | 0.99537 | -0.088464 | 29.1677
31 | 0.018287 | 0.0045863 | -0.018284 | -0.0045845 | 2.9974e-06 | 1.778e-06 | 0.027273 | 0.027273 | 0.027273 | 0.9978 | -0.041857 | 0.99762 | -0.045297 | 7.4925
32 | -0.52557 | -0.13456 | 0.52583 | 0.13472 | 0.00025717 | 0.00016422 | 0.78348 | 0.78348 | 0.78348 | 0.99947 | -0.010098 | 1 | 0 | 43.0486
33 | 0.016365 | 0.0041033 | -0.016359 | -0.0040999 | 5.9238e-06 | 3.4426e-06 | 0.024364 | 0.024365 | 0.024365 | 0.99947 | -0.010098 | 0.99907 | -0.017696 | 6.6935
34 | 0.41434 | 0.10611 | -0.41374 | -0.10573 | 0.00060462 | 0.00038559 | 0.61937 | 0.61937 | 0.61937 | 0.99674 | -0.061644 | 0.99515 | -0.091813 | 34.0312
35 | -0.0057089 | -0.0014305 | 0.0057091 | 0.0014306 | 1.0564e-07 | 1.9661e-08 | 0.0086361 | 0.0086361 | 0.0086361 | 0.98365 | -0.31265 | 0.98367 | -0.31226 | 2.3726
36 | 0.0057089 | 0.0014305 | -0.0057088 | -0.0014305 | 1.1842e-07 | 2.2043e-08 | 0.0086361 | 0.0086361 | 0.0086361 | 0.98365 | -0.31265 | 0.98363 | -0.31309 | 2.3726
37 | 0.0032538 | 0.00081538 | -0.0032537 | -0.00081545 | 9.1196e-08 | -6.9062e-08 | 0.004922 | 0.004922 | 0.004922 | 0.98367 | -0.31226 | 0.98364 | -0.31285 | 1.3522
38 | 0.25492 | 0.064515 | -0.25482 | -0.064454 | 9.7696e-05 | 6.197e-05 | 0.38584 | 0.38584 | 0.38584 | 0.98367 | -0.31226 | 0.98326 | -0.32025 | 21.2001
39 | -0.26388 | -0.066761 | 0.26421 | 0.066971 | 0.00032945 | 0.0002091 | 0.3994 | 0.3994 | 0.3994 | 0.98367 | -0.31226 | 0.98501 | -0.28628 | 21.945
40 | 0.0057088 | 0.0014305 | -0.0057085 | -0.0014305 | 3.3125e-07 | 6.1673e-08 | 0.0086361 | 0.0086362 | 0.0086362 | 0.98363 | -0.31309 | 0.98357 | -0.3143 | 2.3726
41 | 0.071011 | 0.017838 | -0.070915 | -0.017777 | 9.5422e-05 | 6.0777e-05 | 0.10617 | 0.10617 | 0.10617 | 0.99537 | -0.088464 | 0.99391 | -0.11666 | 29.1677
42 | 0.01445 | 0.0036237 | -0.014445 | -0.003621 | 4.8956e-06 | 2.7664e-06 | 0.021554 | 0.021555 | 0.021555 | 0.99762 | -0.045297 | 0.99725 | -0.052407 | 5.9216
43 | 0.037476 | 0.0094149 | -0.037463 | -0.0094072 | 1.231e-05 | 7.7489e-06 | 0.056722 | 0.056722 | 0.056722 | 0.98326 | -0.32025 | 0.98291 | -0.32714 | 15.5829
44 | 0.21734 | 0.055039 | -0.21713 | -0.0549 | 0.00021911 | 0.00013852 | 0.32912 | 0.32912 | 0.32912 | 0.98326 | -0.32025 | 0.98218 | -0.34127 | 18.0836
45 | 0.033106 | 0.0083152 | -0.033093 | -0.0083067 | 1.3509e-05 | 8.4643e-06 | 0.050125 | 0.050125 | 0.050125 | 0.98291 | -0.32714 | 0.98247 | -0.33569 | 13.7707
46 | 0.21282 | 0.053821 | -0.21271 | -0.05375 | 0.00011183 | 7.0667e-05 | 0.3226 | 0.3226 | 0.3226 | 0.98218 | -0.34127 | 0.98162 | -0.35223 | 17.7251
47 | -0.10672 | -0.026891 | 0.1068 | 0.026936 | 7.437e-05 | 4.5246e-05 | 0.16259 | 0.16259 | 0.16259 | 0.97704 | -0.4416 | 0.97778 | -0.42705 | 8.9334
48 | 0.10672 | 0.026891 | -0.10665 | -0.026848 | 7.013e-05 | 4.267e-05 | 0.16259 | 0.16259 | 0.16259 | 0.97704 | -0.4416 | 0.97634 | -0.45535 | 8.9335
49 | -0.12007 | -0.030265 | 0.1201 | 0.030282 | 2.8063e-05 | 1.7258e-05 | 0.18279 | 0.18279 | 0.18279 | 0.97778 | -0.42705 | 0.97803 | -0.42216 | 10.0435
50 | 0.013277 | 0.0033287 | -0.013272 | -0.0033262 | 4.5071e-06 | 2.5154e-06 | 0.020205 | 0.020205 | 0.020205 | 0.97778 | -0.42705 | 0.97742 | -0.43417 | 5.5509
51 | 0.098983 | 0.024926 | -0.098944 | -0.024903 | 3.8402e-05 | 2.3172e-05 | 0.1509 | 0.1509 | 0.1509 | 0.97634 | -0.45535 | 0.97592 | -0.46347 | 8.2912
52 | 0.0095773 | 0.0024005 | -0.0095762 | -0.0023999 | 1.1354e-06 | 5.4562e-07 | 0.014528 | 0.014529 | 0.014529 | 0.98092 | -0.36599 | 0.9808 | -0.36848 | 3.9914
53 | 0.0040889 | 0.0010247 | -0.0040887 | -0.0010247 | 2.089e-07 | -4.8997e-08 | 0.0062033 | 0.0062034 | 0.0062034 | 0.98082 | -0.36793 | 0.98077 | -0.369 | 1.7042
54 | -0.1264 | -0.031861 | 0.12644 | 0.031885 | 3.9824e-05 | 2.4587e-05 | 0.19237 | 0.19237 | 0.19237 | 0.97803 | -0.42216 | 0.97837 | -0.41558 | 10.57
55 | 0.0070136 | 0.0017577 | -0.007013 | -0.0017575 | 6.6692e-07 | 2.3134e-07 | 0.010677 | 0.010678 | 0.010678 | 0.97742 | -0.43417 | 0.97732 | -0.43617 | 2.9334
56 | 0.0025268 | 0.00063305 | -0.0025267 | -0.00063325 | 1.1692e-07 | -1.9595e-07 | 0.0038226 | 0.0038227 | 0.0038227 | 0.98357 | -0.3143 | 0.98352 | -0.31528 | 1.0502
57 | 0.072049 | 0.018116 | -0.071899 | -0.018024 | 0.00014965 | 9.2096e-05 | 0.11008 | 0.11008 | 0.11008 | 0.9741 | -0.49931 | 0.97189 | -0.5429 | 10.0809
58 | -0.072049 | -0.018116 | 0.072071 | 0.018129 | 2.2341e-05 | 1.2768e-05 | 0.11008 | 0.11008 | 0.11008 | 0.9741 | -0.49931 | 0.97443 | -0.49282 | 6.0485
59 | 0.001394 | 0.00034921 | -0.001394 | -0.00034934 | 1.9676e-08 | -1.3015e-07 | 0.0021342 | 0.0021343 | 0.0021343 | 0.97189 | -0.5429 | 0.97188 | -0.5432 | 0.58634
60 | 0.070505 | 0.017675 | -0.070494 | -0.017668 | 1.1006e-05 | 7.0127e-06 | 0.10795 | 0.10795 | 0.10795 | 0.97189 | -0.5429 | 0.97173 | -0.54618 | 29.6563
61 | 0.018757 | 0.0047048 | -0.018747 | -0.0046984 | 1.0787e-05 | 6.4311e-06 | 0.028084 | 0.028084 | 0.028084 | 0.99391 | -0.11666 | 0.99329 | -0.12873 | 7.7154
62 | 0.001394 | 0.00034934 | -0.001394 | -0.00034937 | 3.8315e-09 | -2.5342e-08 | 0.0021343 | 0.0021343 | 0.0021343 | 0.97188 | -0.5432 | 0.97187 | -0.54326 | 0.58635
63 | -0.030357 | -0.0076137 | 0.03036 | 0.0076156 | 3.0405e-06 | 1.8983e-06 | 0.046216 | 0.046216 | 0.046216 | 0.97744 | -0.43399 | 0.97754 | -0.43189 | 12.6967
64 | 0.030357 | 0.0076137 | -0.030342 | -0.0076044 | 1.4861e-05 | 9.2789e-06 | 0.046216 | 0.046216 | 0.046216 | 0.97744 | -0.43399 | 0.97692 | -0.44426 | 12.6968
65 | -0.03036 | -0.0076156 | 0.030381 | 0.0076285 | 2.0695e-05 | 1.2921e-05 | 0.046216 | 0.046216 | 0.046216 | 0.97754 | -0.43189 | 0.97827 | -0.4176 | 12.6967
66 | -0.038039 | -0.0095478 | 0.038049 | 0.0095541 | 1.0003e-05 | 6.3017e-06 | 0.057865 | 0.057864 | 0.057865 | 0.97827 | -0.4176 | 0.97855 | -0.41209 | 15.8968
67 | -0.20393 | -0.051485 | 0.204 | 0.051528 | 6.7115e-05 | 4.2364e-05 | 0.30956 | 0.30956 | 0.30956 | 0.98071 | -0.36986 | 0.98106 | -0.363 | 17.0089
68 | 0.051288 | 0.012884 | -0.051258 | -0.012865 | 2.9615e-05 | 1.879e-05 | 0.077951 | 0.077951 | 0.077951 | 0.97917 | -0.39998 | 0.97855 | -0.41209 | 21.4151
69 | -0.20832 | -0.052611 | 0.20843 | 0.052678 | 0.00010756 | 6.7934e-05 | 0.31612 | 0.31612 | 0.31612 | 0.98106 | -0.363 | 0.98162 | -0.35223 | 17.369
70 | -0.092081 | -0.023176 | 0.092102 | 0.023188 | 2.0267e-05 | 1.2116e-05 | 0.14047 | 0.14047 | 0.14047 | 0.97569 | -0.46807 | 0.97592 | -0.46347 | 7.718
71 | 0.01383 | 0.0034677 | -0.013828 | -0.0034665 | 2.0536e-06 | 1.1503e-06 | 0.020754 | 0.020754 | 0.020754 | 0.99161 | -0.15961 | 0.99145 | -0.16273 | 5.7016
72 | -0.060103 | -0.015139 | 0.060128 | 0.015155 | 2.5458e-05 | 1.6186e-05 | 0.090217 | 0.090217 | 0.090217 | 0.99161 | -0.15961 | 0.99207 | -0.15076 | 24.785
73 | 0.046273 | 0.011671 | -0.046221 | -0.011639 | 5.1151e-05 | 3.2373e-05 | 0.069463 | 0.069464 | 0.069464 | 0.99161 | -0.15961 | 0.99041 | -0.18273 | 19.0834
74 | 0.01139 | 0.0028556 | -0.011388 | -0.0028543 | 2.4011e-06 | 1.2542e-06 | 0.017095 | 0.017095 | 0.017095 | 0.99145 | -0.16273 | 0.99122 | -0.16715 | 4.6965
75 | 0.020754 | 0.0052076 | -0.020739 | -0.0051989 | 1.4438e-05 | 8.7275e-06 | 0.031131 | 0.031131 | 0.031131 | 0.99207 | -0.15076 | 0.99131 | -0.16536 | 8.5525
76 | 0.32342 | 0.082552 | -0.32327 | -0.08246 | 0.00014388 | 9.1557e-05 | 0.48563 | 0.48563 | 0.48563 | 0.99207 | -0.15076 | 0.99158 | -0.15997 | 26.6831
77 | -0.4043 | -0.10291 | 0.40466 | 0.10314 | 0.00035757 | 0.00022801 | 0.60698 | 0.60698 | 0.60698 | 0.99207 | -0.15076 | 0.99302 | -0.13243 | 33.3506
78 | 0.043959 | 0.011071 | -0.04393 | -0.011053 | 2.9204e-05 | 1.8461e-05 | 0.066064 | 0.066064 | 0.066064 | 0.99041 | -0.18273 | 0.98969 | -0.19663 | 18.1496
79 | 0.017039 | 0.0042715 | -0.017036 | -0.0042696 | 3.311e-06 | 1.9451e-06 | 0.025577 | 0.025577 | 0.025577 | 0.99131 | -0.16536 | 0.9911 | -0.16944 | 7.0267
80 | 0.31823 | 0.081197 | -0.31792 | -0.080999 | 0.00031194 | 0.00019847 | 0.47807 | 0.47807 | 0.47807 | 0.99158 | -0.15997 | 0.99052 | -0.18028 | 26.2676
81 | 0.0050392 | 0.0012629 | -0.0050391 | -0.0012629 | 1.1497e-07 | 4.4243e-09 | 0.007562 | 0.0075621 | 0.0075621 | 0.99158 | -0.15997 | 0.99156 | -0.16045 | 2.0775
82 | -0.40791 | -0.10396 | 0.40871 | 0.10447 | 0.00080129 | 0.00051098 | 0.61185 | 0.61185 | 0.61185 | 0.99302 | -0.13243 | 0.99515 | -0.091813 | 33.6184
83 | 0.0081415 | 0.0020405 | -0.0081395 | -0.0020396 | 2.0018e-06 | 8.2099e-07 | 0.012224 | 0.012225 | 0.012225 | 0.99103 | -0.17083 | 0.99076 | -0.17599 | 3.3584
84 | -0.0081415 | -0.0020405 | 0.0081424 | 0.0020408 | 8.8729e-07 | 3.6382e-07 | 0.012224 | 0.012224 | 0.012224 | 0.99103 | -0.17083 | 0.99115 | -0.16854 | 3.3583
85 | 0.0065069 | 0.0016305 | -0.0065066 | -0.0016304 | 2.8575e-07 | 8.0134e-08 | 0.0097726 | 0.0097726 | 0.0097726 | 0.99076 | -0.17599 | 0.99071 | -0.17691 | 2.6848
86 | -0.0097714 | -0.0024491 | 0.0097721 | 0.0024494 | 6.4629e-07 | 3.1041e-07 | 0.01467 | 0.01467 | 0.01467 | 0.99115 | -0.16854 | 0.99122 | -0.16715 | 4.0302
87 | 0.0033004 | 0.00082711 | -0.0033003 | -0.00082714 | 4.2514e-08 | -3.2154e-08 | 0.004958 | 0.004958 | 0.004958 | 0.99052 | -0.18028 | 0.99051 | -0.18055 | 1.3621
88 | 0.31462 | 0.080172 | -0.31455 | -0.080128 | 6.8393e-05 | 4.3509e-05 | 0.47311 | 0.47311 | 0.47311 | 0.99052 | -0.18028 | 0.99029 | -0.18479 | 25.9952
89 | 0.0070864 | 0.0017759 | -0.0070862 | -0.0017759 | 1.5817e-07 | 5.3368e-08 | 0.010648 | 0.010648 | 0.010648 | 0.99029 | -0.18479 | 0.99026 | -0.18526 | 2.9253
90 | 0.30747 | 0.078352 | -0.30719 | -0.078174 | 0.00027959 | 0.00017782 | 0.46247 | 0.46247 | 0.46247 | 0.99029 | -0.18479 | 0.9893 | -0.20365 | 25.4102
91 | 0.0070862 | 0.0017759 | -0.0070856 | -0.0017757 | 6.0083e-07 | 2.0275e-07 | 0.010648 | 0.010648 | 0.010648 | 0.99026 | -0.18526 | 0.99017 | -0.18704 | 2.9253
92 | 0.0064115 | 0.0016068 | -0.006411 | -0.0016066 | 5.0221e-07 | 1.428e-07 | 0.0097272 | 0.0097272 | 0.0097272 | 0.9808 | -0.36848 | 0.98071 | -0.37012 | 2.6723
93 | 0.13725 | 0.034628 | -0.1372 | -0.034599 | 4.6443e-05 | 2.883e-05 | 0.20868 | 0.20868 | 0.20868 | 0.97908 | -0.4017 | 0.97872 | -0.40877 | 11.4658
94 | -0.026686 | -0.0066938 | 0.026695 | 0.0066992 | 8.707e-06 | 5.393e-06 | 0.040451 | 0.040451 | 0.040451 | 0.98173 | -0.35021 | 0.98208 | -0.34337 | 11.1128
95 | -0.0032513 | -0.00081485 | 0.0032514 | 0.00081475 | 1.4506e-07 | -1.0495e-07 | 0.0049505 | 0.0049504 | 0.0049505 | 0.97727 | -0.4371 | 0.97732 | -0.43617 | 1.36
96 | -0.0016323 | -0.0004091 | 0.0016323 | 0.00040904 | 1.2777e-08 | -6.4086e-08 | 0.0024579 | 0.0024578 | 0.0024579 | 0.98823 | -0.22422 | 0.98824 | -0.22405 | 0.67524
97 | -0.0031935 | -0.00080029 | 0.0031935 | 0.00080025 | 4.9037e-08 | -4.1081e-08 | 0.0048085 | 0.0048084 | 0.0048085 | 0.98824 | -0.22405 | 0.98826 | -0.22373 | 1.321
98 | 0.010414 | 0.0026106 | -0.010412 | -0.0026094 | 2.4405e-06 | 1.2104e-06 | 0.015539 | 0.015539 | 0.015539 | 0.99725 | -0.052407 | 0.99699 | -0.057327 | 4.2691
99 | 0.029908 | 0.0075084 | -0.029897 | -0.0075016 | 1.0948e-05 | 6.8268e-06 | 0.045302 | 0.045302 | 0.045302 | 0.98247 | -0.33569 | 0.98208 | -0.34337 | 12.4455
100 | -0.13254 | -0.033413 | 0.13258 | 0.03344 | 4.3199e-05 | 2.6757e-05 | 0.20165 | 0.20165 | 0.20165 | 0.97837 | -0.41558 | 0.97872 | -0.40877 | 11.0795
101 | 0.032364 | 0.0081219 | -0.03236 | -0.0081197 | 3.5659e-06 | 2.2311e-06 | 0.048787 | 0.048787 | 0.048787 | 0.98717 | -0.24553 | 0.98705 | -0.24784 | 13.4031
102 | -0.032364 | -0.0081219 | 0.032386 | 0.0081358 | 2.2192e-05 | 1.3885e-05 | 0.048787 | 0.048787 | 0.048787 | 0.98717 | -0.24553 | 0.98791 | -0.23117 | 13.4031
103 | 0.03236 | 0.0081197 | -0.032346 | -0.0081106 | 1.4548e-05 | 9.1026e-06 | 0.048787 | 0.048788 | 0.048788 | 0.98705 | -0.24784 | 0.98657 | -0.25728 | 13.4032
104 | -0.034896 | -0.0087648 | 0.034906 | 0.0087713 | 1.0372e-05 | 6.5098e-06 | 0.052568 | 0.052568 | 0.052568 | 0.98791 | -0.23117 | 0.98823 | -0.22494 | 14.4417
105 | 0.007609 | 0.0019071 | -0.0076081 | -0.0019068 | 8.7956e-07 | 3.3555e-07 | 0.011476 | 0.011477 | 0.011477 | 0.98657 | -0.25728 | 0.98644 | -0.2597 | 3.1529
106 | 0.024737 | 0.0062035 | -0.02473 | -0.0061994 | 6.6379e-06 | 4.0859e-06 | 0.037311 | 0.037311 | 0.037311 | 0.98657 | -0.25728 | 0.98628 | -0.26291 | 10.2503
107 | -0.0063259 | -0.0015854 | 0.0063269 | 0.0015857 | 9.8757e-07 | 2.4698e-07 | 0.0094431 | 0.009443 | 0.0094431 | 0.99682 | -0.060603 | 0.99699 | -0.057327 | 2.5943
108 | 0.040994 | 0.010317 | -0.040971 | -0.010303 | 2.3308e-05 | 1.4707e-05 | 0.061651 | 0.061651 | 0.061651 | 0.98969 | -0.19663 | 0.98908 | -0.20854 | 16.9371
109 | 0.0098925 | 0.0024793 | -0.0098923 | -0.0024792 | 1.9822e-07 | 9.5985e-08 | 0.014852 | 0.014852 | 0.014852 | 0.9911 | -0.16944 | 0.99108 | -0.16986 | 4.0803
110 | -0.0043523 | -0.0010908 | 0.0043527 | 0.0010907 | 3.5199e-07 | -5.6852e-08 | 0.0065414 | 0.0065413 | 0.0065414 | 0.99006 | -0.18915 | 0.99015 | -0.18745 | 1.7971
111 | -0.0043527 | -0.0010907 | 0.0043528 | 0.0010907 | 8.5608e-08 | -1.3836e-08 | 0.0065413 | 0.0065412 | 0.0065413 | 0.99015 | -0.18745 | 0.99017 | -0.18704 | 1.797
112 | 0.0048864 | 0.0012243 | -0.0048862 | -0.0012243 | 2.9651e-07 | 7.5354e-10 | 0.0073391 | 0.0073392 | 0.0073392 | 0.99071 | -0.17691 | 0.99065 | -0.17818 | 2.0163
113 | 0.0032072 | 0.00080366 | -0.003207 | -0.00080376 | 1.2645e-07 | -9.8752e-08 | 0.0048661 | 0.0048662 | 0.0048662 | 0.98071 | -0.37012 | 0.98067 | -0.37095 | 1.3369
114 | -0.0016264 | -0.00040762 | 0.0016265 | 0.00040745 | 3.2874e-08 | -1.6805e-07 | 0.0024431 | 0.002443 | 0.0024431 | 0.9906 | -0.17907 | 0.99062 | -0.17865 | 0.67118
115 | -0.0032665 | -0.00081849 | 0.0032666 | 0.00081843 | 7.2164e-08 | -5.673e-08 | 0.0049065 | 0.0049065 | 0.0049065 | 0.99062 | -0.17865 | 0.99065 | -0.17818 | 1.348
116 | -0.037429 | -0.0094037 | 0.037449 | 0.0094158 | 1.9234e-05 | 1.2103e-05 | 0.056367 | 0.056367 | 0.056367 | 0.98823 | -0.22494 | 0.98879 | -0.21418 | 15.4854
117 | -0.039193 | -0.009853 | 0.039204 | 0.0098597 | 1.0561e-05 | 6.655e-06 | 0.058992 | 0.058992 | 0.058992 | 0.98879 | -0.21418 | 0.98908 | -0.20854 | 16.2067
118 | 0.017253 | 0.0043254 | -0.017248 | -0.0043228 | 4.3134e-06 | 2.544e-06 | 0.02603 | 0.02603 | 0.02603 | 0.98628 | -0.26291 | 0.98601 | -0.26816 | 7.1511
119 | -0.0062058 | -0.0015553 | 0.0062066 | 0.0015555 | 8.0519e-07 | 1.9674e-07 | 0.0093188 | 0.0093187 | 0.0093188 | 0.99094 | -0.17258 | 0.99108 | -0.16986 | 2.5601

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.52748 | 0.13472

## res_load
| p_mw | q_mvar
0 | 0.0039625 | 0.00099309
1 | 0.0040227 | 0.0010082
2 | 0.0039421 | 0.00098798
3 | 0.0040267 | 0.0010092
4 | 0.0058953 | 0.0014775
5 | 0.0039236 | 0.00098334
6 | 0.0043444 | 0.0010888
7 | 0.003259 | 0.00081679
8 | 0.0062309 | 0.0015616
9 | 0.0042276 | 0.0010595
10 | 0.0038337 | 0.00096081
11 | 0.016359 | 0.0040999
12 | 0.0032537 | 0.00081545
13 | 0.004029 | 0.0010098
14 | 0.0043571 | 0.001092
15 | 0.0043064 | 0.0010793
16 | 0.0076694 | 0.0019221
17 | 0.0032895 | 0.00082444
18 | 0.0032933 | 0.00082537
19 | 0.0062976 | 0.0015783
20 | 0.0062584 | 0.0015685
21 | 0.0031817 | 0.00079741
22 | 0.0046946 | 0.0011766
23 | 0.052158 | 0.013072
24 | 0.070494 | 0.017668
25 | 0.030342 | 0.0076044
26 | 0.0076581 | 0.0019193
27 | 0.0061235 | 0.0015347
28 | 0.0043213 | 0.001083
29 | 0.0021389 | 0.00053606
30 | 0.0068488 | 0.0017165
31 | 0.0024377 | 0.00061095
32 | 0.0022625 | 0.00056704
33 | 0.0037 | 0.00092732
34 | 0.0032533 | 0.00081537
35 | 0.0016326 | 0.00040916
36 | 0.0016291 | 0.00040828
37 | 0.0050391 | 0.0012629
38 | 0.0040349 | 0.0010113
39 | 0.0040887 | 0.0010247
40 | 0.0031647 | 0.00079315
41 | 0.0046248 | 0.0011591
42 | 0.0031613 | 0.00079231
43 | 0.0032513 | 0.00081485
44 | 0.0037615 | 0.00094273
45 | 0.0050256 | 0.0012595
46 | 0.0016323 | 0.0004091
47 | 0.0015611 | 0.00039126
48 | 0.0031768 | 0.00079618
49 | 0.0040313 | 0.0010104
50 | 0.0031851 | 0.00079825
51 | 0.004276 | 0.0010717
52 | 0.0068426 | 0.0017149
53 | 0.0025267 | 0.00063325
54 | 0.0060974 | 0.0015281
55 | 0.0025099 | 0.00062904
56 | 0.0063259 | 0.0015854
57 | 0.0040847 | 0.0010237
58 | 0.018747 | 0.0046984
59 | 0.001394 | 0.00034937
60 | 0.013209 | 0.0033106
61 | 0.0016157 | 0.00040493
62 | 0.0029355 | 0.0007357
63 | 0.0071432 | 0.0017903
64 | 0.0043523 | 0.0010908
65 | 0.0016202 | 0.00040605
66 | 0.0033003 | 0.00082714
67 | 0.0027329 | 0.00068492
68 | 0.0032038 | 0.00080295
69 | 0.003207 | 0.00080376
70 | 0.0032016 | 0.00080239
71 | 0.0046245 | 0.001159
72 | 0.0016264 | 0.00040762
73 | 0.00164 | 0.00041104
74 | 0.0025231 | 0.00063235
75 | 0.0017446 | 0.00043724
76 | 0.0017672 | 0.00044291
77 | 0.0076081 | 0.0019068
78 | 0.0074774 | 0.001874
79 | 0.0062058 | 0.0015553
80 | 0.0036857 | 0.00092372
81 | 0.017248 | 0.0043228
82 | 0.0016428 | 0.00041172
83 | 0.0016196 | 0.0004059

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1