## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-576_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-576_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-576_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_261-576_0_3_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_261-576_0_3_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_261-576_0_3_node_3 | 0.4 | n |  | TRUE
6 | bus_LV_261-576_0_3_node_32 | 0.4 | n |  | TRUE
7 | bus_LV_261-576_0_3_node_24 | 0.4 | n |  | TRUE
8 | bus_LV_261-576_0_3_node_69 | 0.4 | n |  | TRUE
9 | bus_LV_261-576_0_3_node_6 | 0.4 | n |  | TRUE
10 | bus_LV_261-576_0_3_node_12 | 0.4 | n |  | TRUE
11 | bus_LV_261-576_0_3_node_23 | 0.4 | n |  | TRUE
12 | bus_LV_261-576_0_3_node_64 | 0.4 | n |  | TRUE
13 | bus_LV_261-576_0_3_node_7 | 0.4 | n |  | TRUE
14 | bus_LV_261-576_0_3_node_20 | 0.4 | n |  | TRUE
15 | bus_LV_261-576_0_3_node_44 | 0.4 | n |  | TRUE
16 | bus_LV_261-576_0_3_node_8 | 0.4 | n |  | TRUE
17 | bus_LV_261-576_0_3_node_43 | 0.4 | n |  | TRUE
18 | bus_LV_261-576_0_3_node_11 | 0.4 | n |  | TRUE
19 | bus_LV_261-576_0_3_node_40 | 0.4 | n |  | TRUE
20 | bus_LV_261-576_0_3_node_9 | 0.4 | n |  | TRUE
21 | bus_LV_261-576_0_3_node_62 | 0.4 | n |  | TRUE
22 | bus_LV_261-576_0_3_node_10 | 0.4 | n |  | TRUE
23 | bus_LV_261-576_0_3_node_36 | 0.4 | n |  | TRUE
24 | bus_LV_261-576_0_3_node_84 | 0.4 | n |  | TRUE
25 | bus_LV_261-576_0_3_node_14 | 0.4 | n |  | TRUE
26 | bus_LV_261-576_0_3_node_15 | 0.4 | n |  | TRUE
27 | bus_LV_261-576_0_3_node_50 | 0.4 | n |  | TRUE
28 | bus_LV_261-576_0_3_node_70 | 0.4 | n |  | TRUE
29 | bus_LV_261-576_0_3_node_16 | 0.4 | n |  | TRUE
30 | bus_LV_261-576_0_3_node_22 | 0.4 | n |  | TRUE
31 | bus_LV_261-576_0_3_node_46 | 0.4 | n |  | TRUE
32 | bus_LV_261-576_0_3_node_17 | 0.4 | n |  | TRUE
33 | bus_LV_261-576_0_3_node_18 | 0.4 | n |  | TRUE
34 | bus_LV_261-576_0_3_node_72 | 0.4 | n |  | TRUE
35 | bus_LV_261-576_0_3_node_51 | 0.4 | n |  | TRUE
36 | bus_LV_261-576_0_3_node_75 | 0.4 | n |  | TRUE
37 | bus_LV_261-576_0_3_node_55 | 0.4 | n |  | TRUE
38 | bus_LV_261-576_0_3_node_34 | 0.4 | n |  | TRUE
39 | bus_LV_261-576_0_3_node_45 | 0.4 | n |  | TRUE
40 | bus_LV_261-576_0_3_node_25 | 0.4 | n |  | TRUE
41 | bus_LV_261-576_0_3_node_26 | 0.4 | n |  | TRUE
42 | bus_LV_261-576_0_3_node_39 | 0.4 | n |  | TRUE
43 | bus_LV_261-576_0_3_node_38 | 0.4 | n |  | TRUE
44 | bus_LV_261-576_0_3_node_41 | 0.4 | n |  | TRUE
45 | bus_LV_261-576_0_3_node_48 | 0.4 | n |  | TRUE
46 | bus_LV_261-576_0_3_node_35 | 0.4 | n |  | TRUE
47 | bus_LV_261-576_0_3_node_67 | 0.4 | n |  | TRUE
48 | bus_LV_261-576_0_3_node_66 | 0.4 | n |  | TRUE
49 | bus_LV_261-576_0_3_node_42 | 0.4 | n |  | TRUE
50 | bus_LV_261-576_0_3_node_47 | 0.4 | n |  | TRUE
51 | bus_LV_261-576_0_3_node_71 | 0.4 | n |  | TRUE
52 | bus_LV_261-576_0_3_node_52 | 0.4 | n |  | TRUE
53 | bus_LV_261-576_0_3_node_76 | 0.4 | n |  | TRUE
54 | bus_LV_261-576_0_3_node_74 | 0.4 | n |  | TRUE
55 | bus_LV_261-576_0_3_node_73 | 0.4 | n |  | TRUE
56 | bus_LV_261-576_0_3_node_56 | 0.4 | n |  | TRUE
57 | bus_LV_261-576_0_3_node_33 | 0.4 | n |  | TRUE
58 | bus_LV_261-576_0_3_node_49 | 0.4 | n |  | TRUE
59 | bus_LV_261-576_0_3_node_27 | 0.4 | n |  | TRUE
60 | bus_LV_261-576_0_3_node_28 | 0.4 | n |  | TRUE
61 | bus_LV_261-576_0_3_node_30 | 0.4 | n |  | TRUE
62 | bus_LV_261-576_0_3_node_31 | 0.4 | n |  | TRUE
63 | bus_LV_261-576_0_3_node_37 | 0.4 | n |  | TRUE
64 | bus_LV_261-576_0_3_node_53 | 0.4 | n |  | TRUE
65 | bus_LV_261-576_0_3_node_54 | 0.4 | n |  | TRUE
66 | bus_LV_261-576_0_3_node_63 | 0.4 | n |  | TRUE
67 | bus_LV_261-576_0_3_node_59 | 0.4 | n |  | TRUE
68 | bus_LV_261-576_0_3_node_58 | 0.4 | n |  | TRUE
69 | bus_LV_261-576_0_3_node_57 | 0.4 | n |  | TRUE
70 | bus_LV_261-576_0_3_node_82 | 0.4 | n |  | TRUE
71 | bus_LV_261-576_0_3_node_61 | 0.4 | n |  | TRUE
72 | bus_LV_261-576_0_3_node_60 | 0.4 | n |  | TRUE
73 | bus_LV_261-576_0_3_node_80 | 0.4 | n |  | TRUE
74 | bus_LV_261-576_0_3_node_68 | 0.4 | n |  | TRUE
75 | bus_LV_261-576_0_3_node_78 | 0.4 | n |  | TRUE
76 | bus_LV_261-576_0_3_node_77 | 0.4 | n |  | TRUE
77 | bus_LV_261-576_0_3_node_79 | 0.4 | n |  | TRUE
78 | bus_LV_261-576_0_3_node_81 | 0.4 | n |  | TRUE
79 | bus_LV_261-576_0_3_node_83 | 0.4 | n |  | TRUE
80 | bus_MV_359_0_node_89 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-576_0_3_load_0 | 0 | 0.0031634 | 0.00079283 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-576_0_3_load_1 | 1 | 0.010109 | 0.0025337 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-576_0_3_load_4 | 3 | 0.0015403 | 0.00038604 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-576_0_3_load_5 | 4 | 0.0011867 | 0.0002974 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-576_0_3_load_3 | 5 | 0.0018362 | 0.00046019 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-576_0_3_load_69 | 8 | 0.0092843 | 0.0023269 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-576_0_3_load_64 | 12 | 0.0021982 | 0.00055092 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-576_0_3_load_44 | 15 | 0.012728 | 0.0031899 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-576_0_3_load_43 | 17 | 0.0039344 | 0.00098606 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-576_0_3_load_40 | 19 | 0.0038655 | 0.00096878 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-576_0_3_load_62 | 21 | 0.0040998 | 0.0010275 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-576_0_3_load_36 | 23 | 0.0063494 | 0.0015913 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-576_0_3_load_84 | 24 | 0.0021894 | 0.00054872 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-576_0_3_load_50 | 27 | 0.0037334 | 0.00093569 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-576_0_3_load_70 | 28 | 0.0023169 | 0.00058067 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-576_0_3_load_46 | 31 | 0.0029055 | 0.00072818 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-576_0_3_load_72 | 34 | 0.012802 | 0.0032084 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_261-576_0_3_load_51 | 35 | 0.0064275 | 0.0016109 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_261-576_0_3_load_75 | 36 | 0.0071737 | 0.0017979 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_261-576_0_3_load_55 | 37 | 0.00089145 | 0.00022342 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_261-576_0_3_load_34 | 38 | 0.0014744 | 0.00036952 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_261-576_0_3_load_45 | 39 | 0.005508 | 0.0013804 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_261-576_0_3_load_25 | 40 | 0.0055217 | 0.0013839 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_261-576_0_3_load_26 | 41 | 0.005553 | 0.0013917 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_261-576_0_3_load_39 | 42 | 0.0022265 | 0.00055801 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_261-576_0_3_load_38 | 43 | 0.0019825 | 0.00049687 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_261-576_0_3_load_41 | 44 | 0.0040356 | 0.0010114 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_261-576_0_3_load_48 | 45 | 0.0090132 | 0.0022589 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_261-576_0_3_load_35 | 46 | 0.0056021 | 0.001404 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_261-576_0_3_load_67 | 47 | 0.0049491 | 0.0012404 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_261-576_0_3_load_66 | 48 | 0.0030531 | 0.00076518 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_261-576_0_3_load_42 | 49 | 0.0038087 | 0.00095454 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_261-576_0_3_load_47 | 50 | 0.0069126 | 0.0017325 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_261-576_0_3_load_71 | 51 | 0.012874 | 0.0032266 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_261-576_0_3_load_76 | 53 | 0.0071592 | 0.0017943 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_261-576_0_3_load_74 | 54 | 0.0044058 | 0.0011042 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_261-576_0_3_load_33 | 57 | 0.0054384 | 0.001363 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_261-576_0_3_load_49 | 58 | 0.0056495 | 0.0014159 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_261-576_0_3_load_27 | 59 | 0.0041103 | 0.0010301 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_261-576_0_3_load_28 | 60 | 0.0050468 | 0.0012648 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_261-576_0_3_load_30 | 61 | 0.0012541 | 0.0003143 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_261-576_0_3_load_31 | 62 | 0.0022442 | 0.00056245 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_261-576_0_3_load_37 | 63 | 0.0072041 | 0.0018055 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_261-576_0_3_load_53 | 64 | 0.0087031 | 0.0021812 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_261-576_0_3_load_54 | 65 | 0.008926 | 0.0022371 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_261-576_0_3_load_63 | 66 | 0.0063638 | 0.0015949 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_261-576_0_3_load_82 | 70 | 0.00077956 | 0.00019538 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_261-576_0_3_load_80 | 73 | 0.00090213 | 0.00022609 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_261-576_0_3_load_68 | 74 | 0.0029542 | 0.00074039 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_261-576_0_3_load_78 | 75 | 0.00090895 | 0.00022781 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_261-576_0_3_load_77 | 76 | 0.00078631 | 0.00019707 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_261-576_0_3_load_79 | 77 | 0.00075318 | 0.00018876 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_261-576_0_3_load_81 | 78 | 0.0021236 | 0.00053222 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_261-576_0_3_load_83 | 79 | 0.0013796 | 0.00034577 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 63 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-576_0_3_line_0 |  | 0 | 1 | 0.027944 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-576_0_3_line_1 |  | 0 | 2 | 0.026571 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-576_0_3_line_2 |  | 2 | 3 | 0.013201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-576_0_3_line_3 |  | 2 | 4 | 0.037451 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-576_0_3_line_4 |  | 3 | 7 | 0.01771 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_261-576_0_3_line_5 |  | 4 | 8 | 0.014398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_261-576_0_3_line_6 |  | 5 | 6 | 0.012621 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_261-576_0_3_line_7 |  | 6 | 39 | 0.014828 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_261-576_0_3_line_8 |  | 6 | 17 | 0.039285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_261-576_0_3_line_9 |  | 7 | 40 | 0.034542 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_261-576_0_3_line_10 |  | 7 | 41 | 0.0030053 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_261-576_0_3_line_11 |  | 8 | 38 | 0.008521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_261-576_0_3_line_12 |  | 9 | 10 | 0.048289 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-576_0_3_line_13 |  | 9 | 11 | 0.059157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_261-576_0_3_line_14 |  | 9 | 12 | 0.082318 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_261-576_0_3_line_15 |  | 10 | 24 | 0.037415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_261-576_0_3_line_16 |  | 11 | 38 | 0.020939 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_261-576_0_3_line_17 |  | 12 | 42 | 0.034148 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_261-576_0_3_line_18 |  | 13 | 14 | 0.02633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_261-576_0_3_line_19 |  | 13 | 15 | 0.01057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_261-576_0_3_line_20 |  | 14 | 36 | 0.0076541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_261-576_0_3_line_21 |  | 15 | 43 | 0.03149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_261-576_0_3_line_22 |  | 16 | 17 | 0.018913 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_261-576_0_3_line_23 |  | 16 | 18 | 0.0098508 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_261-576_0_3_line_24 |  | 16 | 19 | 0.050089 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_261-576_0_3_line_25 |  | 18 | 20 | 0.027536 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_261-576_0_3_line_26 |  | 18 | 22 | 0.011481 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_261-576_0_3_line_27 |  | 19 | 44 | 0.031153 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_261-576_0_3_line_28 |  | 20 | 21 | 0.021486 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_261-576_0_3_line_29 |  | 21 | 45 | 0.0048844 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_261-576_0_3_line_30 |  | 22 | 23 | 0.02792 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_261-576_0_3_line_31 |  | 23 | 46 | 0.015088 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_261-576_0_3_line_32 |  | 25 | 26 | 0.067839 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_261-576_0_3_line_33 |  | 25 | 27 | 0.0074743 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_261-576_0_3_line_34 |  | 26 | 28 | 0.022412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_261-576_0_3_line_35 |  | 27 | 49 | 0.025165 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_261-576_0_3_line_36 |  | 29 | 30 | 0.16207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_261-576_0_3_line_37 |  | 29 | 31 | 0.050633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_261-576_0_3_line_38 |  | 30 | 37 | 0.03306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_261-576_0_3_line_39 |  | 31 | 50 | 0.022937 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_261-576_0_3_line_40 |  | 32 | 33 | 0.018699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_261-576_0_3_line_41 |  | 32 | 34 | 0.0062045 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_261-576_0_3_line_42 |  | 33 | 35 | 0.031167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_261-576_0_3_line_43 |  | 34 | 51 | 0.023256 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_261-576_0_3_line_44 |  | 35 | 52 | 0.017847 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_261-576_0_3_line_45 |  | 36 | 55 | 0.026678 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_261-576_0_3_line_46 |  | 37 | 56 | 0.021201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_261-576_0_3_line_47 |  | 39 | 58 | 0.030334 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_261-576_0_3_line_48 |  | 40 | 57 | 0.02918 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_261-576_0_3_line_49 |  | 41 | 58 | 0.027168 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_261-576_0_3_line_50 |  | 42 | 62 | 0.064095 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_261-576_0_3_line_51 |  | 43 | 63 | 0.030549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_261-576_0_3_line_52 |  | 44 | 49 | 0.031924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_261-576_0_3_line_53 |  | 45 | 50 | 0.013099 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_261-576_0_3_line_54 |  | 46 | 63 | 0.015161 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
55 | LV_261-576_0_3_line_55 |  | 47 | 48 | 0.0060346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_261-576_0_3_line_56 |  | 48 | 68 | 0.028722 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_261-576_0_3_line_57 |  | 51 | 55 | 0.018537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_261-576_0_3_line_58 |  | 52 | 64 | 0.018591 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_261-576_0_3_line_59 |  | 52 | 65 | 0.028616 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_261-576_0_3_line_60 |  | 53 | 54 | 0.001488 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_261-576_0_3_line_61 |  | 54 | 55 | 0.0097702 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_261-576_0_3_line_62 |  | 56 | 69 | 0.032509 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_261-576_0_3_line_63 |  | 59 | 60 | 0.033348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_261-576_0_3_line_64 |  | 60 | 61 | 0.027531 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_261-576_0_3_line_65 |  | 61 | 62 | 0.025083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_261-576_0_3_line_66 |  | 64 | 66 | 0.024651 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_261-576_0_3_line_67 |  | 65 | 67 | 0.010147 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_261-576_0_3_line_68 |  | 67 | 68 | 0.041393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_261-576_0_3_line_69 |  | 68 | 71 | 0.63215 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_261-576_0_3_line_70 |  | 69 | 70 | 0.057225 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_261-576_0_3_line_71 |  | 70 | 72 | 0.080377 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_261-576_0_3_line_72 |  | 71 | 74 | 0.050056 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_261-576_0_3_line_73 |  | 72 | 73 | 0.047351 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_261-576_0_3_line_74 |  | 73 | 75 | 0.0083476 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_261-576_0_3_line_75 |  | 75 | 76 | 0.014494 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_261-576_0_3_line_76 |  | 76 | 77 | 0.0076026 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_261-576_0_3_line_77 |  | 77 | 78 | 0.019632 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_261-576_0_3_line_78 |  | 78 | 79 | 0.008581 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-576_0_3_trafo_37 | 0.63 MVA 20/0.4 kV | 80 | 63 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17
0 | 2682112.2863 | 1244665.1362 | 2682093.249 | 1244685.5923
1 | 2682130.3881 | 1244645.6855 | 2682112.2863 | 1244665.1362
2 | 2682130.3881 | 1244645.6855 | 2682120.2586 | 1244637.221
3 | 2682130.3881 | 1244645.6855 | 2682155.5112 | 1244617.9114
4 | 2682106.6688 | 1244625.865 | 2682120.2586 | 1244637.221
5 | 2682165.17 | 1244607.2334 | 2682155.5112 | 1244617.9114
6 | 2682052.7881 | 1244677.6239 | 2682062.5454 | 1244685.6297
7 | 2682052.7881 | 1244677.6239 | 2682062.6665 | 1244666.5662
8 | 2682052.7881 | 1244677.6239 | 2682028.8694 | 1244658.0012 | 2682028.176 | 1244655.6788 | 2682028.2002 | 1244653.9334 | 2682028.0988 | 1244650.8854 | 2682027.7471 | 1244649.8139
9 | 2682106.6688 | 1244625.865 | 2682115.4063 | 1244617.024 | 2682130.4973 | 1244600.8629
10 | 2682106.6688 | 1244625.865 | 2682103.9525 | 1244627.1509
11 | 2682165.17 | 1244607.2334 | 2682170.8862 | 1244600.9141
12 | 2682222.2755 | 1244629.8466 | 2682220.7665 | 1244623.1319 | 2682219.7364 | 1244616.7575 | 2682219.3046 | 1244608.1119 | 2682219.2232 | 1244599.271 | 2682220.1627 | 1244589.8327 | 2682220.7367 | 1244584.9482 | 2682221.0357 | 1244581.9168
13 | 2682184.9323 | 1244585.3858 | 2682193.6722 | 1244575.8444 | 2682197.7324 | 1244571.3418 | 2682200.7486 | 1244568.5483 | 2682205.2119 | 1244566.5865 | 2682208.3062 | 1244565.7954 | 2682212.4796 | 1244566.7539 | 2682218.5525 | 1244569.1621 | 2682221.8826 | 1244570.4425 | 2682224.4632 | 1244571.8125 | 2682223.225 | 1244575.5425 | 2682221.0357 | 1244581.9168
14 | 2682221.0357 | 1244581.9168 | 2682217.0956 | 1244579.9386 | 2682213.4109 | 1244578.0751 | 2682208.9177 | 1244577.29 | 2682204.8351 | 1244577.9562 | 2682202.0591 | 1244579.2297 | 2682199.8504 | 1244581.0115 | 2682160.2965 | 1244625.045
15 | 2682222.2755 | 1244629.8466 | 2682197.5057 | 1244657.8882
16 | 2682184.9323 | 1244585.3858 | 2682170.8862 | 1244600.9141
17 | 2682137.2974 | 1244650.284 | 2682145.868 | 1244641.1076 | 2682160.2965 | 1244625.045
18 | 2682111.945 | 1244764.9168 | 2682112.8194 | 1244755.2552 | 2682113.5557 | 1244738.6422
19 | 2682113.5557 | 1244738.6422 | 2682105.4086 | 1244731.9087
20 | 2682111.945 | 1244764.9168 | 2682111.749 | 1244767.0601 | 2682113.2931 | 1244772.3409
21 | 2682081.1358 | 1244711.8477 | 2682105.4086 | 1244731.9087
22 | 2682012.1252 | 1244641.9914 | 2682016.2882 | 1244642.605 | 2682019.7739 | 1244643.0201 | 2682023.6877 | 1244644.164 | 2682025.6216 | 1244645.8586 | 2682027.1198 | 1244647.903 | 2682027.7471 | 1244649.8139
23 | 2682005.6444 | 1244649.4072 | 2682008.3605 | 1244646.4538 | 2682012.1252 | 1244641.9914
24 | 2682012.1252 | 1244641.9914 | 2682016.42 | 1244636.9027 | 2682027.7558 | 1244623.7832 | 2682045.2083 | 1244604.3871
25 | 2681991.2476 | 1244630.3167 | 2682003.255 | 1244641.8576 | 2682004.6732 | 1244643.1337 | 2682008.3605 | 1244646.4538 | 2682005.6444 | 1244649.4072
26 | 2682011.6418 | 1244658.3633 | 2682009.8773 | 1244656.9935 | 2682009.0661 | 1244652.2566 | 2682005.6444 | 1244649.4072
27 | 2682066.0462 | 1244581.2287 | 2682045.2083 | 1244604.3871
28 | 2681991.2476 | 1244630.3167 | 2681977.343 | 1244646.6969
29 | 2681974.1821 | 1244650.4207 | 2681977.343 | 1244646.6969
30 | 2682011.6418 | 1244658.3633 | 2682016.305 | 1244662.1527 | 2682021.0055 | 1244662.151 | 2682034.272 | 1244673.1155
31 | 2682034.272 | 1244673.1155 | 2682045.9023 | 1244682.7278
32 | 2682066.4095 | 1244527.2143 | 2682059.771 | 1244545.469 | 2682070.7624 | 1244542.5078 | 2682098.8104 | 1244530.8207 | 2682105.4299 | 1244531.4127
33 | 2682105.4299 | 1244531.4127 | 2682104.232 | 1244538.7903
34 | 2682066.4095 | 1244527.2143 | 2682066.5634 | 1244516.0972 | 2682064.5558 | 1244504.9836
35 | 2682104.232 | 1244538.7903 | 2682087.3993 | 1244557.4976
36 | 2681882.1765 | 1244516.9838 | 2681913.3298 | 1244545.2677 | 2681881.8099 | 1244578.5568 | 2681878.709 | 1244583.1062 | 2681877.2875 | 1244588.0901 | 2681878.173 | 1244592.3721 | 2681880.6925 | 1244596.5321 | 2681914.1403 | 1244639.2137
37 | 2681914.1403 | 1244639.2137 | 2681936.1951 | 1244671.7974 | 2681947.4608 | 1244671.1035
38 | 2681882.1765 | 1244516.9838 | 2681859.9477 | 1244541.4548
39 | 2681947.4608 | 1244671.1035 | 2681957.1309 | 1244670.5078 | 2681965.7048 | 1244660.4073
40 | 2682041.2718 | 1244794.4495 | 2682059.9432 | 1244796.209
41 | 2682059.9432 | 1244796.209 | 2682061.4061 | 1244794.25 | 2682064.9899 | 1244793.1138
42 | 2682041.2718 | 1244794.4495 | 2682030.9556 | 1244784.1438 | 2682019.1891 | 1244772.4554
43 | 2682087.9094 | 1244791.28 | 2682071.7896 | 1244790.9579 | 2682064.9899 | 1244793.1138
44 | 2682006.5272 | 1244759.8774 | 2682019.1891 | 1244772.4554
45 | 2682105.107 | 1244795.9447 | 2682107.1078 | 1244794.9828 | 2682109.5807 | 1244791.5812 | 2682110.0795 | 1244785.0278 | 2682113.6059 | 1244779.2168 | 2682113.2931 | 1244772.3409
46 | 2681843.127 | 1244547.1781 | 2681846.4168 | 1244549.1916 | 2681848.7008 | 1244550.1682 | 2681851.0748 | 1244550.0898 | 2681853.1385 | 1244548.9508 | 2681859.9477 | 1244541.4548
47 | 2682083.8102 | 1244644.8646 | 2682073.874 | 1244654.0207 | 2682062.6665 | 1244666.5662
48 | 2682152.0748 | 1244581.5159 | 2682145.3299 | 1244587.2165 | 2682141.1347 | 1244589.4712 | 2682130.4973 | 1244600.8629
49 | 2682103.9525 | 1244627.1509 | 2682098.1109 | 1244629.9162 | 2682088.4487 | 1244640.5903 | 2682083.8102 | 1244644.8646
50 | 2682093.5483 | 1244697.1257 | 2682137.2974 | 1244650.284
51 | 2682081.1358 | 1244711.8477 | 2682057.5885 | 1244692.3862
52 | 2682087.3993 | 1244557.4976 | 2682066.0462 | 1244581.2287
53 | 2681974.1821 | 1244650.4207 | 2681965.7048 | 1244660.4073
54 | 2682057.5885 | 1244692.3862 | 2682045.9023 | 1244682.7278
55 | 2681964.9968 | 1244693.4869 | 2681969.0877 | 1244689.0506
56 | 2681945.526 | 1244714.6017 | 2681964.9968 | 1244693.4869
57 | 2682105.107 | 1244795.9447 | 2682102.8171 | 1244797.0472 | 2682088.1005 | 1244791.2838 | 2682087.9094 | 1244791.28
58 | 2682006.5272 | 1244759.8774 | 2682020.0567 | 1244747.1263
59 | 2682006.5272 | 1244759.8774 | 2681986.2208 | 1244739.7155
60 | 2682109.4776 | 1244804.6829 | 2682110.1432 | 1244806.0136
61 | 2682105.107 | 1244795.9447 | 2682109.4776 | 1244804.6829
62 | 2681843.127 | 1244547.1781 | 2681836.7344 | 1244542.7423 | 2681828.7993 | 1244538.363 | 2681813.8118 | 1244533.5417
63 | 2682146.5719 | 1244754.7922 | 2682120.7563 | 1244733.6822
64 | 2682120.7563 | 1244733.6822 | 2682099.4435 | 1244716.2542
65 | 2682093.5483 | 1244697.1257 | 2682091.7043 | 1244699.1 | 2682090.149 | 1244701.18 | 2682089.4675 | 1244702.9163 | 2682089.1513 | 1244705.0135 | 2682089.3348 | 1244707.0397 | 2682090.2658 | 1244708.5759 | 2682094.6422 | 1244712.3281 | 2682099.4435 | 1244716.2542
66 | 2682020.0567 | 1244747.1263 | 2682033.1422 | 1244734.7938 | 2682036.2168 | 1244728.875
67 | 2681976.3778 | 1244742.1813 | 2681986.2208 | 1244739.7155
68 | 2681976.3778 | 1244742.1813 | 2681961.2441 | 1244727.2058 | 2681947.8965 | 1244716.9584 | 2681945.526 | 1244714.6017
69 | 2681602.1012 | 1244960.3358 | 2681613.8827 | 1244967.4252 | 2681739.4375 | 1245031.5113 | 2681739.2261 | 1245025.4706 | 2681746.9001 | 1245007.6412 | 2681685.0573 | 1244976.8782 | 2681710.7633 | 1244953.4263 | 2681732.8012 | 1244934.0602 | 2681774.1996 | 1244895.5138 | 2681869.1304 | 1244806.6695 | 2681877.3975 | 1244799.0225 | 2681925.2174 | 1244754.1834 | 2681941.9394 | 1244738.9921 | 2681937.6061 | 1244734.2956 | 2681938.8238 | 1244719.4572 | 2681939.559 | 1244717.1101 | 2681943.4623 | 1244712.4606 | 2681945.526 | 1244714.6017
70 | 2681813.8118 | 1244533.5417 | 2681806.5195 | 1244531.3173 | 2681797.7215 | 1244525.9366 | 2681790.4695 | 1244518.0531 | 2681774.2973 | 1244494.4928
71 | 2681725.4359 | 1244431.6722 | 2681737.278 | 1244439.9191 | 2681753.5532 | 1244464.272 | 2681774.2973 | 1244494.4928
72 | 2681602.1012 | 1244960.3358 | 2681599.9607 | 1244963.2196 | 2681592.1911 | 1244971.0073 | 2681587.1476 | 1244972.8837 | 2681578.3457 | 1244973.3185 | 2681566.2928 | 1244971.1179 | 2681559.0772 | 1244965.7088
73 | 2681725.4359 | 1244431.6722 | 2681732.2583 | 1244466.3469 | 2681735.6764 | 1244477.8619
74 | 2681735.6764 | 1244477.8619 | 2681738.0518 | 1244485.8644
75 | 2681742.1762 | 1244499.7588 | 2681738.0518 | 1244485.8644
76 | 2681742.1762 | 1244499.7588 | 2681742.9829 | 1244502.4763 | 2681744.4649 | 1244507.0079
77 | 2681751.2777 | 1244525.4097 | 2681746.8842 | 1244514.4054 | 2681744.4649 | 1244507.0079
78 | 2681754.4595 | 1244533.3791 | 2681751.2777 | 1244525.4097

## bus_geodata
| x | y | coords
0 | 2682112.2863 | 1244665.1362
1 | 2682093.249 | 1244685.5923
2 | 2682130.3881 | 1244645.6855
3 | 2682120.2586 | 1244637.221
4 | 2682155.5112 | 1244617.9114
5 | 2682062.5454 | 1244685.6297
6 | 2682052.7881 | 1244677.6239
7 | 2682106.6688 | 1244625.865
8 | 2682165.17 | 1244607.2334
9 | 2682221.0357 | 1244581.9168
10 | 2682222.2755 | 1244629.8466
11 | 2682184.9323 | 1244585.3858
12 | 2682160.2965 | 1244625.045
13 | 2682113.5557 | 1244738.6422
14 | 2682111.945 | 1244764.9168
15 | 2682105.4086 | 1244731.9087
16 | 2682012.1252 | 1244641.9914
17 | 2682027.7471 | 1244649.8139
18 | 2682005.6444 | 1244649.4072
19 | 2682045.2083 | 1244604.3871
20 | 2681991.2476 | 1244630.3167
21 | 2681977.343 | 1244646.6969
22 | 2682011.6418 | 1244658.3633
23 | 2682034.272 | 1244673.1155
24 | 2682197.5057 | 1244657.8882
25 | 2682105.4299 | 1244531.4127
26 | 2682066.4095 | 1244527.2143
27 | 2682104.232 | 1244538.7903
28 | 2682064.5558 | 1244504.9836
29 | 2681914.1403 | 1244639.2137
30 | 2681882.1765 | 1244516.9838
31 | 2681947.4608 | 1244671.1035
32 | 2682059.9432 | 1244796.209
33 | 2682041.2718 | 1244794.4495
34 | 2682064.9899 | 1244793.1138
35 | 2682019.1891 | 1244772.4554
36 | 2682113.2931 | 1244772.3409
37 | 2681859.9477 | 1244541.4548
38 | 2682170.8862 | 1244600.9141
39 | 2682062.6665 | 1244666.5662
40 | 2682130.4973 | 1244600.8629
41 | 2682103.9525 | 1244627.1509
42 | 2682137.2974 | 1244650.284
43 | 2682081.1358 | 1244711.8477
44 | 2682066.0462 | 1244581.2287
45 | 2681974.1821 | 1244650.4207
46 | 2682045.9023 | 1244682.7278
47 | 2681969.0877 | 1244689.0506
48 | 2681964.9968 | 1244693.4869
49 | 2682087.3993 | 1244557.4976
50 | 2681965.7048 | 1244660.4073
51 | 2682087.9094 | 1244791.28
52 | 2682006.5272 | 1244759.8774
53 | 2682110.1432 | 1244806.0136
54 | 2682109.4776 | 1244804.6829
55 | 2682105.107 | 1244795.9447
56 | 2681843.127 | 1244547.1781
57 | 2682152.0748 | 1244581.5159
58 | 2682083.8102 | 1244644.8646
59 | 2682146.5719 | 1244754.7922
60 | 2682120.7563 | 1244733.6822
61 | 2682099.4435 | 1244716.2542
62 | 2682093.5483 | 1244697.1257
63 | 2682057.5885 | 1244692.3862
64 | 2682020.0567 | 1244747.1263
65 | 2681986.2208 | 1244739.7155
66 | 2682036.2168 | 1244728.875
67 | 2681976.3778 | 1244742.1813
68 | 2681945.526 | 1244714.6017
69 | 2681813.8118 | 1244533.5417
70 | 2681774.2973 | 1244494.4928
71 | 2681602.1012 | 1244960.3358
72 | 2681725.4359 | 1244431.6722
73 | 2681735.6764 | 1244477.8619
74 | 2681559.0772 | 1244965.7088
75 | 2681738.0519 | 1244485.8644
76 | 2681742.1762 | 1244499.7588
77 | 2681744.4649 | 1244507.0079
78 | 2681751.2777 | 1244525.4097
79 | 2681754.4595 | 1244533.3791
80 | 2682011.6418 | 1244658.3633

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98117 | -0.36231 | 0.0031634 | 0.00079283
1 | 0.9809 | -0.36743 | 0.010109 | 0.0025337
2 | 0.98149 | -0.35593 | 0 | 0
3 | 0.98204 | -0.3453 | 0.0015403 | 0.00038604
4 | 0.98041 | -0.37711 | 0.0011867 | 0.0002974
5 | 0.98743 | -0.24059 | 0.0018362 | 0.00046019
6 | 0.98745 | -0.24018 | 0 | 0
7 | 0.98279 | -0.33058 | 0 | 0
8 | 0.98001 | -0.38496 | 0.0092843 | 0.0023269
9 | 0.97841 | -0.41625 | 0 | 0
10 | 0.97831 | -0.41818 | 0 | 0
11 | 0.97947 | -0.3955 | 0 | 0
12 | 0.9771 | -0.44189 | 0.0021982 | 0.00055092
13 | 0.99349 | -0.12424 | 0 | 0
14 | 0.99141 | -0.16423 | 0 | 0
15 | 0.99432 | -0.10824 | 0.012728 | 0.0031899
16 | 0.99158 | -0.16058 | 0 | 0
17 | 0.99019 | -0.18727 | 0.0039344 | 0.00098606
18 | 0.99247 | -0.14361 | 0 | 0
19 | 0.99077 | -0.17637 | 0.0038655 | 0.00096878
20 | 0.99167 | -0.15896 | 0 | 0
21 | 0.99105 | -0.17095 | 0.0040998 | 0.0010275
22 | 0.99383 | -0.11749 | 0 | 0
23 | 0.99714 | -0.05427 | 0.0063494 | 0.0015913
24 | 0.97823 | -0.41967 | 0.0021894 | 0.00054872
25 | 0.98993 | -0.19267 | 0 | 0
26 | 0.98978 | -0.19547 | 0 | 0
27 | 0.98994 | -0.19236 | 0.0037334 | 0.00093569
28 | 0.98974 | -0.19639 | 0.0023169 | 0.00058067
29 | 0.99007 | -0.18995 | 0 | 0
30 | 0.98881 | -0.21458 | 0 | 0
31 | 0.99047 | -0.18226 | 0.0029055 | 0.00072818
32 | 0.98633 | -0.26255 | 0 | 0
33 | 0.98562 | -0.27643 | 0 | 0
34 | 0.98657 | -0.25795 | 0.012802 | 0.0032084
35 | 0.98443 | -0.29961 | 0.0064275 | 0.0016109
36 | 0.99081 | -0.17589 | 0.0071737 | 0.0017979
37 | 0.98855 | -0.21961 | 0.00089145 | 0.00022342
38 | 0.97984 | -0.38817 | 0.0014744 | 0.00036952
39 | 0.98644 | -0.25974 | 0.005508 | 0.0013804
40 | 0.98244 | -0.33741 | 0.0055217 | 0.0013839
41 | 0.98295 | -0.32749 | 0.005553 | 0.0013917
42 | 0.97663 | -0.45118 | 0.0022265 | 0.00055801
43 | 0.99718 | -0.053682 | 0.0019825 | 0.00049687
44 | 0.99037 | -0.18406 | 0.0040356 | 0.0010114
45 | 0.99093 | -0.17332 | 0.0090132 | 0.0022589
46 | 0.99902 | -0.018607 | 0.0056021 | 0.001404
47 | 0.98257 | -0.33601 | 0.0049491 | 0.0012404
48 | 0.9826 | -0.33547 | 0.0030531 | 0.00076518
49 | 0.99008 | -0.18965 | 0.0038087 | 0.00095454
50 | 0.99071 | -0.17759 | 0.0069126 | 0.0017325
51 | 0.98773 | -0.2354 | 0.012874 | 0.0032266
52 | 0.98386 | -0.31085 | 0 | 0
53 | 0.98876 | -0.21542 | 0.0071592 | 0.0017943
54 | 0.98877 | -0.21523 | 0.0044058 | 0.0011042
55 | 0.98888 | -0.21321 | 0 | 0
56 | 0.9884 | -0.2225 | 0 | 0
57 | 0.98229 | -0.34028 | 0.0054384 | 0.001363
58 | 0.98452 | -0.29687 | 0.0056495 | 0.0014159
59 | 0.97527 | -0.47793 | 0.0041103 | 0.0010301
60 | 0.9754 | -0.47542 | 0.0050468 | 0.0012648
61 | 0.97563 | -0.4708 | 0.0012541 | 0.0003143
62 | 0.97588 | -0.46602 | 0.0022442 | 0.00056245
63 | 1 | 0 | -0.24586 | -0.062366
64 | 0.9836 | -0.31589 | 0.0087031 | 0.0021812
65 | 0.98333 | -0.32111 | 0.008926 | 0.0022371
66 | 0.98345 | -0.31872 | 0.0063638 | 0.0015949
67 | 0.98323 | -0.32312 | 0 | 0
68 | 0.98281 | -0.33132 | 0 | 0
69 | 0.98817 | -0.22694 | 0 | 0
70 | 0.98777 | -0.23474 | 0.00077956 | 0.00019538
71 | 0.98109 | -0.36521 | 0 | 0
72 | 0.98726 | -0.2446 | 0 | 0
73 | 0.98697 | -0.2504 | 0.00090213 | 0.00022609
74 | 0.98095 | -0.36789 | 0.0029542 | 0.00074039
75 | 0.98692 | -0.25129 | 0.00090895 | 0.00022781
76 | 0.98685 | -0.2526 | 0.00078631 | 0.00019707
77 | 0.98682 | -0.25318 | 0.00075318 | 0.00018876
78 | 0.98676 | -0.25441 | 0.0021236 | 0.00053222
79 | 0.98675 | -0.25462 | 0.0013796 | 0.00034577
80 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.010112 | 0.0025349 | -0.010109 | -0.0025337 | 2.4646e-06 | 1.2245e-06 | 0.015336 | 0.015336 | 0.015336 | 0.98117 | -0.36231 | 0.9809 | -0.36743 | 4.2132
1 | -0.013275 | -0.0033277 | 0.013279 | 0.00333 | 4.0389e-06 | 2.2492e-06 | 0.020133 | 0.020133 | 0.020133 | 0.98117 | -0.36231 | 0.98149 | -0.35593 | 5.5312
2 | -0.044608 | -0.01122 | 0.044631 | 0.011234 | 2.265e-05 | 1.4329e-05 | 0.067644 | 0.067644 | 0.067644 | 0.98149 | -0.35593 | 0.98204 | -0.3453 | 18.5834
3 | 0.031329 | 0.0078898 | -0.031297 | -0.00787 | 3.1701e-05 | 1.9816e-05 | 0.04751 | 0.04751 | 0.04751 | 0.98149 | -0.35593 | 0.98041 | -0.37711 | 13.0523
4 | -0.046171 | -0.01162 | 0.046204 | 0.011641 | 3.2521e-05 | 2.0589e-05 | 0.069977 | 0.069977 | 0.069977 | 0.98204 | -0.3453 | 0.98279 | -0.33058 | 19.2246
5 | 0.03011 | 0.0075726 | -0.030099 | -0.0075656 | 1.1281e-05 | 7.0385e-06 | 0.045709 | 0.045709 | 0.045709 | 0.98041 | -0.37711 | 0.98001 | -0.38496 | 12.5575
6 | -0.0018362 | -0.00046019 | 0.0018362 | 0.00046005 | 3.6238e-08 | -1.3826e-07 | 0.0027671 | 0.002767 | 0.0027671 | 0.98743 | -0.24059 | 0.98745 | -0.24018 | 0.76018
7 | 0.07417 | 0.018763 | -0.074101 | -0.018719 | 6.954e-05 | 4.4316e-05 | 0.11183 | 0.11183 | 0.11183 | 0.98745 | -0.24018 | 0.98644 | -0.25974 | 30.7231
8 | -0.076007 | -0.019223 | 0.0762 | 0.019347 | 0.00019347 | 0.00012332 | 0.1146 | 0.1146 | 0.1146 | 0.98745 | -0.24018 | 0.99019 | -0.18727 | 31.4832
9 | 0.010964 | 0.0027488 | -0.010961 | -0.002747 | 3.5699e-06 | 1.8472e-06 | 0.016601 | 0.016601 | 0.016601 | 0.98279 | -0.33058 | 0.98244 | -0.33741 | 4.5608
10 | -0.057168 | -0.01439 | 0.057176 | 0.014395 | 8.4476e-06 | 5.3684e-06 | 0.086579 | 0.086579 | 0.086579 | 0.98279 | -0.33058 | 0.98295 | -0.32749 | 23.7853
11 | 0.020815 | 0.0052387 | -0.020812 | -0.0052368 | 3.1933e-06 | 1.9364e-06 | 0.031612 | 0.031613 | 0.031613 | 0.98001 | -0.38496 | 0.97984 | -0.38817 | 8.6848
12 | 0.0021898 | 0.00054787 | -0.0021896 | -0.00054835 | 2.0082e-07 | -4.7787e-07 | 0.00333 | 0.0033302 | 0.0033302 | 0.97841 | -0.41625 | 0.97831 | -0.41818 | 0.91489
13 | -0.019311 | -0.0048517 | 0.01933 | 0.0048632 | 1.9141e-05 | 1.1506e-05 | 0.029374 | 0.029374 | 0.029374 | 0.97841 | -0.41625 | 0.97947 | -0.3955 | 8.0697
14 | 0.017121 | 0.0043038 | -0.017101 | -0.0042914 | 2.0938e-05 | 1.2368e-05 | 0.026044 | 0.026044 | 0.026044 | 0.97841 | -0.41625 | 0.9771 | -0.44189 | 7.155
15 | 0.0021896 | 0.00054835 | -0.0021894 | -0.00054872 | 1.5561e-07 | -3.7017e-07 | 0.0033302 | 0.0033304 | 0.0033304 | 0.97831 | -0.41818 | 0.97823 | -0.41967 | 0.91494
16 | -0.01933 | -0.0048632 | 0.019337 | 0.0048673 | 6.7747e-06 | 4.0722e-06 | 0.029374 | 0.029373 | 0.029374 | 0.97947 | -0.3955 | 0.97984 | -0.38817 | 8.0697
17 | 0.014902 | 0.0037405 | -0.014896 | -0.0037367 | 6.5966e-06 | 3.7943e-06 | 0.022697 | 0.022697 | 0.022697 | 0.9771 | -0.44189 | 0.97663 | -0.45118 | 6.2354
18 | 0.086405 | 0.021881 | -0.086239 | -0.021775 | 0.00016557 | 0.00010563 | 0.12949 | 0.12949 | 0.12949 | 0.99349 | -0.12424 | 0.99141 | -0.16423 | 35.5755
19 | -0.086405 | -0.021881 | 0.086471 | 0.021923 | 6.6465e-05 | 4.2401e-05 | 0.12949 | 0.12949 | 0.12949 | 0.99349 | -0.12424 | 0.99432 | -0.10824 | 35.5754
20 | 0.086239 | 0.021775 | -0.086191 | -0.021745 | 4.8131e-05 | 3.0705e-05 | 0.12949 | 0.12949 | 0.12949 | 0.99141 | -0.16423 | 0.99081 | -0.17589 | 35.5755
21 | -0.099199 | -0.025113 | 0.09946 | 0.025279 | 0.00026055 | 0.00016634 | 0.14854 | 0.14854 | 0.14854 | 0.99432 | -0.10824 | 0.99718 | -0.053682 | 40.8081
22 | 0.080237 | 0.020399 | -0.080134 | -0.020333 | 0.000103 | 6.5678e-05 | 0.12051 | 0.12051 | 0.12051 | 0.99158 | -0.16058 | 0.99019 | -0.18727 | 33.1075
23 | -0.09802 | -0.024861 | 0.0981 | 0.024912 | 8.004e-05 | 5.1098e-05 | 0.1472 | 0.1472 | 0.1472 | 0.99158 | -0.16058 | 0.99247 | -0.14361 | 40.4391
24 | 0.017782 | 0.0044624 | -0.017769 | -0.0044544 | 1.3378e-05 | 7.9163e-06 | 0.026687 | 0.026687 | 0.026687 | 0.99158 | -0.16058 | 0.99077 | -0.17637 | 7.3317
25 | 0.031533 | 0.0079249 | -0.03151 | -0.0079105 | 2.3089e-05 | 1.4421e-05 | 0.047286 | 0.047286 | 0.047286 | 0.99247 | -0.14361 | 0.99167 | -0.15896 | 12.9906
26 | -0.12963 | -0.032837 | 0.1298 | 0.032941 | 0.00016285 | 0.00010407 | 0.19448 | 0.19448 | 0.19448 | 0.99247 | -0.14361 | 0.99383 | -0.11749 | 53.4296
27 | 0.013904 | 0.0034857 | -0.013898 | -0.0034828 | 5.0943e-06 | 2.8593e-06 | 0.020882 | 0.020882 | 0.020882 | 0.99077 | -0.17637 | 0.99037 | -0.18406 | 5.7368
28 | 0.03151 | 0.0079105 | -0.031492 | -0.0078992 | 1.8016e-05 | 1.1253e-05 | 0.047286 | 0.047286 | 0.047286 | 0.99167 | -0.15896 | 0.99105 | -0.17095 | 12.9907
29 | 0.027392 | 0.0068717 | -0.027389 | -0.0068698 | 3.0986e-06 | 1.9202e-06 | 0.04113 | 0.04113 | 0.04113 | 0.99105 | -0.17095 | 0.99093 | -0.17332 | 11.2995
30 | -0.1298 | -0.032941 | 0.13019 | 0.033194 | 0.00039602 | 0.00025309 | 0.19448 | 0.19448 | 0.19448 | 0.99383 | -0.11749 | 0.99714 | -0.05427 | 53.4296
31 | -0.13654 | -0.034785 | 0.13678 | 0.034936 | 0.00023537 | 0.00015044 | 0.20396 | 0.20396 | 0.20396 | 0.99714 | -0.05427 | 0.99902 | -0.018607 | 56.0326
32 | 0.0023173 | 0.00057977 | -0.002317 | -0.00058044 | 3.0863e-07 | -6.7452e-07 | 0.0034829 | 0.0034832 | 0.0034832 | 0.98993 | -0.19267 | 0.98978 | -0.19547 | 0.95693
33 | -0.0023173 | -0.00057977 | 0.0023173 | 0.0005797 | 3.4e-08 | -7.4334e-08 | 0.0034829 | 0.0034829 | 0.0034829 | 0.98993 | -0.19267 | 0.98994 | -0.19236 | 0.95684
34 | 0.002317 | 0.00058044 | -0.0023169 | -0.00058067 | 1.0197e-07 | -2.2277e-07 | 0.0034832 | 0.0034833 | 0.0034833 | 0.98978 | -0.19547 | 0.98974 | -0.19639 | 0.95696
35 | -0.0060508 | -0.0015154 | 0.0060515 | 0.0015156 | 7.8057e-07 | 1.7597e-07 | 0.0090947 | 0.0090946 | 0.0090947 | 0.98994 | -0.19236 | 0.99008 | -0.18965 | 2.4985
36 | 0.0085484 | 0.0021453 | -0.0085384 | -0.002141 | 1.0034e-05 | 4.3403e-06 | 0.012849 | 0.012849 | 0.012849 | 0.99007 | -0.18995 | 0.98881 | -0.21458 | 3.5301
37 | -0.0085484 | -0.0021453 | 0.0085515 | 0.0021467 | 3.1346e-06 | 1.3547e-06 | 0.012849 | 0.012848 | 0.012849 | 0.99007 | -0.18995 | 0.99047 | -0.18226 | 3.5299
38 | 0.0085384 | 0.002141 | -0.0085363 | -0.0021401 | 2.0469e-06 | 8.8608e-07 | 0.012849 | 0.01285 | 0.01285 | 0.98881 | -0.21458 | 0.98855 | -0.21961 | 3.5301
39 | -0.011457 | -0.0028749 | 0.01146 | 0.0028762 | 2.5486e-06 | 1.3358e-06 | 0.017213 | 0.017213 | 0.017213 | 0.99047 | -0.18226 | 0.99071 | -0.17759 | 4.729
40 | 0.041495 | 0.010434 | -0.041468 | -0.010417 | 2.7491e-05 | 1.7356e-05 | 0.062614 | 0.062614 | 0.062614 | 0.98633 | -0.26255 | 0.98562 | -0.27643 | 17.2015
41 | -0.041495 | -0.010434 | 0.041504 | 0.01044 | 9.1216e-06 | 5.7586e-06 | 0.062614 | 0.062613 | 0.062614 | 0.98633 | -0.26255 | 0.98657 | -0.25795 | 17.2015
42 | 0.041468 | 0.010417 | -0.041422 | -0.010388 | 4.5821e-05 | 2.8929e-05 | 0.062614 | 0.062614 | 0.062614 | 0.98562 | -0.27643 | 0.98443 | -0.29961 | 17.2016
43 | -0.054306 | -0.013648 | 0.054365 | 0.013686 | 5.8529e-05 | 3.7161e-05 | 0.081922 | 0.081922 | 0.081922 | 0.98657 | -0.25795 | 0.98773 | -0.2354 | 22.506
44 | 0.034994 | 0.0087771 | -0.034976 | -0.0087654 | 1.8728e-05 | 1.1759e-05 | 0.052898 | 0.052898 | 0.052898 | 0.98443 | -0.29961 | 0.98386 | -0.31085 | 14.5325
45 | 0.079017 | 0.019947 | -0.078876 | -0.019857 | 0.00014101 | 8.9902e-05 | 0.11872 | 0.11872 | 0.11872 | 0.99081 | -0.17589 | 0.98888 | -0.21321 | 32.6157
46 | 0.0076449 | 0.0019167 | -0.0076438 | -0.0019163 | 1.0528e-06 | 4.0206e-07 | 0.011508 | 0.011508 | 0.011508 | 0.98855 | -0.21961 | 0.9884 | -0.2225 | 3.1615
47 | 0.068593 | 0.017339 | -0.068471 | -0.017261 | 0.00012191 | 7.7636e-05 | 0.10352 | 0.10352 | 0.10352 | 0.98644 | -0.25974 | 0.98452 | -0.29687 | 28.4405
48 | 0.0054391 | 0.0013631 | -0.0054384 | -0.001363 | 7.4264e-07 | 1.0585e-07 | 0.0082381 | 0.0082383 | 0.0082383 | 0.98244 | -0.33741 | 0.98229 | -0.34028 | 2.2633
49 | -0.062729 | -0.015787 | 0.062821 | 0.015845 | 9.1919e-05 | 5.8483e-05 | 0.094985 | 0.094985 | 0.094985 | 0.98295 | -0.32749 | 0.98452 | -0.29687 | 26.0948
50 | 0.012669 | 0.0031787 | -0.01266 | -0.0031738 | 8.9572e-06 | 4.9312e-06 | 0.019304 | 0.019305 | 0.019305 | 0.97663 | -0.45118 | 0.97588 | -0.46602 | 5.3035
51 | -0.10144 | -0.025776 | 0.10171 | 0.025944 | 0.00026294 | 0.00016788 | 0.1515 | 0.1515 | 0.1515 | 0.99718 | -0.053682 | 1 | 0 | 41.6208
52 | 0.0098629 | 0.0024714 | -0.0098602 | -0.0024701 | 2.6288e-06 | 1.2718e-06 | 0.014819 | 0.014819 | 0.014819 | 0.99037 | -0.18406 | 0.99008 | -0.18965 | 4.0711
53 | 0.018376 | 0.0046109 | -0.018372 | -0.0046086 | 3.7409e-06 | 2.2254e-06 | 0.027596 | 0.027596 | 0.027596 | 0.99093 | -0.17332 | 0.99071 | -0.17759 | 7.5813
54 | -0.14238 | -0.03634 | 0.14251 | 0.036421 | 0.00012813 | 8.1603e-05 | 0.2123 | 0.2123 | 0.2123 | 0.99902 | -0.018607 | 1 | 0 | 29.1625
55 | -0.0049491 | -0.0012404 | 0.0049493 | 0.0012404 | 1.2712e-07 | 4.9227e-09 | 0.007495 | 0.007495 | 0.007495 | 0.98257 | -0.33601 | 0.9826 | -0.33547 | 2.0591
56 | -0.0080024 | -0.0020056 | 0.0080039 | 0.0020062 | 1.5818e-06 | 6.4844e-07 | 0.012119 | 0.012118 | 0.012119 | 0.9826 | -0.33547 | 0.98281 | -0.33132 | 3.3293
57 | -0.067239 | -0.016912 | 0.06731 | 0.016958 | 7.1358e-05 | 4.5432e-05 | 0.10132 | 0.10132 | 0.10132 | 0.98773 | -0.2354 | 0.98888 | -0.21321 | 27.8343
58 | 0.015071 | 0.0037784 | -0.015068 | -0.0037764 | 3.6226e-06 | 2.0824e-06 | 0.022795 | 0.022795 | 0.022795 | 0.98386 | -0.31085 | 0.9836 | -0.31589 | 6.2623
59 | 0.019904 | 0.0049869 | -0.019895 | -0.0049811 | 9.7245e-06 | 5.8605e-06 | 0.030103 | 0.030104 | 0.030104 | 0.98386 | -0.31085 | 0.98333 | -0.32111 | 8.2702
60 | -0.0071592 | -0.0017943 | 0.0071593 | 0.0017943 | 6.4771e-08 | 2.2369e-08 | 0.010774 | 0.010774 | 0.010774 | 0.98876 | -0.21542 | 0.98877 | -0.21523 | 2.9599
61 | -0.011565 | -0.0028985 | 0.011566 | 0.0028991 | 1.1098e-06 | 5.8496e-07 | 0.017404 | 0.017404 | 0.017404 | 0.98877 | -0.21523 | 0.98888 | -0.21321 | 4.7814
62 | 0.0076438 | 0.0019163 | -0.0076422 | -0.0019157 | 1.6145e-06 | 6.1669e-07 | 0.011508 | 0.011508 | 0.011508 | 0.9884 | -0.2225 | 0.98817 | -0.22694 | 3.1615
63 | -0.0041103 | -0.0010301 | 0.0041108 | 0.00103 | 4.9182e-07 | -1.0142e-07 | 0.0062713 | 0.0062712 | 0.0062713 | 0.97527 | -0.47793 | 0.9754 | -0.47542 | 1.7229
64 | -0.0091576 | -0.0022949 | 0.0091596 | 0.0022958 | 2.015e-06 | 9.4585e-07 | 0.01397 | 0.01397 | 0.01397 | 0.9754 | -0.47542 | 0.97563 | -0.4708 | 3.838
65 | -0.010414 | -0.0026101 | 0.010416 | 0.0026113 | 2.3728e-06 | 1.2053e-06 | 0.015883 | 0.015883 | 0.015883 | 0.97563 | -0.4708 | 0.97588 | -0.46602 | 4.3634
66 | 0.0063646 | 0.0015952 | -0.0063638 | -0.0015949 | 8.5703e-07 | 2.3567e-07 | 0.0096286 | 0.0096287 | 0.0096287 | 0.9836 | -0.31589 | 0.98345 | -0.31872 | 2.6453
67 | 0.010969 | 0.002744 | -0.010968 | -0.0027435 | 1.0481e-06 | 5.4208e-07 | 0.016596 | 0.016596 | 0.016596 | 0.98333 | -0.32111 | 0.98323 | -0.32312 | 4.5594
68 | 0.010968 | 0.0027435 | -0.010963 | -0.0027412 | 4.2755e-06 | 2.2116e-06 | 0.016596 | 0.016597 | 0.016597 | 0.98323 | -0.32312 | 0.98281 | -0.33132 | 4.5595
69 | 0.0029593 | 0.00073505 | -0.0029546 | -0.00074 | 4.757e-06 | -4.9522e-06 | 0.0044782 | 0.004481 | 0.004481 | 0.98281 | -0.33132 | 0.98109 | -0.36521 | 1.2311
70 | 0.0076422 | 0.0019157 | -0.0076394 | -0.0019146 | 2.842e-06 | 1.0861e-06 | 0.011508 | 0.011508 | 0.011508 | 0.98817 | -0.22694 | 0.98777 | -0.23474 | 3.1616
71 | 0.0068598 | 0.0017192 | -0.0068566 | -0.0017182 | 3.2189e-06 | 1.0318e-06 | 0.010334 | 0.010334 | 0.010334 | 0.98777 | -0.23474 | 0.98726 | -0.2446 | 2.8391
72 | 0.0029546 | 0.00074 | -0.0029542 | -0.00074039 | 3.7693e-07 | -3.9077e-07 | 0.004481 | 0.0044813 | 0.0044813 | 0.98109 | -0.36521 | 0.98095 | -0.36789 | 1.2311
73 | 0.0068566 | 0.0017182 | -0.0068547 | -0.0017176 | 1.8964e-06 | 6.0838e-07 | 0.010334 | 0.010334 | 0.010334 | 0.98726 | -0.2446 | 0.98697 | -0.2504 | 2.8391
74 | 0.0059526 | 0.0014915 | -0.0059523 | -0.0014914 | 2.5212e-07 | 5.4682e-08 | 0.0089744 | 0.0089744 | 0.0089744 | 0.98697 | -0.2504 | 0.98692 | -0.25129 | 2.4655
75 | 0.0050434 | 0.0012636 | -0.005043 | -0.0012636 | 3.1426e-07 | 1.5934e-08 | 0.0076039 | 0.007604 | 0.007604 | 0.98692 | -0.25129 | 0.98685 | -0.2526 | 2.089
76 | 0.0042567 | 0.0010665 | -0.0042566 | -0.0010665 | 1.1745e-07 | -2.1966e-08 | 0.0064184 | 0.0064184 | 0.0064184 | 0.98685 | -0.2526 | 0.98682 | -0.25318 | 1.7633
77 | 0.0035034 | 0.00087777 | -0.0035032 | -0.00087789 | 2.0545e-07 | -1.1931e-07 | 0.0052827 | 0.0052828 | 0.0052828 | 0.98682 | -0.25318 | 0.98676 | -0.25441 | 1.4513
78 | 0.0013797 | 0.00034567 | -0.0013796 | -0.00034577 | 1.3928e-08 | -1.007e-07 | 0.0020805 | 0.0020805 | 0.0020805 | 0.98676 | -0.25441 | 0.98675 | -0.25462 | 0.57157

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.25307 | 0.064171

## res_load
| p_mw | q_mvar
0 | 0.0031634 | 0.00079283
1 | 0.010109 | 0.0025337
2 | 0.0015403 | 0.00038604
3 | 0.0011867 | 0.0002974
4 | 0.0018362 | 0.00046019
5 | 0.0092843 | 0.0023269
6 | 0.0021982 | 0.00055092
7 | 0.012728 | 0.0031899
8 | 0.0039344 | 0.00098606
9 | 0.0038655 | 0.00096878
10 | 0.0040998 | 0.0010275
11 | 0.0063494 | 0.0015913
12 | 0.0021894 | 0.00054872
13 | 0.0037334 | 0.00093569
14 | 0.0023169 | 0.00058067
15 | 0.0029055 | 0.00072818
16 | 0.012802 | 0.0032084
17 | 0.0064275 | 0.0016109
18 | 0.0071737 | 0.0017979
19 | 0.00089145 | 0.00022342
20 | 0.0014744 | 0.00036952
21 | 0.005508 | 0.0013804
22 | 0.0055217 | 0.0013839
23 | 0.005553 | 0.0013917
24 | 0.0022265 | 0.00055801
25 | 0.0019825 | 0.00049687
26 | 0.0040356 | 0.0010114
27 | 0.0090132 | 0.0022589
28 | 0.0056021 | 0.001404
29 | 0.0049491 | 0.0012404
30 | 0.0030531 | 0.00076518
31 | 0.0038087 | 0.00095454
32 | 0.0069126 | 0.0017325
33 | 0.012874 | 0.0032266
34 | 0.0071592 | 0.0017943
35 | 0.0044058 | 0.0011042
36 | 0.0054384 | 0.001363
37 | 0.0056495 | 0.0014159
38 | 0.0041103 | 0.0010301
39 | 0.0050468 | 0.0012648
40 | 0.0012541 | 0.0003143
41 | 0.0022442 | 0.00056245
42 | 0.0072041 | 0.0018055
43 | 0.0087031 | 0.0021812
44 | 0.008926 | 0.0022371
45 | 0.0063638 | 0.0015949
46 | 0.00077956 | 0.00019538
47 | 0.00090213 | 0.00022609
48 | 0.0029542 | 0.00074039
49 | 0.00090895 | 0.00022781
50 | 0.00078631 | 0.00019707
51 | 0.00075318 | 0.00018876
52 | 0.0021236 | 0.00053222
53 | 0.0013796 | 0.00034577

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1