## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-57_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-57_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-57_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_261-57_0_5_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_261-57_0_5_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_261-57_0_5_node_48 | 0.4 | n |  | TRUE
6 | bus_LV_261-57_0_5_node_145 | 0.4 | n |  | TRUE
7 | bus_LV_261-57_0_5_node_9 | 0.4 | n |  | TRUE
8 | bus_LV_261-57_0_5_node_5 | 0.4 | n |  | TRUE
9 | bus_LV_261-57_0_5_node_6 | 0.4 | n |  | TRUE
10 | bus_LV_261-57_0_5_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_261-57_0_5_node_41 | 0.4 | n |  | TRUE
12 | bus_LV_261-57_0_5_node_10 | 0.4 | n |  | TRUE
13 | bus_LV_261-57_0_5_node_23 | 0.4 | n |  | TRUE
14 | bus_LV_261-57_0_5_node_72 | 0.4 | n |  | TRUE
15 | bus_LV_261-57_0_5_node_138 | 0.4 | n |  | TRUE
16 | bus_LV_261-57_0_5_node_12 | 0.4 | n |  | TRUE
17 | bus_LV_261-57_0_5_node_45 | 0.4 | n |  | TRUE
18 | bus_LV_261-57_0_5_node_26 | 0.4 | n |  | TRUE
19 | bus_LV_261-57_0_5_node_46 | 0.4 | n |  | TRUE
20 | bus_LV_261-57_0_5_node_13 | 0.4 | n |  | TRUE
21 | bus_LV_261-57_0_5_node_19 | 0.4 | n |  | TRUE
22 | bus_LV_261-57_0_5_node_87 | 0.4 | n |  | TRUE
23 | bus_LV_261-57_0_5_node_15 | 0.4 | n |  | TRUE
24 | bus_LV_261-57_0_5_node_139 | 0.4 | n |  | TRUE
25 | bus_LV_261-57_0_5_node_16 | 0.4 | n |  | TRUE
26 | bus_LV_261-57_0_5_node_29 | 0.4 | n |  | TRUE
27 | bus_LV_261-57_0_5_node_60 | 0.4 | n |  | TRUE
28 | bus_LV_261-57_0_5_node_17 | 0.4 | n |  | TRUE
29 | bus_LV_261-57_0_5_node_63 | 0.4 | n |  | TRUE
30 | bus_LV_261-57_0_5_node_64 | 0.4 | n |  | TRUE
31 | bus_LV_261-57_0_5_node_61 | 0.4 | n |  | TRUE
32 | bus_LV_261-57_0_5_node_81 | 0.4 | n |  | TRUE
33 | bus_LV_261-57_0_5_node_20 | 0.4 | n |  | TRUE
34 | bus_LV_261-57_0_5_node_44 | 0.4 | n |  | TRUE
35 | bus_LV_261-57_0_5_node_28 | 0.4 | n |  | TRUE
36 | bus_LV_261-57_0_5_node_152 | 0.4 | n |  | TRUE
37 | bus_LV_261-57_0_5_node_21 | 0.4 | n |  | TRUE
38 | bus_LV_261-57_0_5_node_38 | 0.4 | n |  | TRUE
39 | bus_LV_261-57_0_5_node_55 | 0.4 | n |  | TRUE
40 | bus_LV_261-57_0_5_node_25 | 0.4 | n |  | TRUE
41 | bus_LV_261-57_0_5_node_90 | 0.4 | n |  | TRUE
42 | bus_LV_261-57_0_5_node_30 | 0.4 | n |  | TRUE
43 | bus_LV_261-57_0_5_node_88 | 0.4 | n |  | TRUE
44 | bus_LV_261-57_0_5_node_153 | 0.4 | n |  | TRUE
45 | bus_LV_261-57_0_5_node_40 | 0.4 | n |  | TRUE
46 | bus_LV_261-57_0_5_node_99 | 0.4 | n |  | TRUE
47 | bus_LV_261-57_0_5_node_137 | 0.4 | n |  | TRUE
48 | bus_LV_261-57_0_5_node_89 | 0.4 | n |  | TRUE
49 | bus_LV_261-57_0_5_node_85 | 0.4 | n |  | TRUE
50 | bus_LV_261-57_0_5_node_37 | 0.4 | n |  | TRUE
51 | bus_LV_261-57_0_5_node_67 | 0.4 | n |  | TRUE
52 | bus_LV_261-57_0_5_node_31 | 0.4 | n |  | TRUE
53 | bus_LV_261-57_0_5_node_71 | 0.4 | n |  | TRUE
54 | bus_LV_261-57_0_5_node_33 | 0.4 | n |  | TRUE
55 | bus_LV_261-57_0_5_node_95 | 0.4 | n |  | TRUE
56 | bus_LV_261-57_0_5_node_96 | 0.4 | n |  | TRUE
57 | bus_LV_261-57_0_5_node_92 | 0.4 | n |  | TRUE
58 | bus_LV_261-57_0_5_node_34 | 0.4 | n |  | TRUE
59 | bus_LV_261-57_0_5_node_52 | 0.4 | n |  | TRUE
60 | bus_LV_261-57_0_5_node_53 | 0.4 | n |  | TRUE
61 | bus_LV_261-57_0_5_node_49 | 0.4 | n |  | TRUE
62 | bus_LV_261-57_0_5_node_35 | 0.4 | n |  | TRUE
63 | bus_LV_261-57_0_5_node_76 | 0.4 | n |  | TRUE
64 | bus_LV_261-57_0_5_node_79 | 0.4 | n |  | TRUE
65 | bus_LV_261-57_0_5_node_132 | 0.4 | n |  | TRUE
66 | bus_LV_261-57_0_5_node_111 | 0.4 | n |  | TRUE
67 | bus_LV_261-57_0_5_node_54 | 0.4 | n |  | TRUE
68 | bus_LV_261-57_0_5_node_39 | 0.4 | n |  | TRUE
69 | bus_LV_261-57_0_5_node_103 | 0.4 | n |  | TRUE
70 | bus_LV_261-57_0_5_node_104 | 0.4 | n |  | TRUE
71 | bus_LV_261-57_0_5_node_100 | 0.4 | n |  | TRUE
72 | bus_LV_261-57_0_5_node_83 | 0.4 | n |  | TRUE
73 | bus_LV_261-57_0_5_node_150 | 0.4 | n |  | TRUE
74 | bus_LV_261-57_0_5_node_149 | 0.4 | n |  | TRUE
75 | bus_LV_261-57_0_5_node_42 | 0.4 | n |  | TRUE
76 | bus_LV_261-57_0_5_node_43 | 0.4 | n |  | TRUE
77 | bus_LV_261-57_0_5_node_73 | 0.4 | n |  | TRUE
78 | bus_LV_261-57_0_5_node_70 | 0.4 | n |  | TRUE
79 | bus_LV_261-57_0_5_node_147 | 0.4 | n |  | TRUE
80 | bus_LV_261-57_0_5_node_47 | 0.4 | n |  | TRUE
81 | bus_LV_261-57_0_5_node_86 | 0.4 | n |  | TRUE
82 | bus_LV_261-57_0_5_node_133 | 0.4 | n |  | TRUE
83 | bus_LV_261-57_0_5_node_134 | 0.4 | n |  | TRUE
84 | bus_LV_261-57_0_5_node_58 | 0.4 | n |  | TRUE
85 | bus_LV_261-57_0_5_node_62 | 0.4 | n |  | TRUE
86 | bus_LV_261-57_0_5_node_82 | 0.4 | n |  | TRUE
87 | bus_LV_261-57_0_5_node_151 | 0.4 | n |  | TRUE
88 | bus_LV_261-57_0_5_node_65 | 0.4 | n |  | TRUE
89 | bus_LV_261-57_0_5_node_66 | 0.4 | n |  | TRUE
90 | bus_LV_261-57_0_5_node_115 | 0.4 | n |  | TRUE
91 | bus_LV_261-57_0_5_node_116 | 0.4 | n |  | TRUE
92 | bus_LV_261-57_0_5_node_101 | 0.4 | n |  | TRUE
93 | bus_LV_261-57_0_5_node_69 | 0.4 | n |  | TRUE
94 | bus_LV_261-57_0_5_node_112 | 0.4 | n |  | TRUE
95 | bus_LV_261-57_0_5_node_113 | 0.4 | n |  | TRUE
96 | bus_LV_261-57_0_5_node_93 | 0.4 | n |  | TRUE
97 | bus_LV_261-57_0_5_node_135 | 0.4 | n |  | TRUE
98 | bus_LV_261-57_0_5_node_75 | 0.4 | n |  | TRUE
99 | bus_LV_261-57_0_5_node_77 | 0.4 | n |  | TRUE
100 | bus_LV_261-57_0_5_node_131 | 0.4 | n |  | TRUE
101 | bus_LV_261-57_0_5_node_105 | 0.4 | n |  | TRUE
102 | bus_LV_261-57_0_5_node_108 | 0.4 | n |  | TRUE
103 | bus_LV_261-57_0_5_node_98 | 0.4 | n |  | TRUE
104 | bus_LV_261-57_0_5_node_117 | 0.4 | n |  | TRUE
105 | bus_LV_261-57_0_5_node_148 | 0.4 | n |  | TRUE
106 | bus_LV_261-57_0_5_node_50 | 0.4 | n |  | TRUE
107 | bus_LV_261-57_0_5_node_51 | 0.4 | n |  | TRUE
108 | bus_LV_261-57_0_5_node_91 | 0.4 | n |  | TRUE
109 | bus_LV_261-57_0_5_node_107 | 0.4 | n |  | TRUE
110 | bus_LV_261-57_0_5_node_136 | 0.4 | n |  | TRUE
111 | bus_LV_261-57_0_5_node_56 | 0.4 | n |  | TRUE
112 | bus_LV_261-57_0_5_node_57 | 0.4 | n |  | TRUE
113 | bus_LV_261-57_0_5_node_59 | 0.4 | n |  | TRUE
114 | bus_LV_261-57_0_5_node_84 | 0.4 | n |  | TRUE
115 | bus_LV_261-57_0_5_node_68 | 0.4 | n |  | TRUE
116 | bus_LV_261-57_0_5_node_74 | 0.4 | n |  | TRUE
117 | bus_LV_261-57_0_5_node_78 | 0.4 | n |  | TRUE
118 | bus_LV_261-57_0_5_node_80 | 0.4 | n |  | TRUE
119 | bus_LV_261-57_0_5_node_128 | 0.4 | n |  | TRUE
120 | bus_LV_261-57_0_5_node_125 | 0.4 | n |  | TRUE
121 | bus_LV_261-57_0_5_node_120 | 0.4 | n |  | TRUE
122 | bus_LV_261-57_0_5_node_94 | 0.4 | n |  | TRUE
123 | bus_LV_261-57_0_5_node_130 | 0.4 | n |  | TRUE
124 | bus_LV_261-57_0_5_node_114 | 0.4 | n |  | TRUE
125 | bus_LV_261-57_0_5_node_97 | 0.4 | n |  | TRUE
126 | bus_LV_261-57_0_5_node_102 | 0.4 | n |  | TRUE
127 | bus_LV_261-57_0_5_node_106 | 0.4 | n |  | TRUE
128 | bus_LV_261-57_0_5_node_109 | 0.4 | n |  | TRUE
129 | bus_LV_261-57_0_5_node_110 | 0.4 | n |  | TRUE
130 | bus_LV_261-57_0_5_node_126 | 0.4 | n |  | TRUE
131 | bus_LV_261-57_0_5_node_118 | 0.4 | n |  | TRUE
132 | bus_LV_261-57_0_5_node_124 | 0.4 | n |  | TRUE
133 | bus_LV_261-57_0_5_node_129 | 0.4 | n |  | TRUE
134 | bus_LV_261-57_0_5_node_127 | 0.4 | n |  | TRUE
135 | bus_LV_261-57_0_5_node_119 | 0.4 | n |  | TRUE
136 | bus_LV_261-57_0_5_node_121 | 0.4 | n |  | TRUE
137 | bus_LV_261-57_0_5_node_122 | 0.4 | n |  | TRUE
138 | bus_LV_261-57_0_5_node_123 | 0.4 | n |  | TRUE
139 | bus_LV_261-57_0_5_node_140 | 0.4 | n |  | TRUE
140 | bus_LV_261-57_0_5_node_141 | 0.4 | n |  | TRUE
141 | bus_LV_261-57_0_5_node_142 | 0.4 | n |  | TRUE
142 | bus_LV_261-57_0_5_node_143 | 0.4 | n |  | TRUE
143 | bus_LV_261-57_0_5_node_144 | 0.4 | n |  | TRUE
144 | bus_LV_261-57_0_5_node_146 | 0.4 | n |  | TRUE
145 | bus_MV_542_0_node_48 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-57_0_5_load_0 | 0 | 0.0019607 | 0.0004914 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-57_0_5_load_1 | 1 | 0.0020447 | 0.00051245 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-57_0_5_load_2 | 2 | 0.001959 | 0.00049097 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-57_0_5_load_3 | 3 | 0.0019354 | 0.00048507 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-57_0_5_load_4 | 4 | 0.0019609 | 0.00049144 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-57_0_5_load_48 | 5 | 0.001938 | 0.0004857 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-57_0_5_load_145 | 6 | 0.001959 | 0.00049098 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-57_0_5_load_9 | 7 | 0.0020456 | 0.00051268 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-57_0_5_load_5 | 8 | 0.0019393 | 0.00048605 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-57_0_5_load_138 | 15 | 0.0079548 | 0.0019937 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-57_0_5_load_46 | 19 | 0.0083326 | 0.0020883 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-57_0_5_load_87 | 22 | 0.004435 | 0.0011115 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-57_0_5_load_139 | 24 | 0.0096867 | 0.0024277 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-57_0_5_load_60 | 27 | 0.0046802 | 0.001173 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-57_0_5_load_63 | 29 | 0.023762 | 0.0059554 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-57_0_5_load_64 | 30 | 0.0044853 | 0.0011241 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-57_0_5_load_61 | 31 | 0.005348 | 0.0013403 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_261-57_0_5_load_81 | 32 | 0.0069498 | 0.0017418 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_261-57_0_5_load_152 | 36 | 0.0079525 | 0.0019931 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_261-57_0_5_load_55 | 39 | 0.011581 | 0.0029025 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_261-57_0_5_load_90 | 41 | 0.011937 | 0.0029918 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_261-57_0_5_load_88 | 43 | 0.0038999 | 0.00097741 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_261-57_0_5_load_153 | 44 | 0.0078186 | 0.0019595 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_261-57_0_5_load_137 | 47 | 0.0029536 | 0.00074023 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_261-57_0_5_load_89 | 48 | 0.0050992 | 0.001278 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_261-57_0_5_load_85 | 49 | 0.0044297 | 0.0011102 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_261-57_0_5_load_67 | 51 | 0.0068518 | 0.0017172 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_261-57_0_5_load_71 | 53 | 0.0094753 | 0.0023747 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_261-57_0_5_load_95 | 55 | 0.001842 | 0.00046164 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_261-57_0_5_load_96 | 56 | 0.0019619 | 0.00049169 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_261-57_0_5_load_92 | 57 | 0.0018947 | 0.00047487 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_261-57_0_5_load_52 | 59 | 0.0018923 | 0.00047425 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_261-57_0_5_load_53 | 60 | 0.0017696 | 0.00044351 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_261-57_0_5_load_49 | 61 | 0.0018902 | 0.00047372 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_261-57_0_5_load_76 | 63 | 0.0047064 | 0.0011795 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_261-57_0_5_load_79 | 64 | 0.0047028 | 0.0011786 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_261-57_0_5_load_132 | 65 | 0.0045729 | 0.0011461 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_261-57_0_5_load_111 | 66 | 0.0019635 | 0.00049211 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_261-57_0_5_load_54 | 67 | 0.024513 | 0.0061435 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_261-57_0_5_load_103 | 69 | 0.0017319 | 0.00043405 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_261-57_0_5_load_104 | 70 | 0.0016602 | 0.00041608 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_261-57_0_5_load_100 | 71 | 0.0016477 | 0.00041295 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_261-57_0_5_load_83 | 72 | 0.012776 | 0.003202 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_261-57_0_5_load_150 | 73 | 0.0070683 | 0.0017715 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_261-57_0_5_load_149 | 74 | 0.0069717 | 0.0017473 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_261-57_0_5_load_42 | 75 | 0.0017363 | 0.00043515 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_261-57_0_5_load_73 | 77 | 0.016887 | 0.0042322 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_261-57_0_5_load_70 | 78 | 0.009356 | 0.0023448 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_261-57_0_5_load_147 | 79 | 0.0017378 | 0.00043554 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_261-57_0_5_load_47 | 80 | 0.0083308 | 0.0020879 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_261-57_0_5_load_86 | 81 | 0.0033777 | 0.00084652 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_261-57_0_5_load_133 | 82 | 0.001891 | 0.00047394 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_261-57_0_5_load_134 | 83 | 0.0018881 | 0.0004732 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_261-57_0_5_load_58 | 84 | 0.0032874 | 0.0008239 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_261-57_0_5_load_62 | 85 | 0.010681 | 0.002677 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_261-57_0_5_load_82 | 86 | 0.0058531 | 0.0014669 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_261-57_0_5_load_151 | 87 | 0.0052877 | 0.0013252 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_261-57_0_5_load_65 | 88 | 0.017581 | 0.0044062 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_261-57_0_5_load_66 | 89 | 0.016444 | 0.0041214 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_261-57_0_5_load_115 | 90 | 0.0048302 | 0.0012106 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_261-57_0_5_load_116 | 91 | 0.0054189 | 0.0013581 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_261-57_0_5_load_101 | 92 | 0.009844 | 0.0024671 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_261-57_0_5_load_69 | 93 | 0.0097871 | 0.0024529 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_261-57_0_5_load_112 | 94 | 0.001829 | 0.0004584 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_261-57_0_5_load_113 | 95 | 0.0018247 | 0.00045731 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_261-57_0_5_load_93 | 96 | 0.0018876 | 0.00047307 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_261-57_0_5_load_135 | 97 | 0.0017705 | 0.00044372 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_261-57_0_5_load_75 | 98 | 0.0047064 | 0.0011795 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_261-57_0_5_load_77 | 99 | 0.004509 | 0.0011301 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_261-57_0_5_load_131 | 100 | 0.0018656 | 0.00046757 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_261-57_0_5_load_105 | 101 | 0.0018703 | 0.00046875 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_261-57_0_5_load_108 | 102 | 0.0017705 | 0.00044372 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_261-57_0_5_load_98 | 103 | 0.0016989 | 0.00042578 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_261-57_0_5_load_117 | 104 | 0.0053302 | 0.0013359 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_261-57_0_5_load_148 | 105 | 0.0017384 | 0.00043569 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_261-57_0_5_load_50 | 106 | 0.0019204 | 0.0004813 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_261-57_0_5_load_51 | 107 | 0.0018584 | 0.00046577 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_261-57_0_5_load_91 | 108 | 0.0018628 | 0.00046687 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_261-57_0_5_load_107 | 109 | 0.0018311 | 0.00045891 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_261-57_0_5_load_136 | 110 | 0.0017705 | 0.00044372 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_261-57_0_5_load_56 | 111 | 0.0053023 | 0.0013289 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_261-57_0_5_load_57 | 112 | 0.0063989 | 0.0016037 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_261-57_0_5_load_59 | 113 | 0.021734 | 0.005447 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_261-57_0_5_load_84 | 114 | 0.015523 | 0.0038906 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_261-57_0_5_load_68 | 115 | 0.016871 | 0.0042282 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_261-57_0_5_load_74 | 116 | 0.0047064 | 0.0011795 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_261-57_0_5_load_78 | 117 | 0.0018099 | 0.00045359 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_261-57_0_5_load_80 | 118 | 0.004509 | 0.0011301 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_261-57_0_5_load_128 | 119 | 0.0018213 | 0.00045646 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_261-57_0_5_load_125 | 120 | 0.0045124 | 0.0011309 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_261-57_0_5_load_120 | 121 | 0.0018594 | 0.00046601 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_261-57_0_5_load_94 | 122 | 0.0018791 | 0.00047095 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_261-57_0_5_load_130 | 123 | 0.0018714 | 0.00046902 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_261-57_0_5_load_114 | 124 | 0.0018627 | 0.00046684 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_261-57_0_5_load_97 | 125 | 0.0027078 | 0.00067863 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_261-57_0_5_load_102 | 126 | 0.010016 | 0.0025103 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_261-57_0_5_load_106 | 127 | 0.0025994 | 0.00065146 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_261-57_0_5_load_109 | 128 | 0.0017705 | 0.00044372 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_261-57_0_5_load_110 | 129 | 0.0018601 | 0.00046617 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_261-57_0_5_load_126 | 130 | 0.0045134 | 0.0011312 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_261-57_0_5_load_118 | 131 | 0.0018247 | 0.00045731 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_261-57_0_5_load_124 | 132 | 0.0018473 | 0.00046298 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_261-57_0_5_load_129 | 133 | 0.0018247 | 0.00045731 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_261-57_0_5_load_127 | 134 | 0.0018613 | 0.00046649 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_261-57_0_5_load_119 | 135 | 0.001862 | 0.00046667 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_261-57_0_5_load_121 | 136 | 0.0018247 | 0.00045731 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_261-57_0_5_load_122 | 137 | 0.0045136 | 0.0011312 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_261-57_0_5_load_123 | 138 | 0.0018327 | 0.00045931 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_261-57_0_5_load_140 | 139 | 0.0017378 | 0.00043554 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_261-57_0_5_load_141 | 140 | 0.0019426 | 0.00048686 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_261-57_0_5_load_142 | 141 | 0.0017369 | 0.0004353 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_261-57_0_5_load_143 | 142 | 0.0019393 | 0.00048605 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_261-57_0_5_load_144 | 143 | 0.001737 | 0.00043534 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_261-57_0_5_load_146 | 144 | 0.0020958 | 0.00052525 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 116 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-57_0_5_line_0 |  | 0 | 1 | 0.016822 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-57_0_5_line_1 |  | 0 | 2 | 0.0066039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-57_0_5_line_2 |  | 1 | 3 | 0.0068781 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-57_0_5_line_3 |  | 2 | 4 | 0.0066039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-57_0_5_line_4 |  | 3 | 5 | 0.0066729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_261-57_0_5_line_5 |  | 4 | 6 | 0.0066039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_261-57_0_5_line_6 |  | 5 | 7 | 0.006882 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_261-57_0_5_line_7 |  | 7 | 9 | 0.0078191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_261-57_0_5_line_8 |  | 8 | 9 | 0.014195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_261-57_0_5_line_9 |  | 9 | 10 | 0.017533 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_261-57_0_5_line_10 |  | 10 | 11 | 0.029173 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_261-57_0_5_line_11 |  | 11 | 73 | 0.015635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_261-57_0_5_line_12 |  | 11 | 74 | 0.014286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-57_0_5_line_13 |  | 11 | 68 | 0.0088734 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
14 | LV_261-57_0_5_line_14 |  | 12 | 13 | 0.011915 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_261-57_0_5_line_15 |  | 12 | 14 | 0.025506 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_261-57_0_5_line_16 |  | 12 | 15 | 0.020912 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_261-57_0_5_line_17 |  | 13 | 38 | 0.050882 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_261-57_0_5_line_18 |  | 14 | 77 | 0.039906 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_261-57_0_5_line_19 |  | 14 | 78 | 0.015497 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_261-57_0_5_line_20 |  | 15 | 23 | 0.03237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_261-57_0_5_line_21 |  | 16 | 17 | 0.03843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_261-57_0_5_line_22 |  | 16 | 18 | 0.018805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_261-57_0_5_line_23 |  | 16 | 19 | 0.015668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_261-57_0_5_line_24 |  | 17 | 79 | 0.075901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_261-57_0_5_line_25 |  | 18 | 44 | 0.02535 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_261-57_0_5_line_26 |  | 18 | 45 | 0.078598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_261-57_0_5_line_27 |  | 19 | 80 | 0.017594 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_261-57_0_5_line_28 |  | 20 | 21 | 0.01751 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_261-57_0_5_line_29 |  | 20 | 22 | 0.013059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_261-57_0_5_line_30 |  | 21 | 32 | 0.01061 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_261-57_0_5_line_31 |  | 22 | 81 | 0.01763 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_261-57_0_5_line_32 |  | 23 | 24 | 0.004434 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_261-57_0_5_line_33 |  | 25 | 26 | 0.052005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_261-57_0_5_line_34 |  | 25 | 27 | 0.033877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_261-57_0_5_line_35 |  | 26 | 43 | 0.013332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_261-57_0_5_line_36 |  | 26 | 48 | 0.020314 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_261-57_0_5_line_37 |  | 26 | 49 | 0.033984 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_261-57_0_5_line_38 |  | 26 | 28 | 0.035516 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_261-57_0_5_line_39 |  | 27 | 84 | 0.01819 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_261-57_0_5_line_40 |  | 28 | 29 | 0.018155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_261-57_0_5_line_41 |  | 28 | 30 | 0.012349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_261-57_0_5_line_42 |  | 28 | 31 | 0.015287 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_261-57_0_5_line_43 |  | 31 | 85 | 0.0022335 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_261-57_0_5_line_44 |  | 32 | 86 | 0.01874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_261-57_0_5_line_45 |  | 33 | 34 | 0.001814 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_261-57_0_5_line_46 |  | 33 | 35 | 0.0094896 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_261-57_0_5_line_47 |  | 33 | 36 | 0.012991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_261-57_0_5_line_48 |  | 34 | 80 | 0.013801 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_261-57_0_5_line_49 |  | 34 | 76 | 0.026273 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_261-57_0_5_line_50 |  | 35 | 46 | 0.001894 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_261-57_0_5_line_51 |  | 35 | 47 | 0.012712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_261-57_0_5_line_52 |  | 36 | 87 | 0.017218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_261-57_0_5_line_53 |  | 37 | 38 | 0.035795 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_261-57_0_5_line_54 |  | 37 | 39 | 0.023727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_261-57_0_5_line_55 |  | 38 | 67 | 0.02416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_261-57_0_5_line_56 |  | 40 | 41 | 0.012469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_261-57_0_5_line_57 |  | 40 | 42 | 0.038955 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
58 | LV_261-57_0_5_line_58 |  | 40 | 43 | 0.027353 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_261-57_0_5_line_59 |  | 42 | 50 | 0.014687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
60 | LV_261-57_0_5_line_60 |  | 42 | 51 | 0.040708 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_261-57_0_5_line_61 |  | 45 | 72 | 0.013471 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_261-57_0_5_line_62 |  | 46 | 92 | 0.01427 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_261-57_0_5_line_63 |  | 47 | 52 | 0.015182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_261-57_0_5_line_64 |  | 49 | 81 | 0.017068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_261-57_0_5_line_65 |  | 50 | 66 | 0.013094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
66 | LV_261-57_0_5_line_66 |  | 51 | 89 | 0.059043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_261-57_0_5_line_67 |  | 52 | 53 | 0.014686 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_261-57_0_5_line_68 |  | 53 | 93 | 0.0044913 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_261-57_0_5_line_69 |  | 54 | 55 | 0.011415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
70 | LV_261-57_0_5_line_70 |  | 54 | 56 | 0.0094709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_261-57_0_5_line_71 |  | 54 | 57 | 0.012594 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
72 | LV_261-57_0_5_line_72 |  | 55 | 94 | 0.0058388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
73 | LV_261-57_0_5_line_73 |  | 56 | 95 | 0.022943 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_261-57_0_5_line_74 |  | 57 | 96 | 0.0058744 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
75 | LV_261-57_0_5_line_75 |  | 58 | 59 | 0.011505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_261-57_0_5_line_76 |  | 58 | 60 | 0.012277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_261-57_0_5_line_77 |  | 58 | 61 | 0.0093403 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_261-57_0_5_line_78 |  | 59 | 83 | 0.0060476 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_261-57_0_5_line_79 |  | 60 | 97 | 0.0058638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_261-57_0_5_line_80 |  | 62 | 63 | 0.011927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
81 | LV_261-57_0_5_line_81 |  | 62 | 64 | 0.0095328 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
82 | LV_261-57_0_5_line_82 |  | 62 | 65 | 0.012017 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
83 | LV_261-57_0_5_line_83 |  | 63 | 98 | 0.0060059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
84 | LV_261-57_0_5_line_84 |  | 64 | 99 | 0.019871 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
85 | LV_261-57_0_5_line_85 |  | 65 | 100 | 0.0058717 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
86 | LV_261-57_0_5_line_86 |  | 66 | 94 | 0.0060331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
87 | LV_261-57_0_5_line_87 |  | 68 | 69 | 0.0092618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
88 | LV_261-57_0_5_line_88 |  | 68 | 70 | 0.012464 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_261-57_0_5_line_89 |  | 68 | 71 | 0.011703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_261-57_0_5_line_90 |  | 69 | 101 | 0.020157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
91 | LV_261-57_0_5_line_91 |  | 70 | 102 | 0.0057016 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_261-57_0_5_line_92 |  | 71 | 103 | 0.0058345 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_261-57_0_5_line_93 |  | 73 | 87 | 0.016187 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_261-57_0_5_line_94 |  | 74 | 104 | 0.016323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_261-57_0_5_line_95 |  | 75 | 76 | 0.025688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_261-57_0_5_line_96 |  | 77 | 116 | 0.020128 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_261-57_0_5_line_97 |  | 78 | 115 | 0.0042796 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_261-57_0_5_line_98 |  | 79 | 105 | 0.0056686 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_261-57_0_5_line_99 |  | 82 | 83 | 0.0060456 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_261-57_0_5_line_100 |  | 84 | 111 | 0.0066644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_261-57_0_5_line_101 |  | 88 | 89 | 0.025081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_261-57_0_5_line_102 |  | 90 | 91 | 0.033335 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_261-57_0_5_line_103 |  | 91 | 104 | 0.016388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_261-57_0_5_line_104 |  | 92 | 126 | 0.023664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_261-57_0_5_line_105 |  | 95 | 124 | 0.00036318 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_261-57_0_5_line_106 |  | 96 | 122 | 0.0058731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
107 | LV_261-57_0_5_line_107 |  | 97 | 110 | 0.0058659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_261-57_0_5_line_108 |  | 98 | 116 | 0.0060059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
109 | LV_261-57_0_5_line_109 |  | 99 | 117 | 0.00019382 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
110 | LV_261-57_0_5_line_110 |  | 100 | 123 | 0.005669 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
111 | LV_261-57_0_5_line_111 |  | 101 | 127 | 0.00016135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
112 | LV_261-57_0_5_line_112 |  | 102 | 128 | 0.0058659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_261-57_0_5_line_113 |  | 103 | 125 | 0.0081179 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_261-57_0_5_line_114 |  | 105 | 143 | 0.0060485 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_261-57_0_5_line_115 |  | 106 | 107 | 1.5774e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_261-57_0_5_line_116 |  | 107 | 108 | 0.0058151 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_261-57_0_5_line_117 |  | 108 | 109 | 7.9149e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_261-57_0_5_line_118 |  | 109 | 121 | 0.0057374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_261-57_0_5_line_119 |  | 110 | 128 | 0.0058659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_261-57_0_5_line_120 |  | 111 | 112 | 0.01356 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_261-57_0_5_line_121 |  | 112 | 113 | 0.024872 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_261-57_0_5_line_122 |  | 113 | 114 | 0.020981 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_261-57_0_5_line_123 |  | 117 | 118 | 0.0056813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
124 | LV_261-57_0_5_line_124 |  | 118 | 119 | 0.00018931 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
125 | LV_261-57_0_5_line_125 |  | 119 | 120 | 0.0056867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
126 | LV_261-57_0_5_line_126 |  | 120 | 138 | 0.00018293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
127 | LV_261-57_0_5_line_127 |  | 121 | 131 | 0.00015283 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_261-57_0_5_line_128 |  | 122 | 123 | 0.0058735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
129 | LV_261-57_0_5_line_129 |  | 124 | 133 | 0.0055244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_261-57_0_5_line_130 |  | 127 | 129 | 0.0057064 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
131 | LV_261-57_0_5_line_131 |  | 129 | 130 | 0.00016785 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
132 | LV_261-57_0_5_line_132 |  | 130 | 132 | 0.0057021 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
133 | LV_261-57_0_5_line_133 |  | 131 | 135 | 0.0056641 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_261-57_0_5_line_134 |  | 132 | 137 | 0.00017412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
135 | LV_261-57_0_5_line_135 |  | 133 | 134 | 0.00029118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_261-57_0_5_line_136 |  | 134 | 136 | 0.0055955 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_261-57_0_5_line_137 |  | 135 | 136 | 0.00022348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_261-57_0_5_line_138 |  | 137 | 138 | 0.0056951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
139 | LV_261-57_0_5_line_139 |  | 139 | 140 | 0.027339 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_261-57_0_5_line_140 |  | 139 | 141 | 0.0056055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_261-57_0_5_line_141 |  | 140 | 142 | 0.0062805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_261-57_0_5_line_142 |  | 141 | 143 | 0.0056032 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_261-57_0_5_line_143 |  | 142 | 144 | 0.0066013 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-57_0_5_trafo_74 | 0.63 MVA 20/0.4 kV | 145 | 116 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13
0 | 2683460.1414 | 1249589.1656 | 2683458.6742 | 1249605.9234
1 | 2683460.1414 | 1249589.1656 | 2683460.7173 | 1249582.5869
2 | 2683458.0744 | 1249612.7753 | 2683458.6742 | 1249605.9234
3 | 2683460.7173 | 1249582.5869 | 2683461.2933 | 1249576.0082
4 | 2683457.4924 | 1249619.4228 | 2683458.0744 | 1249612.7753
5 | 2683461.2933 | 1249576.0082 | 2683461.8693 | 1249569.4295
6 | 2683457.4924 | 1249619.4228 | 2683456.8922 | 1249626.2786
7 | 2683456.2102 | 1249634.0679 | 2683456.8922 | 1249626.2786
8 | 2683456.2102 | 1249634.0679 | 2683470.3573 | 1249635.2354
9 | 2683456.2102 | 1249634.0679 | 2683455.2685 | 1249639.8145 | 2683453.3643 | 1249644.2021 | 2683448.7532 | 1249649.3855
10 | 2683448.7532 | 1249649.3855 | 2683423.5736 | 1249664.2421
11 | 2683423.5736 | 1249664.2421 | 2683431.7006 | 1249677.5987
12 | 2683423.5736 | 1249664.2421 | 2683416.2382 | 1249651.9832
13 | 2683415.9366 | 1249668.7602 | 2683418.3351 | 1249667.3374 | 2683423.5736 | 1249664.2421
14 | 2683387.6322 | 1249812.8135 | 2683393.2581 | 1249812.2256 | 2683399.4815 | 1249811.5682
15 | 2683399.4815 | 1249811.5682 | 2683395.8364 | 1249805.5346 | 2683386.9052 | 1249789.3636
16 | 2683399.4815 | 1249811.5682 | 2683404.5587 | 1249811.3394 | 2683420.3834 | 1249811.7392
17 | 2683387.6322 | 1249812.8135 | 2683393.2581 | 1249812.2256 | 2683397.7517 | 1249826.0991 | 2683418.8828 | 1249825.2291 | 2683419.1502 | 1249830.37 | 2683419.376 | 1249834.7097
18 | 2683386.9052 | 1249789.3636 | 2683370.5596 | 1249759.7562 | 2683367.4624 | 1249754.5172
19 | 2683386.9052 | 1249789.3636 | 2683400.5048 | 1249781.9341
20 | 2683452.3672 | 1249808.2433 | 2683433.3991 | 1249812.068 | 2683420.3834 | 1249811.7392
21 | 2683507.093 | 1249741.3419 | 2683508.8536 | 1249746.604 | 2683503.8129 | 1249752.2705 | 2683496.8683 | 1249751.0607 | 2683492.388 | 1249752.3319 | 2683480.6464 | 1249759.3162
22 | 2683482.6514 | 1249773.4994 | 2683478.8297 | 1249767.1408 | 2683475.8257 | 1249762.2393 | 2683480.6464 | 1249759.3162
23 | 2683480.6464 | 1249759.3162 | 2683478.205 | 1249755.2121 | 2683477.3567 | 1249753.2542 | 2683472.8457 | 1249745.746
24 | 2683507.093 | 1249741.3419 | 2683502.5056 | 1249706.8183 | 2683498.7597 | 1249681.6913 | 2683495.6388 | 1249666.3358
25 | 2683482.6514 | 1249773.4994 | 2683467.0507 | 1249786.4338 | 2683462.1493 | 1249784.9081
26 | 2683482.6514 | 1249773.4994 | 2683485.7954 | 1249779.1812 | 2683488.0679 | 1249784.0168 | 2683494.926 | 1249802.0824 | 2683496.8089 | 1249805.6338 | 2683498.2351 | 1249808.367 | 2683502.1432 | 1249817.1619 | 2683505.682 | 1249822.1488 | 2683502.8215 | 1249824.21 | 2683504.9867 | 1249827.0204 | 2683508.3441 | 1249832.027 | 2683509.7755 | 1249834.9271 | 2683510.9153 | 1249839.2352 | 2683511.5798 | 1249842.9807
27 | 2683463.76 | 1249730.6793 | 2683467.183 | 1249736.3206 | 2683472.8457 | 1249745.746
28 | 2683270.889 | 1249801.8199 | 2683266.6196 | 1249803.1276 | 2683253.9272 | 1249806.3406
29 | 2683270.889 | 1249801.8199 | 2683268.045 | 1249789.8155 | 2683267.9334 | 1249789.1018
30 | 2683253.9272 | 1249806.3406 | 2683256.8343 | 1249816.5446 | 2683256.8343 | 1249816.5446
31 | 2683267.9334 | 1249789.1018 | 2683265.2101 | 1249771.6832
32 | 2683452.3672 | 1249808.2433 | 2683451.6133 | 1249803.8739
33 | 2683261.449 | 1249720.8272 | 2683266.689 | 1249720.8341 | 2683266.6913 | 1249717.9876 | 2683271.644 | 1249718.0239 | 2683271.6883 | 1249720.2483 | 2683272.6269 | 1249722.2297 | 2683273.1014 | 1249733.0555 | 2683274.1244 | 1249747.3027 | 2683274.4567 | 1249752.6669 | 2683273.8477 | 1249754.0927 | 2683274.0618 | 1249756.5865
34 | 2683274.0618 | 1249756.5865 | 2683295.3151 | 1249754.0276 | 2683297.4245 | 1249766.3186
35 | 2683261.449 | 1249720.8272 | 2683261.4381 | 1249707.4948
36 | 2683261.449 | 1249720.8272 | 2683241.1354 | 1249720.7867
37 | 2683261.449 | 1249720.8272 | 2683261.7784 | 1249737.1439 | 2683262.4522 | 1249749.9073 | 2683263.0487 | 1249754.7539
38 | 2683261.449 | 1249720.8272 | 2683266.689 | 1249720.8341 | 2683266.6913 | 1249717.9876 | 2683271.644 | 1249718.0239 | 2683294.1205 | 1249718.1619
39 | 2683300.5014 | 1249784.2464 | 2683297.4245 | 1249766.3186
40 | 2683294.1205 | 1249718.1619 | 2683304.3249 | 1249721.6746 | 2683306.9621 | 1249728.5485
41 | 2683293.909 | 1249705.8165 | 2683294.1205 | 1249718.1619
42 | 2683294.1205 | 1249718.1619 | 2683294.9375 | 1249733.4273
43 | 2683295.0569 | 1249735.6576 | 2683294.9375 | 1249733.4273
44 | 2683256.8343 | 1249816.5446 | 2683244.5836 | 1249830.7256
45 | 2683456.601 | 1249718.8809 | 2683455.6183 | 1249717.3548
46 | 2683447.5886 | 1249722.4122 | 2683450.6664 | 1249720.4763 | 2683455.6183 | 1249717.3548
47 | 2683455.6183 | 1249717.3548 | 2683448.9342 | 1249706.2158
48 | 2683456.601 | 1249718.8809 | 2683463.76 | 1249730.6793
49 | 2683456.601 | 1249718.8809 | 2683479.2165 | 1249705.4004
50 | 2683447.5886 | 1249722.4122 | 2683446.6148 | 1249720.7862
51 | 2683447.5886 | 1249722.4122 | 2683449.1968 | 1249725.1035 | 2683454.1398 | 1249733.3065
52 | 2683440.0748 | 1249691.4514 | 2683448.9342 | 1249706.2158
53 | 2683419.376 | 1249834.7097 | 2683420.1559 | 1249858.1492 | 2683429.4124 | 1249859.247 | 2683428.122 | 1249856.5157
54 | 2683428.122 | 1249856.5157 | 2683451.8205 | 1249855.3516
55 | 2683419.376 | 1249834.7097 | 2683395.2468 | 1249835.9204
56 | 2683264.3665 | 1249680.327 | 2683252.1543 | 1249677.8102
57 | 2683264.3665 | 1249680.327 | 2683269.7345 | 1249681.4365 | 2683271.9144 | 1249670.8593 | 2683275.0171 | 1249659.083 | 2683275.445 | 1249657.6546 | 2683282.0242 | 1249660.16 | 2683283.8613 | 1249659.4631
58 | 2683264.3665 | 1249680.327 | 2683262.5246 | 1249692.1099 | 2683261.4369 | 1249706.105 | 2683261.4381 | 1249707.4948
59 | 2683283.8613 | 1249659.4631 | 2683286.3241 | 1249652.3924 | 2683289.0154 | 1249645.7142
60 | 2683283.8613 | 1249659.4631 | 2683285.9352 | 1249660.1817 | 2683287.4458 | 1249661.7596 | 2683309.484 | 1249690.6409
61 | 2683511.5798 | 1249842.9807 | 2683506.7029 | 1249844.0017 | 2683507.0978 | 1249850.8012 | 2683506.4794 | 1249852.3603
62 | 2683446.6148 | 1249720.7862 | 2683434.3275 | 1249728.0418
63 | 2683461.9758 | 1249746.3103 | 2683454.1398 | 1249733.3065
64 | 2683263.0487 | 1249754.7539 | 2683264.8444 | 1249769.3442 | 2683265.2101 | 1249771.6832
65 | 2683289.0154 | 1249645.7142 | 2683296.6686 | 1249656.3394
66 | 2683344.9993 | 1249737.7974 | 2683340.9382 | 1249731.8634 | 2683327.0963 | 1249713.722 | 2683309.484 | 1249690.6409
67 | 2683461.9758 | 1249746.3103 | 2683449.3914 | 1249753.8809
68 | 2683445.5428 | 1249756.1962 | 2683449.3914 | 1249753.8809
69 | 2683310.2786 | 1249675.2349 | 2683303.6072 | 1249665.9726
70 | 2683310.2786 | 1249675.2349 | 2683317.7793 | 1249669.4524
71 | 2683310.2786 | 1249675.2349 | 2683317.9672 | 1249685.2096
72 | 2683300.1946 | 1249661.2349 | 2683303.6072 | 1249665.9726
73 | 2683317.7793 | 1249669.4524 | 2683327.744 | 1249661.7703 | 2683336.3207 | 1249655.958
74 | 2683317.9672 | 1249685.2096 | 2683321.5535 | 1249689.8622
75 | 2683388.3562 | 1249622.4489 | 2683382.212 | 1249612.7221
76 | 2683388.3562 | 1249622.4489 | 2683394.5801 | 1249633.0316
77 | 2683388.3562 | 1249622.4489 | 2683380.325 | 1249627.2176
78 | 2683378.9823 | 1249607.6091 | 2683382.212 | 1249612.7221
79 | 2683394.5801 | 1249633.0316 | 2683397.5528 | 1249638.086
80 | 2683342.7096 | 1249718.1226 | 2683349.7837 | 1249727.725
81 | 2683342.7096 | 1249718.1226 | 2683350.363 | 1249712.4391
82 | 2683342.7096 | 1249718.1226 | 2683335.5829 | 1249708.4473
83 | 2683349.7837 | 1249727.725 | 2683353.3459 | 1249732.5604
84 | 2683366.5835 | 1249700.9672 | 2683356.5817 | 1249707.8211 | 2683350.363 | 1249712.4391
85 | 2683332.1005 | 1249703.7198 | 2683335.5829 | 1249708.4473
86 | 2683296.6686 | 1249656.3394 | 2683300.1946 | 1249661.2349
87 | 2683415.9366 | 1249668.7602 | 2683407.98 | 1249673.5008
88 | 2683415.9366 | 1249668.7602 | 2683409.4223 | 1249658.1345
89 | 2683415.9366 | 1249668.7602 | 2683419.2094 | 1249674.9553 | 2683421.6197 | 1249678.9861
90 | 2683407.98 | 1249673.5008 | 2683397.9052 | 1249679.5034 | 2683390.9517 | 1249684.2684
91 | 2683409.4223 | 1249658.1345 | 2683407.4924 | 1249654.9867 | 2683406.4738 | 1249653.2547
92 | 2683421.6197 | 1249678.9861 | 2683424.614 | 1249683.9936
93 | 2683431.7006 | 1249677.5987 | 2683436.1711 | 1249684.9459 | 2683440.0748 | 1249691.4514
94 | 2683407.9366 | 1249637.9288 | 2683415.9309 | 1249651.4695 | 2683416.2382 | 1249651.9832
95 | 2683479.2165 | 1249705.4004 | 2683477.6078 | 1249702.7536 | 2683476.7181 | 1249695.6913 | 2683468.7194 | 1249682.4466
96 | 2683367.4624 | 1249754.5172 | 2683359.0987 | 1249740.3695 | 2683356.908 | 1249737.3958
97 | 2683404.2604 | 1249779.8824 | 2683400.5048 | 1249781.9341
98 | 2683495.6388 | 1249666.3358 | 2683494.5097 | 1249660.7807
99 | 2683375.7537 | 1249602.4979 | 2683378.9823 | 1249607.6091
100 | 2683300.5014 | 1249784.2464 | 2683301.3448 | 1249789.1606 | 2683302.7525 | 1249790.0744
101 | 2683358.2936 | 1249759.0411 | 2683351.9029 | 1249747.885 | 2683344.9993 | 1249737.7974
102 | 2683399.8311 | 1249623.6891 | 2683399.8311 | 1249623.6891 | 2683396.4379 | 1249620.1387 | 2683390.8482 | 1249610.6308 | 2683382.0638 | 1249595.617
103 | 2683399.8311 | 1249623.6891 | 2683403.1944 | 1249629.8965 | 2683407.9366 | 1249637.9288
104 | 2683413.9508 | 1249740.0742 | 2683434.3275 | 1249728.0418
105 | 2683336.3207 | 1249655.958 | 2683336.6213 | 1249655.7543
106 | 2683321.5535 | 1249689.8622 | 2683325.139 | 1249694.5138
107 | 2683397.5528 | 1249638.086 | 2683400.5264 | 1249643.1423
108 | 2683356.908 | 1249737.3958 | 2683353.3459 | 1249732.5604
109 | 2683366.5835 | 1249700.9672 | 2683366.7434 | 1249700.8576
110 | 2683328.7248 | 1249699.1657 | 2683329.2027 | 1249699.7857 | 2683332.1005 | 1249703.7198
111 | 2683390.8186 | 1249684.3596 | 2683390.9517 | 1249684.2684
112 | 2683403.5001 | 1249648.1985 | 2683406.4738 | 1249653.2547
113 | 2683428.7802 | 1249690.9608 | 2683424.614 | 1249683.9936
114 | 2683494.5097 | 1249660.7807 | 2683493.7463 | 1249657.0246 | 2683493.2315 | 1249654.8697
115 | 2683360.6969 | 1249639.4385 | 2683360.71 | 1249639.4297
116 | 2683360.6969 | 1249639.4385 | 2683355.8831 | 1249642.7008
117 | 2683355.8175 | 1249642.7452 | 2683355.8831 | 1249642.7008
118 | 2683355.8175 | 1249642.7452 | 2683351.068 | 1249645.9639
119 | 2683400.5264 | 1249643.1423 | 2683403.5001 | 1249648.1985
120 | 2683315.61 | 1249792.9845 | 2683310.2516 | 1249793.1221 | 2683305.6172 | 1249791.9338 | 2683302.7525 | 1249790.0744
121 | 2683315.61 | 1249792.9845 | 2683340.4742 | 1249792.346
122 | 2683361.448 | 1249791.8074 | 2683340.4742 | 1249792.346
123 | 2683371.4298 | 1249697.6461 | 2683366.7434 | 1249700.8576
124 | 2683371.4298 | 1249697.6461 | 2683371.586 | 1249697.5391
125 | 2683376.2769 | 1249694.3246 | 2683371.586 | 1249697.5391
126 | 2683376.2769 | 1249694.3246 | 2683376.4278 | 1249694.2212
127 | 2683350.9415 | 1249646.0497 | 2683351.068 | 1249645.9639
128 | 2683325.139 | 1249694.5138 | 2683328.7248 | 1249699.1657
129 | 2683341.1945 | 1249652.6551 | 2683336.6213 | 1249655.7543
130 | 2683390.8186 | 1249684.3596 | 2683386.1115 | 1249687.5853
131 | 2683385.973 | 1249687.6802 | 2683386.1115 | 1249687.5853
132 | 2683385.973 | 1249687.6802 | 2683381.2693 | 1249690.9034
133 | 2683350.9415 | 1249646.0497 | 2683346.2527 | 1249649.2273
134 | 2683381.1257 | 1249691.0018 | 2683381.2693 | 1249690.9034
135 | 2683341.1945 | 1249652.6551 | 2683341.4356 | 1249652.4917
136 | 2683346.0677 | 1249649.3526 | 2683341.4356 | 1249652.4917
137 | 2683346.0677 | 1249649.3526 | 2683346.2527 | 1249649.2273
138 | 2683381.1257 | 1249691.0018 | 2683376.4278 | 1249694.2212
139 | 2683490.6269 | 1249643.9678 | 2683487.4718 | 1249630.7612 | 2683484.0946 | 1249617.4214
140 | 2683491.9295 | 1249649.4199 | 2683490.6269 | 1249643.9678
141 | 2683484.0946 | 1249617.4214 | 2683482.5533 | 1249611.333
142 | 2683493.2315 | 1249654.8697 | 2683491.9295 | 1249649.4199
143 | 2683482.5533 | 1249611.333 | 2683480.9332 | 1249604.9336

## bus_geodata
| x | y | coords
0 | 2683460.1414 | 1249589.1656
1 | 2683458.6742 | 1249605.9234
2 | 2683460.7173 | 1249582.5869
3 | 2683458.0744 | 1249612.7753
4 | 2683461.2933 | 1249576.0082
5 | 2683457.4924 | 1249619.4228
6 | 2683461.8693 | 1249569.4295
7 | 2683456.8922 | 1249626.2786
8 | 2683470.3573 | 1249635.2354
9 | 2683456.2102 | 1249634.0679
10 | 2683448.7532 | 1249649.3855
11 | 2683423.5736 | 1249664.2421
12 | 2683399.4815 | 1249811.5682
13 | 2683387.6322 | 1249812.8135
14 | 2683386.9052 | 1249789.3636
15 | 2683420.3834 | 1249811.7392
16 | 2683480.6464 | 1249759.3162
17 | 2683507.093 | 1249741.3419
18 | 2683482.6514 | 1249773.4994
19 | 2683472.8458 | 1249745.746
20 | 2683270.889 | 1249801.8199
21 | 2683253.9272 | 1249806.3406
22 | 2683267.9334 | 1249789.1018
23 | 2683452.3672 | 1249808.2433
24 | 2683451.6133 | 1249803.8739
25 | 2683274.0618 | 1249756.5865
26 | 2683261.449 | 1249720.8272
27 | 2683297.4245 | 1249766.3186
28 | 2683294.1205 | 1249718.1619
29 | 2683306.9621 | 1249728.5485
30 | 2683293.909 | 1249705.8165
31 | 2683294.9375 | 1249733.4273
32 | 2683256.8343 | 1249816.5446
33 | 2683455.6183 | 1249717.3548
34 | 2683456.601 | 1249718.8809
35 | 2683447.5886 | 1249722.4122
36 | 2683448.9342 | 1249706.2158
37 | 2683428.122 | 1249856.5157
38 | 2683419.376 | 1249834.7097
39 | 2683451.8205 | 1249855.3516
40 | 2683264.3665 | 1249680.327
41 | 2683252.1543 | 1249677.8102
42 | 2683283.8613 | 1249659.4631
43 | 2683261.4381 | 1249707.4948
44 | 2683462.1493 | 1249784.9081
45 | 2683511.5798 | 1249842.9807
46 | 2683446.6148 | 1249720.7862
47 | 2683454.1398 | 1249733.3065
48 | 2683241.1354 | 1249720.7867
49 | 2683263.0487 | 1249754.7539
50 | 2683289.0154 | 1249645.7142
51 | 2683309.484 | 1249690.6409
52 | 2683461.9758 | 1249746.3103
53 | 2683449.3914 | 1249753.8809
54 | 2683310.2786 | 1249675.2349
55 | 2683303.6072 | 1249665.9726
56 | 2683317.7793 | 1249669.4524
57 | 2683317.9672 | 1249685.2096
58 | 2683388.3562 | 1249622.4489
59 | 2683382.212 | 1249612.7221
60 | 2683394.5801 | 1249633.0316
61 | 2683380.325 | 1249627.2176
62 | 2683342.7096 | 1249718.1226
63 | 2683349.7837 | 1249727.725
64 | 2683350.363 | 1249712.4391
65 | 2683335.5829 | 1249708.4473
66 | 2683296.6686 | 1249656.3394
67 | 2683395.2468 | 1249835.9204
68 | 2683415.9366 | 1249668.7602
69 | 2683407.98 | 1249673.5008
70 | 2683409.4223 | 1249658.1345
71 | 2683421.6197 | 1249678.9861
72 | 2683506.4794 | 1249852.3603
73 | 2683431.7006 | 1249677.5987
74 | 2683416.2382 | 1249651.9832
75 | 2683468.7194 | 1249682.4466
76 | 2683479.2165 | 1249705.4004
77 | 2683367.4624 | 1249754.5172
78 | 2683400.5048 | 1249781.9341
79 | 2683495.6388 | 1249666.3358
80 | 2683463.76 | 1249730.6793
81 | 2683265.2101 | 1249771.6832
82 | 2683375.7537 | 1249602.4979
83 | 2683378.9823 | 1249607.6091
84 | 2683300.5014 | 1249784.2464
85 | 2683295.0569 | 1249735.6576
86 | 2683244.5836 | 1249830.7256
87 | 2683440.0748 | 1249691.4514
88 | 2683358.2936 | 1249759.0411
89 | 2683344.9993 | 1249737.7974
90 | 2683382.0638 | 1249595.617
91 | 2683399.8311 | 1249623.6891
92 | 2683434.3275 | 1249728.0418
93 | 2683445.5428 | 1249756.1962
94 | 2683300.1946 | 1249661.2349
95 | 2683336.3207 | 1249655.958
96 | 2683321.5535 | 1249689.8622
97 | 2683397.5528 | 1249638.086
98 | 2683353.3459 | 1249732.5604
99 | 2683366.5835 | 1249700.9672
100 | 2683332.1005 | 1249703.7198
101 | 2683390.9517 | 1249684.2684
102 | 2683406.4738 | 1249653.2547
103 | 2683424.614 | 1249683.9936
104 | 2683407.9366 | 1249637.9288
105 | 2683494.5097 | 1249660.7807
106 | 2683360.71 | 1249639.4297
107 | 2683360.6969 | 1249639.4385
108 | 2683355.8831 | 1249642.7008
109 | 2683355.8175 | 1249642.7452
110 | 2683400.5264 | 1249643.1423
111 | 2683302.7525 | 1249790.0744
112 | 2683315.61 | 1249792.9845
113 | 2683340.4742 | 1249792.346
114 | 2683361.448 | 1249791.8074
115 | 2683404.2604 | 1249779.8824
116 | 2683356.908 | 1249737.3958
117 | 2683366.7434 | 1249700.8576
118 | 2683371.4298 | 1249697.6461
119 | 2683371.586 | 1249697.5391
120 | 2683376.2769 | 1249694.3246
121 | 2683351.068 | 1249645.9639
122 | 2683325.139 | 1249694.5138
123 | 2683328.7248 | 1249699.1657
124 | 2683336.6213 | 1249655.7543
125 | 2683428.7802 | 1249690.9608
126 | 2683413.9508 | 1249740.0742
127 | 2683390.8186 | 1249684.3596
128 | 2683403.5001 | 1249648.1985
129 | 2683386.1115 | 1249687.5853
130 | 2683385.973 | 1249687.6802
131 | 2683350.9415 | 1249646.0497
132 | 2683381.2693 | 1249690.9034
133 | 2683341.1945 | 1249652.6551
134 | 2683341.4356 | 1249652.4917
135 | 2683346.2527 | 1249649.2273
136 | 2683346.0677 | 1249649.3526
137 | 2683381.1257 | 1249691.0018
138 | 2683376.4278 | 1249694.2212
139 | 2683490.6269 | 1249643.9678
140 | 2683484.0946 | 1249617.4214
141 | 2683491.9295 | 1249649.4199
142 | 2683482.5533 | 1249611.333
143 | 2683493.2315 | 1249654.8697
144 | 2683480.9332 | 1249604.9336
145 | 2683342.7096 | 1249718.1226

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99157 | -0.16153 | 0.0019607 | 0.0004914
1 | 0.99169 | -0.1592 | 0.0020447 | 0.00051245
2 | 0.99153 | -0.16222 | 0.001959 | 0.00049097
3 | 0.99175 | -0.15799 | 0.0019354 | 0.00048507
4 | 0.99151 | -0.16268 | 0.0019609 | 0.00049144
5 | 0.99182 | -0.15659 | 0.001938 | 0.0004857
6 | 0.9915 | -0.16291 | 0.001959 | 0.00049098
7 | 0.99191 | -0.15492 | 0.0020456 | 0.00051268
8 | 0.992 | -0.15321 | 0.0019393 | 0.00048605
9 | 0.99202 | -0.15273 | 0 | 0
10 | 0.99231 | -0.14722 | 0 | 0
11 | 0.99278 | -0.13806 | 0 | 0
12 | 0.99405 | -0.11417 | 0 | 0
13 | 0.99366 | -0.12176 | 0 | 0
14 | 0.99531 | -0.090026 | 0 | 0
15 | 0.99372 | -0.12068 | 0.0079548 | 0.0019937
16 | 0.98473 | -0.29392 | 0 | 0
17 | 0.98421 | -0.30406 | 0 | 0
18 | 0.98437 | -0.30089 | 0 | 0
19 | 0.98524 | -0.28399 | 0.0083326 | 0.0020883
20 | 0.98323 | -0.32218 | 0 | 0
21 | 0.98302 | -0.32623 | 0 | 0
22 | 0.98339 | -0.31917 | 0.004435 | 0.0011115
23 | 0.99343 | -0.12622 | 0 | 0
24 | 0.99339 | -0.12698 | 0.0096867 | 0.0024277
25 | 0.98203 | -0.3454 | 0 | 0
26 | 0.98478 | -0.29204 | 0 | 0
27 | 0.98024 | -0.38032 | 0.0046802 | 0.001173
28 | 0.98332 | -0.32035 | 0 | 0
29 | 0.98293 | -0.32813 | 0.023762 | 0.0059554
30 | 0.98327 | -0.32135 | 0.0044853 | 0.0011241
31 | 0.9831 | -0.32477 | 0.005348 | 0.0013403
32 | 0.9829 | -0.32868 | 0.0069498 | 0.0017418
33 | 0.9867 | -0.25564 | 0 | 0
34 | 0.98661 | -0.25739 | 0 | 0
35 | 0.98633 | -0.26279 | 0 | 0
36 | 0.98784 | -0.2334 | 0.0079525 | 0.0019931
37 | 0.9916 | -0.16159 | 0 | 0
38 | 0.99198 | -0.15424 | 0 | 0
39 | 0.99135 | -0.16646 | 0.011581 | 0.0029025
40 | 0.98982 | -0.19457 | 0 | 0
41 | 0.98968 | -0.19722 | 0.011937 | 0.0029918
42 | 0.99246 | -0.1437 | 0 | 0
43 | 0.98639 | -0.26062 | 0.0038999 | 0.00097741
44 | 0.98419 | -0.30445 | 0.0078186 | 0.0019595
45 | 0.98345 | -0.31897 | 0 | 0
46 | 0.9863 | -0.26347 | 0 | 0
47 | 0.98607 | -0.26786 | 0.0029536 | 0.00074023
48 | 0.98468 | -0.29391 | 0.0050992 | 0.001278
49 | 0.98399 | -0.30736 | 0.0044297 | 0.0011102
50 | 0.9931 | -0.13149 | 0 | 0
51 | 0.99094 | -0.1732 | 0.0068518 | 0.0017172
52 | 0.9858 | -0.2731 | 0 | 0
53 | 0.98554 | -0.27817 | 0.0094753 | 0.0023747
54 | 0.9947 | -0.10087 | 0 | 0
55 | 0.99419 | -0.11062 | 0.001842 | 0.00046164
56 | 0.99449 | -0.10491 | 0.0019619 | 0.00049169
57 | 0.99534 | -0.088794 | 0.0018947 | 0.00047487
58 | 0.99279 | -0.13805 | 0 | 0
59 | 0.99273 | -0.1392 | 0.0018923 | 0.00047425
60 | 0.99287 | -0.1364 | 0.0017696 | 0.00044351
61 | 0.99277 | -0.13836 | 0.0018902 | 0.00047372
62 | 0.99748 | -0.047954 | 0 | 0
63 | 0.99872 | -0.024216 | 0.0047064 | 0.0011795
64 | 0.99699 | -0.057274 | 0.0047028 | 0.0011786
65 | 0.99684 | -0.060165 | 0.0045729 | 0.0011461
66 | 0.99367 | -0.12061 | 0.0019635 | 0.00049211
67 | 0.99144 | -0.16474 | 0.024513 | 0.0061435
68 | 0.99342 | -0.1258 | 0 | 0
69 | 0.9938 | -0.11842 | 0.0017319 | 0.00043405
70 | 0.99321 | -0.12978 | 0.0016602 | 0.00041608
71 | 0.99335 | -0.12705 | 0.0016477 | 0.00041295
72 | 0.98329 | -0.32207 | 0.012776 | 0.003202
73 | 0.99111 | -0.1702 | 0.0070683 | 0.0017715
74 | 0.99249 | -0.14376 | 0.0069717 | 0.0017473
75 | 0.98653 | -0.259 | 0.0017363 | 0.00043515
76 | 0.98657 | -0.2582 | 0 | 0
77 | 0.99822 | -0.034041 | 0.016887 | 0.0042322
78 | 0.99494 | -0.097179 | 0.009356 | 0.0023448
79 | 0.98319 | -0.32411 | 0.0017378 | 0.00043554
80 | 0.98595 | -0.27023 | 0.0083308 | 0.0020879
81 | 0.98367 | -0.31369 | 0.0033777 | 0.00084652
82 | 0.99269 | -0.13981 | 0.001891 | 0.00047394
83 | 0.9927 | -0.1396 | 0.0018881 | 0.0004732
84 | 0.97936 | -0.39758 | 0.0032874 | 0.0008239
85 | 0.98308 | -0.3252 | 0.010681 | 0.002677
86 | 0.9828 | -0.33066 | 0.0058531 | 0.0014669
87 | 0.98949 | -0.20156 | 0.0052877 | 0.0013252
88 | 0.98869 | -0.21678 | 0.017581 | 0.0044062
89 | 0.9891 | -0.20892 | 0.016444 | 0.0041214
90 | 0.99195 | -0.15409 | 0.0048302 | 0.0012106
91 | 0.9921 | -0.15123 | 0.0054189 | 0.0013581
92 | 0.98604 | -0.26855 | 0.009844 | 0.0024671
93 | 0.9855 | -0.27896 | 0.0097871 | 0.0024529
94 | 0.99393 | -0.11556 | 0.001829 | 0.0004584
95 | 0.99403 | -0.11389 | 0.0018247 | 0.00045731
96 | 0.99563 | -0.083117 | 0.0018876 | 0.00047307
97 | 0.99292 | -0.13544 | 0.0017705 | 0.00044372
98 | 0.99936 | -0.012162 | 0.0047064 | 0.0011795
99 | 0.996 | -0.07632 | 0.004509 | 0.0011301
100 | 0.99653 | -0.066019 | 0.0018656 | 0.00046757
101 | 0.99464 | -0.10223 | 0.0018703 | 0.00046875
102 | 0.99313 | -0.13143 | 0.0017705 | 0.00044372
103 | 0.99333 | -0.1275 | 0.0016989 | 0.00042578
104 | 0.99225 | -0.14826 | 0.0053302 | 0.0013359
105 | 0.98312 | -0.32544 | 0.0017384 | 0.00043569
106 | 0.99373 | -0.11973 | 0.0019204 | 0.0004813
107 | 0.99373 | -0.11973 | 0.0018584 | 0.00046577
108 | 0.99375 | -0.11934 | 0.0018628 | 0.00046687
109 | 0.99375 | -0.11933 | 0.0018311 | 0.00045891
110 | 0.99298 | -0.13429 | 0.0017705 | 0.00044372
111 | 0.97906 | -0.40351 | 0.0053023 | 0.0013289
112 | 0.97851 | -0.41428 | 0.0063989 | 0.0016037
113 | 0.97765 | -0.43116 | 0.021734 | 0.005447
114 | 0.97735 | -0.4371 | 0.015523 | 0.0038906
115 | 0.99487 | -0.09845 | 0.016871 | 0.0042282
116 | 1 | 0 | -0.5687 | -0.14436
117 | 0.99599 | -0.076502 | 0.0018099 | 0.00045359
118 | 0.99571 | -0.081797 | 0.004509 | 0.0011301
119 | 0.9957 | -0.08197 | 0.0018213 | 0.00045646
120 | 0.99543 | -0.087114 | 0.0045124 | 0.0011309
121 | 0.99379 | -0.11857 | 0.0018594 | 0.00046601
122 | 0.99593 | -0.077395 | 0.0018791 | 0.00047095
123 | 0.99623 | -0.071628 | 0.0018714 | 0.00046902
124 | 0.99402 | -0.11403 | 0.0018627 | 0.00046684
125 | 0.99331 | -0.12789 | 0.0027078 | 0.00067863
126 | 0.98582 | -0.2728 | 0.010016 | 0.0025103
127 | 0.99465 | -0.1021 | 0.0025994 | 0.00065146
128 | 0.99305 | -0.13295 | 0.0017705 | 0.00044372
129 | 0.9949 | -0.097406 | 0.0018601 | 0.00046617
130 | 0.9949 | -0.097267 | 0.0045134 | 0.0011312
131 | 0.99379 | -0.11855 | 0.0018247 | 0.00045731
132 | 0.99516 | -0.092422 | 0.0018473 | 0.00046298
133 | 0.99393 | -0.11583 | 0.0018247 | 0.00045731
134 | 0.99392 | -0.11592 | 0.0018613 | 0.00046649
135 | 0.99385 | -0.11743 | 0.001862 | 0.00046667
136 | 0.99385 | -0.11738 | 0.0018247 | 0.00045731
137 | 0.99516 | -0.092272 | 0.0045136 | 0.0011312
138 | 0.99542 | -0.087276 | 0.0018327 | 0.00045931
139 | 0.98297 | -0.32839 | 0.0017378 | 0.00043554
140 | 0.98282 | -0.33134 | 0.0019426 | 0.00048686
141 | 0.98301 | -0.32761 | 0.0017369 | 0.0004353
142 | 0.98279 | -0.3318 | 0.0019393 | 0.00048605
143 | 0.98306 | -0.32666 | 0.001737 | 0.00043534
144 | 0.98278 | -0.33205 | 0.0020958 | 0.00052525
145 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0078399 | -0.0019647 | 0.0078408 | 0.0019651 | 8.7316e-07 | 3.4181e-07 | 0.011765 | 0.011765 | 0.011765 | 0.99157 | -0.16153 | 0.99169 | -0.1592 | 3.2322
1 | 0.0058792 | 0.0014733 | -0.005879 | -0.0014733 | 1.9277e-07 | 3.8191e-08 | 0.0088227 | 0.0088227 | 0.0088227 | 0.99157 | -0.16153 | 0.99153 | -0.16222 | 2.4238
2 | -0.0098855 | -0.0024775 | 0.009886 | 0.0024778 | 5.6749e-07 | 2.7445e-07 | 0.014833 | 0.014833 | 0.014833 | 0.99169 | -0.1592 | 0.99175 | -0.15799 | 4.075
3 | 0.00392 | 0.00098232 | -0.0039199 | -0.00098235 | 8.5703e-08 | -3.0325e-08 | 0.0058828 | 0.0058828 | 0.0058828 | 0.99153 | -0.16222 | 0.99151 | -0.16268 | 1.6162
4 | -0.011821 | -0.0029629 | 0.011822 | 0.0029633 | 7.8723e-07 | 4.1772e-07 | 0.017737 | 0.017737 | 0.017737 | 0.99175 | -0.15799 | 0.99182 | -0.15659 | 4.8728
5 | 0.001959 | 0.0004909 | -0.001959 | -0.00049098 | 2.1406e-08 | -7.1472e-08 | 0.00294 | 0.00294 | 0.00294 | 0.99151 | -0.16268 | 0.9915 | -0.16291 | 0.8077
6 | -0.01376 | -0.003449 | 0.013761 | 0.0034496 | 1.0999e-06 | 6.1511e-07 | 0.020644 | 0.020644 | 0.020644 | 0.99182 | -0.15659 | 0.99191 | -0.15492 | 5.6715
7 | -0.015807 | -0.0039623 | 0.015809 | 0.0039632 | 1.6488e-06 | 9.5428e-07 | 0.023713 | 0.023713 | 0.023713 | 0.99191 | -0.15492 | 0.99202 | -0.15273 | 6.5146
8 | -0.0019393 | -0.00048605 | 0.0019394 | 0.00048589 | 4.5047e-08 | -1.5444e-07 | 0.0029091 | 0.002909 | 0.0029091 | 0.992 | -0.15321 | 0.99202 | -0.15273 | 0.79919
9 | -0.017748 | -0.0044491 | 0.017753 | 0.0044519 | 4.6598e-06 | 2.7559e-06 | 0.026622 | 0.026622 | 0.026622 | 0.99202 | -0.15273 | 0.99231 | -0.14722 | 7.3137
10 | -0.017753 | -0.0044519 | 0.01776 | 0.0044565 | 7.7534e-06 | 4.5851e-06 | 0.026622 | 0.026622 | 0.026622 | 0.99231 | -0.14722 | 0.99278 | -0.13806 | 7.3137
11 | 0.11681 | 0.029568 | -0.11663 | -0.029453 | 0.00017994 | 0.00011496 | 0.17519 | 0.17519 | 0.17519 | 0.99278 | -0.13806 | 0.99111 | -0.1702 | 48.1288
12 | 0.022563 | 0.0056582 | -0.022556 | -0.0056545 | 6.1272e-06 | 3.7367e-06 | 0.033819 | 0.033819 | 0.033819 | 0.99278 | -0.13806 | 0.99249 | -0.14376 | 9.2909
13 | -0.15714 | -0.039683 | 0.15723 | 0.039742 | 9.2374e-05 | 5.889e-05 | 0.23563 | 0.23563 | 0.23563 | 0.99278 | -0.13806 | 0.99342 | -0.1258 | 32.3667
14 | 0.036182 | 0.0091005 | -0.036169 | -0.0090923 | 1.3112e-05 | 8.2374e-06 | 0.054173 | 0.054173 | 0.054173 | 0.99405 | -0.11417 | 0.99366 | -0.12176 | 14.8827
15 | -0.053832 | -0.013527 | 0.053894 | 0.013566 | 6.2127e-05 | 3.943e-05 | 0.080594 | 0.080594 | 0.080594 | 0.99405 | -0.11417 | 0.99531 | -0.090026 | 22.1413
16 | 0.01765 | 0.004426 | -0.017644 | -0.0044228 | 5.4744e-06 | 3.2326e-06 | 0.026421 | 0.026421 | 0.026421 | 0.99405 | -0.11417 | 0.99372 | -0.12068 | 7.2586
17 | 0.036169 | 0.0090923 | -0.036113 | -0.0090571 | 5.5997e-05 | 3.518e-05 | 0.054173 | 0.054173 | 0.054173 | 0.99366 | -0.12176 | 0.99198 | -0.15424 | 14.8828
18 | -0.080131 | -0.020145 | 0.080345 | 0.020282 | 0.00021485 | 0.00013698 | 0.11982 | 0.11982 | 0.11982 | 0.99531 | -0.090026 | 0.99822 | -0.034041 | 32.9176
19 | 0.026237 | 0.0065791 | -0.026228 | -0.0065736 | 8.9415e-06 | 5.5212e-06 | 0.039226 | 0.039226 | 0.039226 | 0.99531 | -0.090026 | 0.99494 | -0.097179 | 10.7763
20 | 0.0096896 | 0.0024291 | -0.0096871 | -0.0024279 | 2.5556e-06 | 1.2164e-06 | 0.01451 | 0.01451 | 0.01451 | 0.99372 | -0.12068 | 0.99343 | -0.12622 | 3.9862
21 | 0.01469 | 0.0036889 | -0.014683 | -0.0036848 | 7.1028e-06 | 4.0571e-06 | 0.0222 | 0.022201 | 0.022201 | 0.98473 | -0.29392 | 0.98421 | -0.30406 | 6.0991
22 | 0.020616 | 0.0051733 | -0.020609 | -0.0051692 | 6.8449e-06 | 4.1416e-06 | 0.031155 | 0.031155 | 0.031155 | 0.98473 | -0.29392 | 0.98437 | -0.30089 | 8.5591
23 | -0.035306 | -0.0088622 | 0.035323 | 0.0088727 | 1.6727e-05 | 1.0506e-05 | 0.053355 | 0.053355 | 0.053355 | 0.98473 | -0.29392 | 0.98524 | -0.28399 | 14.6581
24 | 0.014683 | 0.0036848 | -0.014669 | -0.0036768 | 1.4029e-05 | 8.0148e-06 | 0.022201 | 0.022201 | 0.022201 | 0.98421 | -0.30406 | 0.98319 | -0.32411 | 6.0992
25 | 0.00782 | 0.0019601 | -0.0078186 | -0.0019595 | 1.3284e-06 | 5.2796e-07 | 0.011821 | 0.011821 | 0.011821 | 0.98437 | -0.30089 | 0.98419 | -0.30445 | 3.2476
26 | 0.012789 | 0.0032091 | -0.012778 | -0.0032031 | 1.1018e-05 | 6.0532e-06 | 0.019334 | 0.019334 | 0.019334 | 0.98437 | -0.30089 | 0.98345 | -0.31897 | 5.3116
27 | -0.043655 | -0.010961 | 0.043684 | 0.010979 | 2.8688e-05 | 1.8136e-05 | 0.06594 | 0.06594 | 0.06594 | 0.98524 | -0.28399 | 0.98595 | -0.27023 | 18.1154
28 | 0.012807 | 0.003211 | -0.012805 | -0.0032096 | 2.467e-06 | 1.3568e-06 | 0.019383 | 0.019383 | 0.019383 | 0.98323 | -0.32218 | 0.98302 | -0.32623 | 5.325
29 | -0.012807 | -0.003211 | 0.012809 | 0.003212 | 1.8399e-06 | 1.0119e-06 | 0.019383 | 0.019383 | 0.019383 | 0.98323 | -0.32218 | 0.98339 | -0.31917 | 5.325
30 | 0.012805 | 0.0032096 | -0.012803 | -0.0032088 | 1.4948e-06 | 8.222e-07 | 0.019383 | 0.019383 | 0.019383 | 0.98302 | -0.32623 | 0.9829 | -0.32868 | 5.325
31 | -0.017244 | -0.0043235 | 0.017249 | 0.0043262 | 4.5015e-06 | 2.6572e-06 | 0.026094 | 0.026094 | 0.026094 | 0.98339 | -0.31917 | 0.98367 | -0.31369 | 7.1686
32 | 0.0096871 | 0.0024279 | -0.0096867 | -0.0024277 | 3.5007e-07 | 1.6664e-07 | 0.01451 | 0.01451 | 0.01451 | 0.99343 | -0.12622 | 0.99339 | -0.12698 | 3.9862
33 | -0.057135 | -0.014399 | 0.057281 | 0.014492 | 0.00014626 | 9.2948e-05 | 0.086602 | 0.086602 | 0.086602 | 0.98203 | -0.3454 | 0.98478 | -0.29204 | 23.7919
34 | 0.057135 | 0.014399 | -0.05704 | -0.014339 | 9.528e-05 | 6.0552e-05 | 0.086602 | 0.086603 | 0.086603 | 0.98203 | -0.3454 | 0.98024 | -0.38032 | 23.7919
35 | -0.13181 | -0.03321 | 0.13201 | 0.033337 | 0.00019845 | 0.00012684 | 0.19923 | 0.19923 | 0.19923 | 0.98478 | -0.29204 | 0.98639 | -0.26062 | 54.734
36 | 0.0050997 | 0.001278 | -0.0050992 | -0.001278 | 4.5232e-07 | 3.1061e-08 | 0.0077057 | 0.0077058 | 0.0077058 | 0.98478 | -0.29204 | 0.98468 | -0.29391 | 2.117
37 | 0.025081 | 0.0062979 | -0.025062 | -0.0062867 | 1.8308e-05 | 1.1285e-05 | 0.037902 | 0.037902 | 0.037902 | 0.98478 | -0.29204 | 0.98399 | -0.30736 | 10.4126
38 | 0.044349 | 0.011142 | -0.044289 | -0.011104 | 5.9827e-05 | 3.7838e-05 | 0.067022 | 0.067023 | 0.067023 | 0.98478 | -0.29204 | 0.98332 | -0.32035 | 18.4128
39 | 0.05236 | 0.013166 | -0.052317 | -0.013138 | 4.311e-05 | 2.7361e-05 | 0.079498 | 0.079498 | 0.079498 | 0.98024 | -0.38032 | 0.97936 | -0.39758 | 21.8401
40 | 0.023771 | 0.0059608 | -0.023762 | -0.0059554 | 8.8098e-06 | 5.4081e-06 | 0.035973 | 0.035973 | 0.035973 | 0.98332 | -0.32035 | 0.98293 | -0.32813 | 9.8826
41 | 0.0044855 | 0.0011241 | -0.0044853 | -0.0011241 | 2.1336e-07 | -2.0095e-08 | 0.0067877 | 0.0067877 | 0.0067877 | 0.98332 | -0.32035 | 0.98327 | -0.32135 | 1.8648
42 | 0.016033 | 0.0040194 | -0.016029 | -0.0040174 | 3.3746e-06 | 1.9658e-06 | 0.024262 | 0.024262 | 0.024262 | 0.98332 | -0.32035 | 0.9831 | -0.32477 | 6.6654
43 | 0.010681 | 0.0026771 | -0.010681 | -0.002677 | 2.1893e-07 | 1.1179e-07 | 0.016167 | 0.016167 | 0.016167 | 0.9831 | -0.32477 | 0.98308 | -0.3252 | 4.4416
44 | 0.0058536 | 0.001467 | -0.0058531 | -0.0014669 | 5.5189e-07 | 1.1572e-07 | 0.0088618 | 0.0088619 | 0.0088619 | 0.9829 | -0.32868 | 0.9828 | -0.33066 | 2.4346
45 | 0.053788 | 0.013525 | -0.053783 | -0.013522 | 4.4776e-06 | 2.8425e-06 | 0.081132 | 0.081132 | 0.081132 | 0.9867 | -0.25564 | 0.98661 | -0.25739 | 22.2889
46 | 0.042113 | 0.010568 | -0.042099 | -0.010559 | 1.4356e-05 | 9.0665e-06 | 0.063515 | 0.063515 | 0.063515 | 0.9867 | -0.25564 | 0.98633 | -0.26279 | 17.4491
47 | -0.095901 | -0.024092 | 0.096003 | 0.024158 | 0.00010192 | 6.5065e-05 | 0.14465 | 0.14465 | 0.14465 | 0.9867 | -0.25564 | 0.98784 | -0.2334 | 39.738
48 | 0.052047 | 0.013087 | -0.052015 | -0.013067 | 3.1901e-05 | 2.0241e-05 | 0.078513 | 0.078513 | 0.078513 | 0.98661 | -0.25739 | 0.98595 | -0.27023 | 21.5695
49 | 0.0017364 | 0.00043457 | -0.0017363 | -0.00043486 | 6.7563e-08 | -2.9226e-07 | 0.0026186 | 0.0026187 | 0.0026187 | 0.98661 | -0.25739 | 0.98657 | -0.2582 | 0.71943
50 | 0.019868 | 0.0049817 | -0.019867 | -0.0049813 | 6.3811e-07 | 3.8422e-07 | 0.029974 | 0.029974 | 0.029974 | 0.98633 | -0.26279 | 0.9863 | -0.26347 | 8.2346
51 | 0.022231 | 0.005577 | -0.022226 | -0.0055737 | 5.363e-06 | 3.2701e-06 | 0.033541 | 0.033541 | 0.033541 | 0.98633 | -0.26279 | 0.98607 | -0.26786 | 9.2145
52 | -0.10396 | -0.026151 | 0.10411 | 0.026252 | 0.0001584 | 0.00010115 | 0.15663 | 0.15663 | 0.15663 | 0.98784 | -0.2334 | 0.98949 | -0.20156 | 43.0289
53 | -0.011584 | -0.0029039 | 0.011588 | 0.002906 | 4.056e-06 | 2.1339e-06 | 0.017383 | 0.017383 | 0.017383 | 0.9916 | -0.16159 | 0.99198 | -0.15424 | 4.7756
54 | 0.011584 | 0.0029039 | -0.011581 | -0.0029025 | 2.6886e-06 | 1.4147e-06 | 0.017383 | 0.017383 | 0.017383 | 0.9916 | -0.16159 | 0.99135 | -0.16646 | 4.7756
55 | 0.024525 | 0.0061511 | -0.024513 | -0.0061435 | 1.2263e-05 | 7.5365e-06 | 0.03679 | 0.036791 | 0.036791 | 0.99198 | -0.15424 | 0.99144 | -0.16474 | 10.1073
56 | 0.011939 | 0.0029926 | -0.011937 | -0.0029918 | 1.5063e-06 | 8.0377e-07 | 0.017948 | 0.017948 | 0.017948 | 0.98982 | -0.19457 | 0.98968 | -0.19722 | 4.9309
57 | -0.14828 | -0.037583 | 0.14864 | 0.037815 | 0.00036343 | 0.00023159 | 0.22306 | 0.22306 | 0.22306 | 0.98982 | -0.19457 | 0.99246 | -0.1437 | 30.6405
58 | 0.13634 | 0.03459 | -0.13591 | -0.034315 | 0.00043155 | 0.00027584 | 0.20511 | 0.20511 | 0.20511 | 0.98982 | -0.19457 | 0.98639 | -0.26062 | 56.3503
59 | -0.18964 | -0.048136 | 0.18975 | 0.048207 | 0.00011149 | 7.0594e-05 | 0.28455 | 0.28455 | 0.28455 | 0.99246 | -0.1437 | 0.9931 | -0.13149 | 19.5433
60 | 0.040999 | 0.010321 | -0.040942 | -0.010285 | 5.7715e-05 | 3.6412e-05 | 0.061487 | 0.061487 | 0.061487 | 0.99246 | -0.1437 | 0.99094 | -0.1732 | 16.8921
61 | 0.012778 | 0.0032031 | -0.012776 | -0.003202 | 1.8884e-06 | 1.0377e-06 | 0.019334 | 0.019334 | 0.019334 | 0.98345 | -0.31897 | 0.98329 | -0.32207 | 5.3117
62 | 0.019867 | 0.0049813 | -0.019862 | -0.0049784 | 4.8076e-06 | 2.8948e-06 | 0.029974 | 0.029974 | 0.029974 | 0.9863 | -0.26347 | 0.98604 | -0.26855 | 8.2346
63 | 0.019272 | 0.0048335 | -0.019267 | -0.0048306 | 4.8158e-06 | 2.8885e-06 | 0.029084 | 0.029084 | 0.029084 | 0.98607 | -0.26786 | 0.9858 | -0.2731 | 7.9901
64 | 0.020633 | 0.0051765 | -0.020626 | -0.0051727 | 6.2317e-06 | 3.7716e-06 | 0.031203 | 0.031203 | 0.031203 | 0.98399 | -0.30736 | 0.98367 | -0.31369 | 8.5723
65 | -0.18975 | -0.048207 | 0.18985 | 0.04827 | 9.9397e-05 | 6.2936e-05 | 0.28455 | 0.28455 | 0.28455 | 0.9931 | -0.13149 | 0.99367 | -0.12061 | 19.5432
66 | 0.03409 | 0.0085678 | -0.034032 | -0.0085314 | 5.8039e-05 | 3.6385e-05 | 0.051199 | 0.051199 | 0.051199 | 0.99094 | -0.1732 | 0.9891 | -0.20892 | 14.0656
67 | 0.019267 | 0.0048306 | -0.019263 | -0.0048278 | 4.6585e-06 | 2.7942e-06 | 0.029084 | 0.029084 | 0.029084 | 0.9858 | -0.2731 | 0.98554 | -0.27817 | 7.9901
68 | 0.0097875 | 0.0024531 | -0.0097871 | -0.0024529 | 3.678e-07 | 1.7816e-07 | 0.014778 | 0.014778 | 0.014778 | 0.98554 | -0.27817 | 0.9855 | -0.27896 | 4.0598
69 | 0.19567 | 0.049799 | -0.19558 | -0.049741 | 9.186e-05 | 5.8198e-05 | 0.29298 | 0.29298 | 0.29298 | 0.9947 | -0.10087 | 0.99419 | -0.11062 | 20.1226
70 | 0.024197 | 0.0060705 | -0.024192 | -0.0060676 | 4.6539e-06 | 2.8556e-06 | 0.036199 | 0.036199 | 0.036199 | 0.9947 | -0.10087 | 0.99449 | -0.10491 | 9.9448
71 | -0.21987 | -0.055869 | 0.22 | 0.055951 | 0.00012794 | 8.1228e-05 | 0.32918 | 0.32918 | 0.32918 | 0.9947 | -0.10087 | 0.99534 | -0.088794 | 22.6087
72 | 0.19374 | 0.049279 | -0.19369 | -0.04925 | 4.6108e-05 | 2.9206e-05 | 0.29023 | 0.29023 | 0.29023 | 0.99419 | -0.11062 | 0.99393 | -0.11556 | 19.9332
73 | 0.02223 | 0.0055759 | -0.022221 | -0.0055701 | 9.5196e-06 | 5.795e-06 | 0.033264 | 0.033264 | 0.033264 | 0.99449 | -0.10491 | 0.99403 | -0.11389 | 9.1384
74 | -0.22189 | -0.056425 | 0.22195 | 0.056464 | 6.0709e-05 | 3.8548e-05 | 0.33202 | 0.33202 | 0.33202 | 0.99534 | -0.088794 | 0.99563 | -0.083117 | 22.8033
75 | 0.0056718 | 0.0014213 | -0.0056715 | -0.0014213 | 3.1179e-07 | 5.0789e-08 | 0.0085011 | 0.0085011 | 0.0085011 | 0.99279 | -0.13805 | 0.99273 | -0.1392 | 2.3355
76 | -0.007562 | -0.001895 | 0.0075626 | 0.0018952 | 5.9143e-07 | 2.1975e-07 | 0.011334 | 0.011334 | 0.011334 | 0.99279 | -0.13805 | 0.99287 | -0.1364 | 3.1138
77 | 0.0018902 | 0.00047362 | -0.0018902 | -0.00047372 | 2.8113e-08 | -1.0278e-07 | 0.002833 | 0.0028331 | 0.0028331 | 0.99279 | -0.13805 | 0.99277 | -0.13836 | 0.77832
78 | 0.0037792 | 0.00094704 | -0.0037792 | -0.00094708 | 7.2774e-08 | -3.1613e-08 | 0.0056647 | 0.0056648 | 0.0056648 | 0.99273 | -0.1392 | 0.9927 | -0.1396 | 1.5563
79 | -0.0093322 | -0.0023387 | 0.0093327 | 0.0023389 | 4.3014e-07 | 1.9945e-07 | 0.013986 | 0.013986 | 0.013986 | 0.99287 | -0.1364 | 0.99292 | -0.13544 | 3.8424
80 | -0.45918 | -0.1167 | 0.4597 | 0.11703 | 0.00052552 | 0.00033571 | 0.68556 | 0.68556 | 0.68556 | 0.99748 | -0.047954 | 0.99872 | -0.024216 | 47.0852
81 | 0.22476 | 0.056959 | -0.22466 | -0.056895 | 0.0001006 | 6.3887e-05 | 0.33551 | 0.33551 | 0.33551 | 0.99748 | -0.047954 | 0.99699 | -0.057274 | 23.0433
82 | 0.23442 | 0.059738 | -0.23428 | -0.05965 | 0.00013804 | 8.7721e-05 | 0.35005 | 0.35005 | 0.35005 | 0.99748 | -0.047954 | 0.99684 | -0.060165 | 24.0419
83 | -0.46441 | -0.11821 | 0.46468 | 0.11838 | 0.00027007 | 0.00017253 | 0.69257 | 0.69257 | 0.69257 | 0.99872 | -0.024216 | 0.99936 | -0.012162 | 47.5668
84 | 0.21995 | 0.055716 | -0.21975 | -0.055588 | 0.00020102 | 0.00012762 | 0.32849 | 0.32849 | 0.32849 | 0.99699 | -0.057274 | 0.996 | -0.07632 | 22.5612
85 | 0.22971 | 0.058504 | -0.22964 | -0.058463 | 6.4847e-05 | 4.1196e-05 | 0.34322 | 0.34322 | 0.34322 | 0.99684 | -0.060165 | 0.99653 | -0.066019 | 23.5731
86 | -0.19182 | -0.048762 | 0.19186 | 0.048791 | 4.6748e-05 | 2.9606e-05 | 0.28749 | 0.28749 | 0.28749 | 0.99367 | -0.12061 | 0.99393 | -0.11556 | 19.7452
87 | -0.18137 | -0.045793 | 0.18143 | 0.045834 | 6.4137e-05 | 4.0568e-05 | 0.27178 | 0.27178 | 0.27178 | 0.99342 | -0.1258 | 0.9938 | -0.11842 | 18.6665
88 | 0.018082 | 0.004534 | -0.018079 | -0.004532 | 3.4288e-06 | 2.0331e-06 | 0.027085 | 0.027085 | 0.027085 | 0.99342 | -0.1258 | 0.99321 | -0.12978 | 7.441
89 | 0.0060549 | 0.0015174 | -0.0060545 | -0.0015173 | 3.6098e-07 | 7.9519e-08 | 0.0090694 | 0.0090695 | 0.0090695 | 0.99342 | -0.1258 | 0.99335 | -0.12705 | 2.4916
90 | -0.18316 | -0.046268 | 0.1833 | 0.046358 | 0.00014226 | 9.0002e-05 | 0.27438 | 0.27438 | 0.27438 | 0.9938 | -0.11842 | 0.99464 | -0.10223 | 18.8446
91 | 0.016418 | 0.0041159 | -0.016417 | -0.0041151 | 1.2937e-06 | 7.5418e-07 | 0.024598 | 0.024598 | 0.024598 | 0.99321 | -0.12978 | 0.99313 | -0.13143 | 6.7577
92 | 0.0044068 | 0.0011043 | -0.0044067 | -0.0011043 | 9.5343e-08 | -1.4509e-08 | 0.0066013 | 0.0066013 | 0.0066013 | 0.99335 | -0.12705 | 0.99333 | -0.1275 | 1.8135
93 | 0.10957 | 0.027682 | -0.1094 | -0.027577 | 0.00016442 | 0.00010502 | 0.16458 | 0.16458 | 0.16458 | 0.99111 | -0.1702 | 0.98949 | -0.20156 | 45.2134
94 | 0.015585 | 0.0039072 | -0.015581 | -0.0039053 | 3.3421e-06 | 1.9281e-06 | 0.023366 | 0.023367 | 0.023367 | 0.99249 | -0.14376 | 0.99225 | -0.14826 | 6.4194
95 | -0.0017363 | -0.00043515 | 0.0017363 | 0.00043486 | 6.6064e-08 | -2.8572e-07 | 0.0026189 | 0.0026187 | 0.0026189 | 0.98653 | -0.259 | 0.98657 | -0.2582 | 0.71947
96 | -0.097232 | -0.024514 | 0.097391 | 0.024616 | 0.00015868 | 0.00010129 | 0.14499 | 0.14499 | 0.14499 | 0.99822 | -0.034041 | 1 | 0 | 39.833
97 | 0.016872 | 0.0042288 | -0.016871 | -0.0042282 | 1.0218e-06 | 5.9838e-07 | 0.025233 | 0.025233 | 0.025233 | 0.99494 | -0.097179 | 0.99487 | -0.09845 | 6.9322
98 | 0.012931 | 0.0032412 | -0.01293 | -0.0032408 | 8.1419e-07 | 4.492e-07 | 0.019571 | 0.019571 | 0.019571 | 0.98319 | -0.32411 | 0.98312 | -0.32544 | 5.3766
99 | -0.001891 | -0.00047394 | 0.0018911 | 0.00047387 | 1.8216e-08 | -6.6501e-08 | 0.0028346 | 0.0028346 | 0.0028346 | 0.99269 | -0.13981 | 0.9927 | -0.1396 | 0.77874
100 | 0.049029 | 0.012315 | -0.049015 | -0.012306 | 1.3872e-05 | 8.7944e-06 | 0.074503 | 0.074503 | 0.074503 | 0.97936 | -0.39758 | 0.97906 | -0.40351 | 20.468
101 | -0.017581 | -0.0044062 | 0.017587 | 0.00441 | 6.5847e-06 | 3.8924e-06 | 0.02646 | 0.02646 | 0.02646 | 0.98869 | -0.21678 | 0.9891 | -0.20892 | 7.2691
102 | -0.0048302 | -0.0012106 | 0.0048309 | 0.0012106 | 6.5629e-07 | -1.0362e-08 | 0.0072458 | 0.0072456 | 0.0072458 | 0.99195 | -0.15409 | 0.9921 | -0.15123 | 1.9906
103 | -0.01025 | -0.0025687 | 0.010251 | 0.0025694 | 1.4524e-06 | 7.1787e-07 | 0.015373 | 0.015373 | 0.015373 | 0.9921 | -0.15123 | 0.99225 | -0.14826 | 4.2234
104 | 0.010018 | 0.0025113 | -0.010016 | -0.0025103 | 2.0283e-06 | 9.9635e-07 | 0.015118 | 0.015119 | 0.015119 | 0.98604 | -0.26855 | 0.98582 | -0.2728 | 4.1535
105 | 0.020396 | 0.0051128 | -0.020396 | -0.0051128 | 1.2696e-07 | 7.6547e-08 | 0.030532 | 0.030532 | 0.030532 | 0.99403 | -0.11389 | 0.99402 | -0.11403 | 8.388
106 | -0.22384 | -0.056937 | 0.2239 | 0.056976 | 6.1731e-05 | 3.9202e-05 | 0.33484 | 0.33484 | 0.33484 | 0.99563 | -0.083117 | 0.99593 | -0.077395 | 22.997
107 | -0.011103 | -0.0027826 | 0.011104 | 0.0027829 | 6.0903e-07 | 3.139e-07 | 0.016639 | 0.016639 | 0.016639 | 0.99292 | -0.13544 | 0.99298 | -0.13429 | 4.5713
108 | -0.46938 | -0.11956 | 0.46966 | 0.11974 | 0.00027556 | 0.00017605 | 0.69958 | 0.69958 | 0.69958 | 0.99936 | -0.012162 | 1 | 0 | 48.0481
109 | 0.21524 | 0.054458 | -0.21524 | -0.054457 | 1.8812e-06 | 1.1938e-06 | 0.32176 | 0.32176 | 0.32176 | 0.996 | -0.07632 | 0.99599 | -0.076502 | 22.0986
110 | 0.22778 | 0.057995 | -0.22772 | -0.057956 | 6.1596e-05 | 3.9126e-05 | 0.34044 | 0.34044 | 0.34044 | 0.99653 | -0.066019 | 0.99623 | -0.071628 | 23.3818
111 | -0.18517 | -0.046827 | 0.18518 | 0.046827 | 1.1621e-06 | 7.3539e-07 | 0.27717 | 0.27717 | 0.27717 | 0.99464 | -0.10223 | 0.99465 | -0.1021 | 19.0367
112 | 0.014647 | 0.0036714 | -0.014645 | -0.0036708 | 1.0594e-06 | 6.021e-07 | 0.021945 | 0.021945 | 0.021945 | 0.99313 | -0.13143 | 0.99305 | -0.13295 | 6.029
113 | 0.0027078 | 0.00067856 | -0.0027078 | -0.00067863 | 5.0089e-08 | -7.3025e-08 | 0.0040563 | 0.0040564 | 0.0040564 | 0.99333 | -0.1275 | 0.99331 | -0.12789 | 1.1144
114 | 0.011192 | 0.0028051 | -0.011191 | -0.0028048 | 6.5085e-07 | 3.3986e-07 | 0.01694 | 0.01694 | 0.01694 | 0.98312 | -0.32544 | 0.98306 | -0.32666 | 4.6537
115 | -0.0019204 | -0.0004813 | 0.0019204 | 0.0004813 | 4.8491e-11 | -1.7114e-10 | 0.0028756 | 0.0028756 | 0.0028756 | 0.99373 | -0.11973 | 0.99373 | -0.11973 | 0.79001
116 | -0.0037789 | -0.00094707 | 0.0037789 | 0.00094704 | 6.9822e-08 | -3.0652e-08 | 0.0056585 | 0.0056585 | 0.0056585 | 0.99373 | -0.11973 | 0.99375 | -0.11934 | 1.5545
117 | -0.0056418 | -0.0014139 | 0.0056418 | 0.0014139 | 2.1179e-09 | 3.3074e-10 | 0.0084478 | 0.0084478 | 0.0084478 | 0.99375 | -0.11934 | 0.99375 | -0.11933 | 2.3208
118 | -0.0074729 | -0.0018728 | 0.0074731 | 0.0018729 | 2.6939e-07 | 9.8073e-08 | 0.01119 | 0.01119 | 0.01119 | 0.99375 | -0.11933 | 0.99379 | -0.11857 | 3.0741
119 | -0.012874 | -0.0032266 | 0.012875 | 0.0032271 | 8.1873e-07 | 4.481e-07 | 0.019292 | 0.019292 | 0.019292 | 0.99298 | -0.13429 | 0.99305 | -0.13295 | 5.3001
120 | 0.043713 | 0.010977 | -0.043691 | -0.010963 | 2.2449e-05 | 1.4197e-05 | 0.066445 | 0.066445 | 0.066445 | 0.97906 | -0.40351 | 0.97851 | -0.41428 | 18.2541
121 | 0.037292 | 0.009359 | -0.037262 | -0.0093401 | 3.0001e-05 | 1.8888e-05 | 0.056714 | 0.056714 | 0.056714 | 0.97851 | -0.41428 | 0.97765 | -0.43116 | 15.5808
122 | 0.015528 | 0.0038931 | -0.015523 | -0.0038906 | 4.3949e-06 | 2.5497e-06 | 0.023634 | 0.023635 | 0.023635 | 0.97765 | -0.43116 | 0.97735 | -0.4371 | 6.493
123 | 0.21343 | 0.054004 | -0.21338 | -0.053969 | 5.4217e-05 | 3.4403e-05 | 0.31905 | 0.31905 | 0.31905 | 0.99599 | -0.076502 | 0.99571 | -0.081797 | 21.9129
124 | 0.20887 | 0.052839 | -0.20887 | -0.052838 | 1.7311e-06 | 1.098e-06 | 0.31231 | 0.31231 | 0.31231 | 0.99571 | -0.081797 | 0.9957 | -0.08197 | 21.4501
125 | 0.20705 | 0.052382 | -0.20699 | -0.052349 | 5.1098e-05 | 3.2407e-05 | 0.30959 | 0.30959 | 0.30959 | 0.9957 | -0.08197 | 0.99543 | -0.087114 | 21.2631
126 | 0.20248 | 0.051218 | -0.20248 | -0.051217 | 1.5729e-06 | 9.9715e-07 | 0.30285 | 0.30285 | 0.30285 | 0.99543 | -0.087114 | 0.99542 | -0.087276 | 20.7999
127 | -0.0093325 | -0.0023389 | 0.0093325 | 0.0023389 | 1.1192e-08 | 5.182e-09 | 0.013974 | 0.013974 | 0.013974 | 0.99379 | -0.11857 | 0.99379 | -0.11855 | 3.8389
128 | -0.22578 | -0.057447 | 0.22584 | 0.057487 | 6.2774e-05 | 3.987e-05 | 0.33764 | 0.33764 | 0.33764 | 0.99593 | -0.077395 | 0.99623 | -0.071628 | 23.1898
129 | 0.018533 | 0.0046459 | -0.018532 | -0.004645 | 1.5946e-06 | 9.4895e-07 | 0.027744 | 0.027744 | 0.027744 | 0.99402 | -0.11403 | 0.99393 | -0.11583 | 7.622
130 | -0.18778 | -0.047479 | 0.18782 | 0.047506 | 4.2261e-05 | 2.6751e-05 | 0.28106 | 0.28106 | 0.28106 | 0.99465 | -0.1021 | 0.9949 | -0.097406 | 19.3038
131 | -0.18968 | -0.047972 | 0.18968 | 0.047973 | 1.2678e-06 | 8.0268e-07 | 0.28385 | 0.28385 | 0.28385 | 0.9949 | -0.097406 | 0.9949 | -0.097267 | 19.4949
132 | -0.19419 | -0.049104 | 0.19424 | 0.049132 | 4.5142e-05 | 2.8595e-05 | 0.2906 | 0.2906 | 0.2906 | 0.9949 | -0.097267 | 0.99516 | -0.092422 | 19.9585
133 | -0.011157 | -0.0027962 | 0.011158 | 0.0027966 | 5.9279e-07 | 3.0599e-07 | 0.016706 | 0.016706 | 0.016706 | 0.99379 | -0.11855 | 0.99385 | -0.11743 | 4.5895
134 | -0.19608 | -0.049595 | 0.19609 | 0.049596 | 1.4048e-06 | 8.9002e-07 | 0.29336 | 0.29336 | 0.29336 | 0.99516 | -0.092422 | 0.99516 | -0.092272 | 20.1482
135 | 0.016707 | 0.0041877 | -0.016707 | -0.0041876 | 6.8311e-08 | 3.9945e-08 | 0.025012 | 0.025012 | 0.025012 | 0.99393 | -0.11583 | 0.99392 | -0.11592 | 6.8715
136 | 0.014846 | 0.0037211 | -0.014845 | -0.0037205 | 1.0365e-06 | 5.9086e-07 | 0.022226 | 0.022226 | 0.022226 | 0.99392 | -0.11592 | 0.99385 | -0.11738 | 6.106
137 | -0.01302 | -0.0032632 | 0.01302 | 0.0032632 | 3.1847e-08 | 1.7486e-08 | 0.019494 | 0.019494 | 0.019494 | 0.99385 | -0.11743 | 0.99385 | -0.11738 | 5.3554
138 | -0.2006 | -0.050728 | 0.20065 | 0.050758 | 4.8087e-05 | 3.0479e-05 | 0.30011 | 0.30011 | 0.30011 | 0.99516 | -0.092272 | 0.99542 | -0.087276 | 20.6117
139 | 0.0059787 | 0.0014983 | -0.0059779 | -0.0014981 | 8.3977e-07 | 1.9096e-07 | 0.0090505 | 0.0090506 | 0.0090506 | 0.98297 | -0.32839 | 0.98282 | -0.33134 | 2.4864
140 | -0.0077165 | -0.0019338 | 0.0077168 | 0.0019339 | 2.8683e-07 | 1.1251e-07 | 0.011681 | 0.011681 | 0.011681 | 0.98297 | -0.32839 | 0.98301 | -0.32761 | 3.2091
141 | 0.0040353 | 0.0010112 | -0.0040352 | -0.0010112 | 8.7909e-08 | -2.3324e-08 | 0.0061095 | 0.0061095 | 0.0061095 | 0.98282 | -0.33134 | 0.98279 | -0.3318 | 1.6784
142 | -0.0094537 | -0.0023692 | 0.0094541 | 0.0023694 | 4.303e-07 | 2.0435e-07 | 0.01431 | 0.01431 | 0.01431 | 0.98301 | -0.32761 | 0.98306 | -0.32666 | 3.9314
143 | 0.0020958 | 0.00052519 | -0.0020958 | -0.00052525 | 2.4926e-08 | -6.7695e-08 | 0.0031732 | 0.0031732 | 0.0031732 | 0.98279 | -0.3318 | 0.98278 | -0.33205 | 0.87176

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.57341 | 0.14553

## res_load
| p_mw | q_mvar
0 | 0.0019607 | 0.0004914
1 | 0.0020447 | 0.00051245
2 | 0.001959 | 0.00049097
3 | 0.0019354 | 0.00048507
4 | 0.0019609 | 0.00049144
5 | 0.001938 | 0.0004857
6 | 0.001959 | 0.00049098
7 | 0.0020456 | 0.00051268
8 | 0.0019393 | 0.00048605
9 | 0.0079548 | 0.0019937
10 | 0.0083326 | 0.0020883
11 | 0.004435 | 0.0011115
12 | 0.0096867 | 0.0024277
13 | 0.0046802 | 0.001173
14 | 0.023762 | 0.0059554
15 | 0.0044853 | 0.0011241
16 | 0.005348 | 0.0013403
17 | 0.0069498 | 0.0017418
18 | 0.0079525 | 0.0019931
19 | 0.011581 | 0.0029025
20 | 0.011937 | 0.0029918
21 | 0.0038999 | 0.00097741
22 | 0.0078186 | 0.0019595
23 | 0.0029536 | 0.00074023
24 | 0.0050992 | 0.001278
25 | 0.0044297 | 0.0011102
26 | 0.0068518 | 0.0017172
27 | 0.0094753 | 0.0023747
28 | 0.001842 | 0.00046164
29 | 0.0019619 | 0.00049169
30 | 0.0018947 | 0.00047487
31 | 0.0018923 | 0.00047425
32 | 0.0017696 | 0.00044351
33 | 0.0018902 | 0.00047372
34 | 0.0047064 | 0.0011795
35 | 0.0047028 | 0.0011786
36 | 0.0045729 | 0.0011461
37 | 0.0019635 | 0.00049211
38 | 0.024513 | 0.0061435
39 | 0.0017319 | 0.00043405
40 | 0.0016602 | 0.00041608
41 | 0.0016477 | 0.00041295
42 | 0.012776 | 0.003202
43 | 0.0070683 | 0.0017715
44 | 0.0069717 | 0.0017473
45 | 0.0017363 | 0.00043515
46 | 0.016887 | 0.0042322
47 | 0.009356 | 0.0023448
48 | 0.0017378 | 0.00043554
49 | 0.0083308 | 0.0020879
50 | 0.0033777 | 0.00084652
51 | 0.001891 | 0.00047394
52 | 0.0018881 | 0.0004732
53 | 0.0032874 | 0.0008239
54 | 0.010681 | 0.002677
55 | 0.0058531 | 0.0014669
56 | 0.0052877 | 0.0013252
57 | 0.017581 | 0.0044062
58 | 0.016444 | 0.0041214
59 | 0.0048302 | 0.0012106
60 | 0.0054189 | 0.0013581
61 | 0.009844 | 0.0024671
62 | 0.0097871 | 0.0024529
63 | 0.001829 | 0.0004584
64 | 0.0018247 | 0.00045731
65 | 0.0018876 | 0.00047307
66 | 0.0017705 | 0.00044372
67 | 0.0047064 | 0.0011795
68 | 0.004509 | 0.0011301
69 | 0.0018656 | 0.00046757
70 | 0.0018703 | 0.00046875
71 | 0.0017705 | 0.00044372
72 | 0.0016989 | 0.00042578
73 | 0.0053302 | 0.0013359
74 | 0.0017384 | 0.00043569
75 | 0.0019204 | 0.0004813
76 | 0.0018584 | 0.00046577
77 | 0.0018628 | 0.00046687
78 | 0.0018311 | 0.00045891
79 | 0.0017705 | 0.00044372
80 | 0.0053023 | 0.0013289
81 | 0.0063989 | 0.0016037
82 | 0.021734 | 0.005447
83 | 0.015523 | 0.0038906
84 | 0.016871 | 0.0042282
85 | 0.0047064 | 0.0011795
86 | 0.0018099 | 0.00045359
87 | 0.004509 | 0.0011301
88 | 0.0018213 | 0.00045646
89 | 0.0045124 | 0.0011309
90 | 0.0018594 | 0.00046601
91 | 0.0018791 | 0.00047095
92 | 0.0018714 | 0.00046902
93 | 0.0018627 | 0.00046684
94 | 0.0027078 | 0.00067863
95 | 0.010016 | 0.0025103
96 | 0.0025994 | 0.00065146
97 | 0.0017705 | 0.00044372
98 | 0.0018601 | 0.00046617
99 | 0.0045134 | 0.0011312
100 | 0.0018247 | 0.00045731
101 | 0.0018473 | 0.00046298
102 | 0.0018247 | 0.00045731
103 | 0.0018613 | 0.00046649
104 | 0.001862 | 0.00046667
105 | 0.0018247 | 0.00045731
106 | 0.0045136 | 0.0011312
107 | 0.0018327 | 0.00045931
108 | 0.0017378 | 0.00043554
109 | 0.0019426 | 0.00048686
110 | 0.0017369 | 0.0004353
111 | 0.0019393 | 0.00048605
112 | 0.001737 | 0.00043534
113 | 0.0020958 | 0.00052525

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1