## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-585_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-585_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-585_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_261-585_0_5_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_261-585_0_5_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_261-585_0_5_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_261-585_0_5_node_7 | 0.4 | n |  | TRUE
7 | bus_LV_261-585_0_5_node_17 | 0.4 | n |  | TRUE
8 | bus_LV_261-585_0_5_node_21 | 0.4 | n |  | TRUE
9 | bus_LV_261-585_0_5_node_20 | 0.4 | n |  | TRUE
10 | bus_LV_261-585_0_5_node_19 | 0.4 | n |  | TRUE
11 | bus_LV_261-585_0_5_node_9 | 0.4 | n |  | TRUE
12 | bus_LV_261-585_0_5_node_10 | 0.4 | n |  | TRUE
13 | bus_LV_261-585_0_5_node_18 | 0.4 | n |  | TRUE
14 | bus_LV_261-585_0_5_node_11 | 0.4 | n |  | TRUE
15 | bus_LV_261-585_0_5_node_16 | 0.4 | n |  | TRUE
16 | bus_LV_261-585_0_5_node_13 | 0.4 | n |  | TRUE
17 | bus_LV_261-585_0_5_node_14 | 0.4 | n |  | TRUE
18 | bus_LV_261-585_0_5_node_15 | 0.4 | n |  | TRUE
19 | bus_MV_553_0_node_3 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-585_0_5_load_0 | 0 | 0.074145 | 0.018582 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-585_0_5_load_1 | 1 | 0.036862 | 0.0092385 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-585_0_5_load_3 | 3 | 0.03273 | 0.0082029 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-585_0_5_load_4 | 4 | 0.050526 | 0.012663 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-585_0_5_load_17 | 7 | 0.014429 | 0.0036161 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-585_0_5_load_21 | 8 | 0.094504 | 0.023685 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-585_0_5_load_20 | 9 | 0.01184 | 0.0029673 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-585_0_5_load_19 | 10 | 0.036767 | 0.0092147 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-585_0_5_load_18 | 13 | 0.013954 | 0.0034973 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-585_0_5_load_16 | 15 | 0.02331 | 0.005842 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-585_0_5_load_13 | 16 | 0.073271 | 0.018364 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-585_0_5_load_14 | 17 | 0.083339 | 0.020887 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-585_0_5_load_15 | 18 | 0.024578 | 0.0061599 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 18 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-585_0_5_line_0 |  | 0 | 1 | 0.022709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-585_0_5_line_1 |  | 0 | 2 | 0.017969 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
2 | LV_261-585_0_5_line_2 |  | 1 | 3 | 0.016831 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-585_0_5_line_3 |  | 2 | 4 | 0.030325 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
4 | LV_261-585_0_5_line_4 |  | 2 | 5 | 0.14311 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_261-585_0_5_line_5 |  | 2 | 6 | 0.14332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_261-585_0_5_line_6 |  | 4 | 7 | 0.0097194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
7 | LV_261-585_0_5_line_7 |  | 5 | 8 | 0.0126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_261-585_0_5_line_8 |  | 6 | 9 | 0.000944 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_261-585_0_5_line_9 |  | 6 | 10 | 0.0043772 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_261-585_0_5_line_10 |  | 7 | 15 | 0.021629 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
11 | LV_261-585_0_5_line_11 |  | 10 | 14 | 0.0086655 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_261-585_0_5_line_12 |  | 11 | 12 | 0.004059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-585_0_5_line_13 |  | 11 | 13 | 0.0032808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_261-585_0_5_line_14 |  | 12 | 14 | 0.072235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_261-585_0_5_line_15 |  | 15 | 18 | 0.012833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
16 | LV_261-585_0_5_line_16 |  | 16 | 17 | 0.016106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_261-585_0_5_line_17 |  | 17 | 18 | 0.013611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-585_0_5_trafo_15 | 0.63 MVA 20/0.4 kV | 19 | 18 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16
0 | 2683803.1599 | 1246657.1099 | 2683815.8639 | 1246675.9327
1 | 2683792.4063 | 1246642.7871 | 2683794.7977 | 1246645.167 | 2683795.9508 | 1246646.4287 | 2683803.1599 | 1246657.1099
2 | 2683815.8639 | 1246675.9327 | 2683825.2799 | 1246689.8837
3 | 2683792.4063 | 1246642.7871 | 2683781.3686 | 1246654.5731 | 2683771.9511 | 1246665.1706
4 | 2683719.6235 | 1246723.6632 | 2683723.9513 | 1246718.376 | 2683715.6845 | 1246711.5765 | 2683721.5403 | 1246705.0877 | 2683736.9594 | 1246690.0944 | 2683745.0032 | 1246682.2021 | 2683757.4853 | 1246669.2355 | 2683764.9208 | 1246660.5563 | 2683784.4304 | 1246637.8485 | 2683786.9191 | 1246634.9482 | 2683790.4283 | 1246630.9393 | 2683796.4033 | 1246639.0074 | 2683793.4848 | 1246641.8461 | 2683792.4063 | 1246642.7871
5 | 2683703.5964 | 1246700.4088 | 2683707.4793 | 1246702.5541 | 2683711.4968 | 1246705.335 | 2683725.1471 | 1246690.9505 | 2683743.1896 | 1246676.8948 | 2683746.5923 | 1246673.9963 | 2683747.8288 | 1246672.5683 | 2683759.6879 | 1246658.7811 | 2683778.5182 | 1246636.5641 | 2683779.775 | 1246634.7694 | 2683780.476 | 1246632.7445 | 2683780.6555 | 1246630.7344 | 2683785.8027 | 1246624.6805 | 2683790.4283 | 1246630.9393 | 2683796.4033 | 1246639.0074 | 2683793.4848 | 1246641.8461 | 2683792.4063 | 1246642.7871
6 | 2683771.9511 | 1246665.1706 | 2683767.9114 | 1246669.7164 | 2683765.5015 | 1246672.4417
7 | 2683719.6235 | 1246723.6632 | 2683721.755 | 1246724.6496 | 2683724.1314 | 1246725.9508 | 2683729.8322 | 1246730.8881
8 | 2683703.5964 | 1246700.4088 | 2683702.7694 | 1246699.9535
9 | 2683703.5964 | 1246700.4088 | 2683701.9099 | 1246703.2093 | 2683701.0765 | 1246702.4789
10 | 2683765.5015 | 1246672.4417 | 2683759.7735 | 1246678.9194 | 2683758.2241 | 1246682.7114 | 2683758.4125 | 1246685.9498 | 2683759.1691 | 1246688.5401 | 2683761.1548 | 1246690.7132
11 | 2683694.5597 | 1246696.7675 | 2683701.0765 | 1246702.4789
12 | 2683640.9431 | 1246657.2933 | 2683644.6514 | 1246658.969
13 | 2683640.9431 | 1246657.2933 | 2683641.2586 | 1246660.5589
14 | 2683644.6514 | 1246658.969 | 2683645.4095 | 1246659.3133 | 2683650.4916 | 1246661.6089 | 2683645.8777 | 1246671.6401 | 2683694.5597 | 1246696.7675
15 | 2683761.1548 | 1246690.7132 | 2683761.5572 | 1246691.1536 | 2683770.6802 | 1246699.308
16 | 2683780.8356 | 1246708.3705 | 2683792.8637 | 1246719.0819
17 | 2683780.8356 | 1246708.3705 | 2683776.3584 | 1246704.3835 | 2683770.6802 | 1246699.308

## bus_geodata
| x | y | coords
0 | 2683803.1599 | 1246657.1099
1 | 2683815.8639 | 1246675.9327
2 | 2683792.4063 | 1246642.7871
3 | 2683825.2799 | 1246689.8837
4 | 2683771.9511 | 1246665.1706
5 | 2683719.6235 | 1246723.6632
6 | 2683703.5964 | 1246700.4088
7 | 2683765.5015 | 1246672.4417
8 | 2683729.8322 | 1246730.8881
9 | 2683702.7694 | 1246699.9535
10 | 2683701.0765 | 1246702.4789
11 | 2683640.9431 | 1246657.2933
12 | 2683644.6514 | 1246658.969
13 | 2683641.2586 | 1246660.5589
14 | 2683694.5597 | 1246696.7675
15 | 2683761.1548 | 1246690.7132
16 | 2683792.8637 | 1246719.0819
17 | 2683780.8356 | 1246708.3705
18 | 2683770.6802 | 1246699.308
19 | 2683770.6802 | 1246699.308

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99101 | -0.17187 | 0.074145 | 0.018582
1 | 0.98957 | -0.19995 | 0.036862 | 0.0092385
2 | 0.9922 | -0.14897 | 0 | 0
3 | 0.98906 | -0.20976 | 0.03273 | 0.0082029
4 | 0.995 | -0.09529 | 0.050526 | 0.012663
5 | 0.97966 | -0.39149 | 0 | 0
6 | 0.98393 | -0.30906 | 0 | 0
7 | 0.99605 | -0.075271 | 0.014429 | 0.0036161
8 | 0.97855 | -0.41314 | 0.094504 | 0.023685
9 | 0.98392 | -0.30926 | 0.01184 | 0.0029673
10 | 0.98372 | -0.31306 | 0.036767 | 0.0092147
11 | 0.98263 | -0.33444 | 0 | 0
12 | 0.98268 | -0.33341 | 0 | 0
13 | 0.98259 | -0.33526 | 0.013954 | 0.0034973
14 | 0.98361 | -0.31524 | 0 | 0
15 | 0.99847 | -0.029053 | 0.02331 | 0.005842
16 | 0.99796 | -0.039225 | 0.073271 | 0.018364
17 | 0.99903 | -0.018595 | 0.083339 | 0.020887
18 | 1 | 0 | -0.55201 | -0.13975
19 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.069701 | 0.01751 | -0.069607 | -0.017451 | 9.3299e-05 | 5.9419e-05 | 0.10467 | 0.10467 | 0.10467 | 0.99101 | -0.17187 | 0.98957 | -0.19995 | 28.7558
1 | -0.14385 | -0.036093 | 0.144 | 0.036193 | 0.0001572 | 0.00010014 | 0.216 | 0.216 | 0.216 | 0.99101 | -0.17187 | 0.9922 | -0.14897 | 29.6703
2 | 0.032745 | 0.0082125 | -0.03273 | -0.0082029 | 1.5304e-05 | 9.5786e-06 | 0.049241 | 0.049242 | 0.049242 | 0.98957 | -0.19995 | 0.98906 | -0.20976 | 13.5279
3 | -0.30278 | -0.076648 | 0.30356 | 0.077148 | 0.00078253 | 0.00049964 | 0.45436 | 0.45436 | 0.45436 | 0.9922 | -0.14897 | 0.995 | -0.09529 | 41.6077
4 | 0.09571 | 0.024455 | -0.094602 | -0.023747 | 0.0011083 | 0.00070746 | 0.1437 | 0.14371 | 0.14371 | 0.9922 | -0.14897 | 0.97966 | -0.39149 | 39.4795
5 | 0.063067 | 0.016 | -0.062586 | -0.015694 | 0.00048149 | 0.00030632 | 0.094652 | 0.094653 | 0.094653 | 0.9922 | -0.14897 | 0.98393 | -0.30906 | 26.0035
6 | -0.35409 | -0.08981 | 0.35443 | 0.090028 | 0.00034116 | 0.00021797 | 0.52992 | 0.52992 | 0.52992 | 0.995 | -0.09529 | 0.99605 | -0.075271 | 48.5271
7 | 0.094602 | 0.023747 | -0.094504 | -0.023685 | 9.7574e-05 | 6.2289e-05 | 0.14371 | 0.14371 | 0.14371 | 0.97966 | -0.39149 | 0.97855 | -0.41314 | 39.4795
8 | 0.01184 | 0.0029674 | -0.01184 | -0.0029673 | 1.135e-07 | 6.065e-08 | 0.017906 | 0.017906 | 0.017906 | 0.98393 | -0.30906 | 0.98392 | -0.30926 | 4.9192
9 | 0.050746 | 0.012726 | -0.050736 | -0.01272 | 9.6683e-06 | 6.1321e-06 | 0.076747 | 0.076747 | 0.076747 | 0.98393 | -0.30906 | 0.98372 | -0.31306 | 21.0843
10 | -0.36886 | -0.093645 | 0.36968 | 0.09417 | 0.00082224 | 0.00052539 | 0.55147 | 0.55147 | 0.55147 | 0.99605 | -0.075271 | 0.99847 | -0.029053 | 50.501
11 | 0.013969 | 0.0035056 | -0.013968 | -0.0035048 | 1.4511e-06 | 8.1869e-07 | 0.021132 | 0.021132 | 0.021132 | 0.98372 | -0.31306 | 0.98361 | -0.31524 | 5.8054
12 | -0.013955 | -0.0034976 | 0.013955 | 0.003498 | 6.7972e-07 | 3.836e-07 | 0.021132 | 0.021132 | 0.021132 | 0.98263 | -0.33444 | 0.98268 | -0.33341 | 5.8055
13 | 0.013955 | 0.0034976 | -0.013954 | -0.0034973 | 5.4941e-07 | 3.1007e-07 | 0.021132 | 0.021132 | 0.021132 | 0.98263 | -0.33444 | 0.98259 | -0.33526 | 5.8055
14 | -0.013955 | -0.003498 | 0.013968 | 0.0035048 | 1.2096e-05 | 6.8257e-06 | 0.021132 | 0.021132 | 0.021132 | 0.98268 | -0.33341 | 0.98361 | -0.31524 | 5.8055
15 | -0.39299 | -0.10001 | 0.39354 | 0.10036 | 0.00055123 | 0.00035229 | 0.58621 | 0.58621 | 0.58621 | 0.99847 | -0.029053 | 1 | 0 | 53.6822
16 | -0.073271 | -0.018364 | 0.073343 | 0.018409 | 7.2091e-05 | 4.5927e-05 | 0.10925 | 0.10925 | 0.10925 | 0.99796 | -0.039225 | 0.99903 | -0.018595 | 30.0142
17 | -0.15668 | -0.039296 | 0.15682 | 0.039385 | 0.000139 | 8.8606e-05 | 0.23338 | 0.23338 | 0.23338 | 0.99903 | -0.018595 | 1 | 0 | 32.0579

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.57659 | 0.14591

## res_load
| p_mw | q_mvar
0 | 0.074145 | 0.018582
1 | 0.036862 | 0.0092385
2 | 0.03273 | 0.0082029
3 | 0.050526 | 0.012663
4 | 0.014429 | 0.0036161
5 | 0.094504 | 0.023685
6 | 0.01184 | 0.0029673
7 | 0.036767 | 0.0092147
8 | 0.013954 | 0.0034973
9 | 0.02331 | 0.005842
10 | 0.073271 | 0.018364
11 | 0.083339 | 0.020887
12 | 0.024578 | 0.0061599

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1