## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-586_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-586_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-586_0_4_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_261-586_0_4_node_12 | 0.4 | n |  | TRUE
4 | bus_LV_261-586_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_261-586_0_4_node_14 | 0.4 | n |  | TRUE
6 | bus_LV_261-586_0_4_node_5 | 0.4 | n |  | TRUE
7 | bus_LV_261-586_0_4_node_6 | 0.4 | n |  | TRUE
8 | bus_LV_261-586_0_4_node_9 | 0.4 | n |  | TRUE
9 | bus_LV_261-586_0_4_node_17 | 0.4 | n |  | TRUE
10 | bus_LV_261-586_0_4_node_18 | 0.4 | n |  | TRUE
11 | bus_LV_261-586_0_4_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_261-586_0_4_node_10 | 0.4 | n |  | TRUE
13 | bus_LV_261-586_0_4_node_15 | 0.4 | n |  | TRUE
14 | bus_LV_261-586_0_4_node_20 | 0.4 | n |  | TRUE
15 | bus_LV_261-586_0_4_node_21 | 0.4 | n |  | TRUE
16 | bus_LV_261-586_0_4_node_13 | 0.4 | n |  | TRUE
17 | bus_LV_261-586_0_4_node_16 | 0.4 | n |  | TRUE
18 | bus_LV_261-586_0_4_node_19 | 0.4 | n |  | TRUE
19 | bus_MV_548_0_node_36 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-586_0_4_load_0 | 0 | 0.038346 | 0.0096105 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-586_0_4_load_1 | 1 | 0.027583 | 0.0069128 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-586_0_4_load_3 | 2 | 0.036649 | 0.009185 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-586_0_4_load_4 | 4 | 0.031383 | 0.0078654 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-586_0_4_load_14 | 5 | 0.030207 | 0.0075706 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-586_0_4_load_17 | 9 | 0.06444 | 0.01615 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-586_0_4_load_18 | 10 | 0.083536 | 0.020936 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-586_0_4_load_15 | 13 | 0.0068487 | 0.0017164 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-586_0_4_load_20 | 14 | 0.051277 | 0.012851 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-586_0_4_load_21 | 15 | 0.01003 | 0.0025137 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-586_0_4_load_13 | 16 | 0.030876 | 0.0077381 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-586_0_4_load_16 | 17 | 0.053679 | 0.013453 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-586_0_4_load_19 | 18 | 0.025736 | 0.0064502 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 2 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-586_0_4_line_0 |  | 0 | 1 | 0.012941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-586_0_4_line_1 |  | 1 | 2 | 0.014724 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-586_0_4_line_2 |  | 2 | 3 | 0.0071851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
3 | LV_261-586_0_4_line_3 |  | 3 | 16 | 0.031103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-586_0_4_line_4 |  | 3 | 6 | 0.017045 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
5 | LV_261-586_0_4_line_5 |  | 4 | 5 | 0.012495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_261-586_0_4_line_6 |  | 5 | 16 | 0.018779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_261-586_0_4_line_7 |  | 6 | 7 | 0.025038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_261-586_0_4_line_8 |  | 6 | 8 | 0.017137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_261-586_0_4_line_9 |  | 6 | 9 | 0.045075 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_261-586_0_4_line_10 |  | 7 | 10 | 0.01553 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_261-586_0_4_line_11 |  | 8 | 12 | 0.081551 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_261-586_0_4_line_12 |  | 8 | 14 | 0.0050107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-586_0_4_line_13 |  | 9 | 17 | 0.00098545 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_261-586_0_4_line_14 |  | 11 | 12 | 0.081165 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_261-586_0_4_line_15 |  | 11 | 13 | 0.02525 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_261-586_0_4_line_16 |  | 12 | 15 | 0.00079659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_261-586_0_4_line_17 |  | 14 | 18 | 0.017445 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-586_0_4_trafo_3 | 0.63 MVA 20/0.4 kV | 19 | 2 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14
0 | 2683834.5541 | 1246703.6247 | 2683841.7937 | 1246714.3511
1 | 2683841.7937 | 1246714.3511 | 2683850.0306 | 1246726.5552
2 | 2683853.1109 | 1246732.8 | 2683853.1046 | 1246731.1098 | 2683850.0306 | 1246726.5552
3 | 2683853.1109 | 1246732.8 | 2683852.5917 | 1246734.7942 | 2683851.1396 | 1246737.5757 | 2683849.3282 | 1246740.6635 | 2683844.2205 | 1246743.3933 | 2683834.7694 | 1246747.1625 | 2683830.3431 | 1246748.1895 | 2683828.5396 | 1246747.9906
4 | 2683853.1109 | 1246732.8 | 2683856.746 | 1246733.2407 | 2683861.8365 | 1246733.8575 | 2683862.6209 | 1246730.2104 | 2683863.5749 | 1246725.7873
5 | 2683813.488 | 1246737.4209 | 2683809.6252 | 1246734.0085 | 2683804.1433 | 1246729.1267
6 | 2683813.488 | 1246737.4209 | 2683824.0031 | 1246746.71 | 2683826.8734 | 1246747.8069 | 2683828.5396 | 1246747.9906
7 | 2683885.5907 | 1246716.5807 | 2683883.4639 | 1246716.862 | 2683881.6247 | 1246717.1028 | 2683879.6461 | 1246719.7212 | 2683877.9971 | 1246721.4769 | 2683875.6099 | 1246723.0777 | 2683872.005 | 1246724.7724 | 2683868.6469 | 1246725.5811 | 2683865.5073 | 1246725.9036 | 2683863.5749 | 1246725.7873
8 | 2683863.5749 | 1246725.7873 | 2683862.6209 | 1246730.2104 | 2683861.8365 | 1246733.8575 | 2683863.7001 | 1246738.832 | 2683864.9522 | 1246742.1744
9 | 2683863.5749 | 1246725.7873 | 2683861.1051 | 1246725.2186 | 2683859.1954 | 1246722.9677 | 2683837.0177 | 1246690.1739
10 | 2683885.5907 | 1246716.5807 | 2683894.5131 | 1246703.8692
11 | 2683834.5745 | 1246791.3811 | 2683839.4471 | 1246786.0461 | 2683849.2461 | 1246775.2989 | 2683849.9685 | 1246775.4982 | 2683853.9226 | 1246771.54 | 2683852.1099 | 1246769.9132 | 2683839.6523 | 1246758.7178 | 2683838.884 | 1246758.0286 | 2683837.3622 | 1246756.6616 | 2683843.9019 | 1246753.0959 | 2683849.7564 | 1246749.9097 | 2683854.6668 | 1246747.2438 | 2683858.991 | 1246744.8921 | 2683860.4733 | 1246744.2459 | 2683864.9522 | 1246742.1744
12 | 2683864.9522 | 1246742.1744 | 2683869.5938 | 1246740.287
13 | 2683837.0177 | 1246690.1739 | 2683836.4657 | 1246689.3576
14 | 2683834.5745 | 1246791.3811 | 2683843.0095 | 1246799.0949 | 2683847.9026 | 1246805.1241 | 2683849.194 | 1246806.7546 | 2683875.7379 | 1246783.4239 | 2683882.8308 | 1246792.5531 | 2683887.766 | 1246800.4065 | 2683888.4236 | 1246801.4499 | 2683889.7461 | 1246803.5479
15 | 2683889.7461 | 1246803.5479 | 2683903.2525 | 1246795.0772 | 2683907.914 | 1246794.5094 | 2683912.2901 | 1246795.9612
16 | 2683833.9876 | 1246790.8426 | 2683834.5745 | 1246791.3811
17 | 2683885.9408 | 1246734.2057 | 2683885.2016 | 1246734.4661 | 2683874.5715 | 1246738.2631 | 2683869.5938 | 1246740.287

## bus_geodata
| x | y | coords
0 | 2683834.5541 | 1246703.6247
1 | 2683841.7937 | 1246714.3511
2 | 2683850.0306 | 1246726.5552
3 | 2683853.1109 | 1246732.8
4 | 2683804.1433 | 1246729.1267
5 | 2683813.488 | 1246737.4209
6 | 2683863.5749 | 1246725.7873
7 | 2683885.5907 | 1246716.5807
8 | 2683864.9522 | 1246742.1744
9 | 2683837.0177 | 1246690.1739
10 | 2683894.5131 | 1246703.8692
11 | 2683889.7461 | 1246803.5479
12 | 2683834.5745 | 1246791.3811
13 | 2683912.2901 | 1246795.9612
14 | 2683869.5938 | 1246740.287
15 | 2683833.9876 | 1246790.8426
16 | 2683828.5396 | 1246747.9906
17 | 2683836.4657 | 1246689.3576
18 | 2683885.9408 | 1246734.2057
19 | 2683853.1109 | 1246732.8

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99867 | -0.025602 | 0.038346 | 0.0096105
1 | 0.99912 | -0.016934 | 0.027583 | 0.0069128
2 | 1 | 0 | -0.45763 | -0.11507
3 | 0.99915 | -0.016212 | 0 | 0
4 | 0.99512 | -0.093777 | 0.031383 | 0.0078654
5 | 0.99548 | -0.086878 | 0.030207 | 0.0075706
6 | 0.99762 | -0.045575 | 0 | 0
7 | 0.99571 | -0.082274 | 0 | 0
8 | 0.99615 | -0.073796 | 0 | 0
9 | 0.99276 | -0.13927 | 0.06444 | 0.01615
10 | 0.99453 | -0.10511 | 0.083536 | 0.020936
11 | 0.99439 | -0.10781 | 0 | 0
12 | 0.9949 | -0.09801 | 0 | 0
13 | 0.99424 | -0.11085 | 0.0068487 | 0.0017164
14 | 0.9958 | -0.080576 | 0.051277 | 0.012851
15 | 0.99489 | -0.09815 | 0.01003 | 0.0025137
16 | 0.99653 | -0.066556 | 0.030876 | 0.0077381
17 | 0.99271 | -0.14021 | 0.053679 | 0.013453
18 | 0.99539 | -0.088471 | 0.025736 | 0.0064502
19 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.038346 | -0.0096105 | 0.038362 | 0.0096204 | 1.5842e-05 | 9.9696e-06 | 0.057136 | 0.057136 | 0.057136 | 0.99867 | -0.025602 | 0.99912 | -0.016934 | 15.6966
1 | -0.065945 | -0.016533 | 0.065998 | 0.016567 | 5.326e-05 | 3.3894e-05 | 0.098215 | 0.098215 | 0.098215 | 0.99912 | -0.016934 | 1 | 0 | 26.9822
2 | 0.38998 | 0.098498 | -0.38968 | -0.098305 | 0.00030272 | 0.00019346 | 0.58056 | 0.58056 | 0.58056 | 1 | 0 | 0.99915 | -0.016212 | 53.1652
3 | 0.092759 | 0.023361 | -0.092536 | -0.023219 | 0.00022271 | 0.00014213 | 0.13818 | 0.13818 | 0.13818 | 0.99915 | -0.016212 | 0.99653 | -0.066556 | 37.9626
4 | 0.29692 | 0.074944 | -0.2965 | -0.074678 | 0.00041696 | 0.00026619 | 0.44238 | 0.44238 | 0.44238 | 0.99915 | -0.016212 | 0.99762 | -0.045575 | 40.511
5 | -0.031383 | -0.0078654 | 0.031394 | 0.0078719 | 1.0319e-05 | 6.4415e-06 | 0.046928 | 0.046928 | 0.046928 | 0.99512 | -0.093777 | 0.99548 | -0.086878 | 12.8923
6 | -0.061601 | -0.015443 | 0.061661 | 0.01548 | 5.9711e-05 | 3.7971e-05 | 0.092081 | 0.092081 | 0.092081 | 0.99548 | -0.086878 | 0.99653 | -0.066556 | 25.2969
7 | 0.083773 | 0.021088 | -0.083627 | -0.020994 | 0.00014667 | 9.3545e-05 | 0.12499 | 0.12499 | 0.12499 | 0.99762 | -0.045575 | 0.99571 | -0.082274 | 34.3368
8 | 0.094076 | 0.023647 | -0.09395 | -0.023566 | 0.00012658 | 8.0786e-05 | 0.14035 | 0.14035 | 0.14035 | 0.99762 | -0.045575 | 0.99615 | -0.073796 | 38.5565
9 | 0.11865 | 0.029944 | -0.11812 | -0.029605 | 0.00052986 | 0.00033852 | 0.17705 | 0.17705 | 0.17705 | 0.99762 | -0.045575 | 0.99276 | -0.13927 | 48.64
10 | 0.083627 | 0.020994 | -0.083536 | -0.020936 | 9.0978e-05 | 5.8024e-05 | 0.12499 | 0.12499 | 0.12499 | 0.99571 | -0.082274 | 0.99453 | -0.10511 | 34.3368
11 | 0.016902 | 0.0042429 | -0.016883 | -0.0042315 | 1.9498e-05 | 1.1419e-05 | 0.02525 | 0.025251 | 0.025251 | 0.99615 | -0.073796 | 0.9949 | -0.09801 | 6.937
12 | 0.077048 | 0.019323 | -0.077023 | -0.019307 | 2.4891e-05 | 1.5865e-05 | 0.1151 | 0.1151 | 0.1151 | 0.99615 | -0.073796 | 0.9958 | -0.080576 | 31.6196
13 | 0.053682 | 0.013455 | -0.053679 | -0.013453 | 2.3925e-06 | 1.5185e-06 | 0.080462 | 0.080462 | 0.080462 | 0.99276 | -0.13927 | 0.99271 | -0.14021 | 22.105
14 | -0.0068496 | -0.0017167 | 0.0068528 | 0.0017177 | 3.1976e-06 | 9.9299e-07 | 0.01025 | 0.01025 | 0.01025 | 0.99439 | -0.10781 | 0.9949 | -0.09801 | 2.8159
15 | 0.0068496 | 0.0017167 | -0.0068487 | -0.0017164 | 9.9478e-07 | 3.0916e-07 | 0.01025 | 0.01025 | 0.01025 | 0.99439 | -0.10781 | 0.99424 | -0.11085 | 2.8159
16 | 0.01003 | 0.0025137 | -0.01003 | -0.0025137 | 6.7223e-08 | 3.2678e-08 | 0.015001 | 0.015001 | 0.015001 | 0.9949 | -0.09801 | 0.99489 | -0.09815 | 4.1212
17 | 0.025746 | 0.0064561 | -0.025736 | -0.0064502 | 9.6833e-06 | 5.9705e-06 | 0.038473 | 0.038473 | 0.038473 | 0.9958 | -0.080576 | 0.99539 | -0.088471 | 10.5696

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.49428 | 0.12425

## res_load
| p_mw | q_mvar
0 | 0.038346 | 0.0096105
1 | 0.027583 | 0.0069128
2 | 0.036649 | 0.009185
3 | 0.031383 | 0.0078654
4 | 0.030207 | 0.0075706
5 | 0.06444 | 0.01615
6 | 0.083536 | 0.020936
7 | 0.0068487 | 0.0017164
8 | 0.051277 | 0.012851
9 | 0.01003 | 0.0025137
10 | 0.030876 | 0.0077381
11 | 0.053679 | 0.013453
12 | 0.025736 | 0.0064502

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1