## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-597_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-597_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-597_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_261-597_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_261-597_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_261-597_0_3_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_261-597_0_3_node_12 | 0.4 | n |  | TRUE
7 | bus_LV_261-597_0_3_node_11 | 0.4 | n |  | TRUE
8 | bus_LV_261-597_0_3_node_8 | 0.4 | n |  | TRUE
9 | bus_LV_261-597_0_3_node_17 | 0.4 | n |  | TRUE
10 | bus_LV_261-597_0_3_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_261-597_0_3_node_16 | 0.4 | n |  | TRUE
12 | bus_LV_261-597_0_3_node_19 | 0.4 | n |  | TRUE
13 | bus_LV_261-597_0_3_node_7 | 0.4 | n |  | TRUE
14 | bus_LV_261-597_0_3_node_10 | 0.4 | n |  | TRUE
15 | bus_LV_261-597_0_3_node_13 | 0.4 | n |  | TRUE
16 | bus_LV_261-597_0_3_node_32 | 0.4 | n |  | TRUE
17 | bus_LV_261-597_0_3_node_30 | 0.4 | n |  | TRUE
18 | bus_LV_261-597_0_3_node_35 | 0.4 | n |  | TRUE
19 | bus_LV_261-597_0_3_node_15 | 0.4 | n |  | TRUE
20 | bus_LV_261-597_0_3_node_18 | 0.4 | n |  | TRUE
21 | bus_LV_261-597_0_3_node_14 | 0.4 | n |  | TRUE
22 | bus_LV_261-597_0_3_node_34 | 0.4 | n |  | TRUE
23 | bus_LV_261-597_0_3_node_24 | 0.4 | n |  | TRUE
24 | bus_LV_261-597_0_3_node_20 | 0.4 | n |  | TRUE
25 | bus_LV_261-597_0_3_node_21 | 0.4 | n |  | TRUE
26 | bus_LV_261-597_0_3_node_22 | 0.4 | n |  | TRUE
27 | bus_LV_261-597_0_3_node_23 | 0.4 | n |  | TRUE
28 | bus_LV_261-597_0_3_node_33 | 0.4 | n |  | TRUE
29 | bus_LV_261-597_0_3_node_28 | 0.4 | n |  | TRUE
30 | bus_LV_261-597_0_3_node_25 | 0.4 | n |  | TRUE
31 | bus_LV_261-597_0_3_node_26 | 0.4 | n |  | TRUE
32 | bus_MV_527_0_node_127 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-597_0_3_load_0 | 0 | 0.0127 | 0.003183 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-597_0_3_load_1 | 1 | 0.0077852 | 0.0019512 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-597_0_3_load_4 | 4 | 0.0075446 | 0.0018909 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-597_0_3_load_11 | 7 | 0.011139 | 0.0027918 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-597_0_3_load_17 | 9 | 0.0045355 | 0.0011367 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-597_0_3_load_16 | 11 | 0.004598 | 0.0011524 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-597_0_3_load_13 | 15 | 0.013611 | 0.0034113 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-597_0_3_load_30 | 17 | 0.043444 | 0.010888 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-597_0_3_load_35 | 18 | 0.003197 | 0.00080123 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-597_0_3_load_15 | 19 | 0.0037263 | 0.0009339 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-597_0_3_load_18 | 20 | 0.00609 | 0.0015263 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-597_0_3_load_14 | 21 | 0.0045861 | 0.0011494 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-597_0_3_load_34 | 22 | 0.0052865 | 0.0013249 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-597_0_3_load_24 | 23 | 0.049748 | 0.012468 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-597_0_3_load_20 | 24 | 0.059248 | 0.014849 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-597_0_3_load_22 | 26 | 0.062778 | 0.015734 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-597_0_3_load_23 | 27 | 0.03221 | 0.0080725 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_261-597_0_3_load_28 | 29 | 0.017058 | 0.0042751 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_261-597_0_3_load_25 | 30 | 0.066611 | 0.016694 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 26 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-597_0_3_line_0 |  | 0 | 1 | 0.030981 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-597_0_3_line_1 |  | 0 | 2 | 0.0078608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-597_0_3_line_2 |  | 1 | 3 | 0.086561 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-597_0_3_line_3 |  | 2 | 4 | 0.020706 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-597_0_3_line_4 |  | 2 | 5 | 0.014213 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_261-597_0_3_line_5 |  | 3 | 6 | 0.057303 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_261-597_0_3_line_6 |  | 4 | 7 | 0.026597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_261-597_0_3_line_7 |  | 5 | 8 | 0.008473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_261-597_0_3_line_8 |  | 5 | 9 | 0.032494 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_261-597_0_3_line_9 |  | 6 | 18 | 0.061878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_261-597_0_3_line_10 |  | 8 | 15 | 0.0069985 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_261-597_0_3_line_11 |  | 9 | 19 | 0.014386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_261-597_0_3_line_12 |  | 10 | 11 | 0.013158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-597_0_3_line_13 |  | 10 | 12 | 0.022034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_261-597_0_3_line_14 |  | 11 | 19 | 0.014521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_261-597_0_3_line_15 |  | 12 | 20 | 0.01099 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_261-597_0_3_line_16 |  | 13 | 14 | 0.089098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_261-597_0_3_line_17 |  | 13 | 15 | 0.020163 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_261-597_0_3_line_18 |  | 14 | 16 | 0.024275 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_261-597_0_3_line_19 |  | 14 | 17 | 0.035088 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_261-597_0_3_line_20 |  | 16 | 22 | 0.0021956 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_261-597_0_3_line_21 |  | 16 | 23 | 0.022497 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_261-597_0_3_line_22 |  | 20 | 21 | 0.028792 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_261-597_0_3_line_23 |  | 23 | 25 | 0.0083874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
24 | LV_261-597_0_3_line_24 |  | 24 | 25 | 0.015026 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
25 | LV_261-597_0_3_line_25 |  | 24 | 26 | 0.015158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
26 | LV_261-597_0_3_line_26 |  | 25 | 27 | 0.026469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_261-597_0_3_line_27 |  | 27 | 28 | 0.036986 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_261-597_0_3_line_28 |  | 28 | 29 | 0.030589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_261-597_0_3_line_29 |  | 29 | 31 | 0.023808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_261-597_0_3_line_30 |  | 30 | 31 | 0.036682 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-597_0_3_trafo_22 | 0.63 MVA 20/0.4 kV | 32 | 26 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2680082.5605 | 1248614.4142 | 2680080.0894 | 1248614.9667 | 2680069.6564 | 1248622.5091 | 2680056.6206 | 1248631.0329
1 | 2680090.2352 | 1248613.5916 | 2680088.2021 | 1248613.1528 | 2680082.5605 | 1248614.4142
2 | 2679986.0872 | 1248681.1909 | 2680046.0976 | 1248637.9135 | 2680056.6206 | 1248631.0329
3 | 2680090.2352 | 1248613.5916 | 2680092.5866 | 1248615.0689 | 2680101.7693 | 1248630.4681
4 | 2680090.2352 | 1248613.5916 | 2680095.6476 | 1248610.418 | 2680102.506 | 1248606.4188
5 | 2679986.0872 | 1248681.1909 | 2679986.9837 | 1248682.4706 | 2680002.3126 | 1248706.6284 | 2680014.7656 | 1248726.1997 | 2680018.1429 | 1248728.3135
6 | 2680115.3915 | 1248653.3123 | 2680101.7693 | 1248630.4681
7 | 2680102.506 | 1248606.4188 | 2680103.98 | 1248602.4024 | 2680107.4779 | 1248600.0702
8 | 2680102.506 | 1248606.4188 | 2680103.1448 | 1248611.6757 | 2680114.5388 | 1248630.8103 | 2680117.0605 | 1248635.0451
9 | 2680070.0067 | 1248694.3887 | 2680046.5283 | 1248708.8935 | 2680024.7348 | 1248723.3432 | 2680018.1429 | 1248728.3135
10 | 2680107.4779 | 1248600.0702 | 2680113.298 | 1248596.1837
11 | 2680117.0605 | 1248635.0451 | 2680124.4208 | 1248647.4058
12 | 2680138.5818 | 1248671.187 | 2680131.85 | 1248659.8819
13 | 2680158.063 | 1248660.7872 | 2680138.5818 | 1248671.187
14 | 2680131.85 | 1248659.8819 | 2680124.4208 | 1248647.4058
15 | 2680158.063 | 1248660.7872 | 2680156.8721 | 1248657.8245 | 2680160.7417 | 1248652.5729 | 2680160.0202 | 1248651.523
16 | 2680130.066 | 1248584.9866 | 2680148.8772 | 1248568.8624 | 2680161.122 | 1248557.4751 | 2680175.7606 | 1248547.7881 | 2680200.9051 | 1248531.3383
17 | 2680130.066 | 1248584.9866 | 2680113.298 | 1248596.1837
18 | 2680200.9051 | 1248531.3383 | 2680216.4664 | 1248550.007
19 | 2680200.9051 | 1248531.3383 | 2680230.1865 | 1248512.0049
20 | 2680216.4664 | 1248550.007 | 2680217.8767 | 1248551.6897
21 | 2680216.4664 | 1248550.007 | 2680199.0551 | 1248564.2533
22 | 2680143.7135 | 1248627.7938 | 2680160.0202 | 1248651.523
23 | 2680192.5638 | 1248569.5646 | 2680199.0551 | 1248564.2533
24 | 2680192.5638 | 1248569.5646 | 2680180.9052 | 1248579.0438
25 | 2680169.144 | 1248588.6063 | 2680180.9052 | 1248579.0438
26 | 2680192.5638 | 1248569.5646 | 2680209.8673 | 1248589.5945
27 | 2680234.0463 | 1248617.5832 | 2680209.8673 | 1248589.5945
28 | 2680234.0463 | 1248617.5832 | 2680210.4453 | 1248637.0425
29 | 2680197.9434 | 1248652.5093 | 2680195.1577 | 1248649.6473 | 2680210.4453 | 1248637.0425
30 | 2680197.9434 | 1248652.5093 | 2680211.8587 | 1248668.3424 | 2680217.9151 | 1248670.0367 | 2680225.6801 | 1248664.8935

## bus_geodata
| x | y | coords
0 | 2680082.5605 | 1248614.4142
1 | 2680056.6206 | 1248631.0329
2 | 2680090.2352 | 1248613.5916
3 | 2679986.0872 | 1248681.1909
4 | 2680101.7693 | 1248630.4681
5 | 2680102.506 | 1248606.4188
6 | 2680018.1429 | 1248728.3135
7 | 2680115.3915 | 1248653.3123
8 | 2680107.4779 | 1248600.0702
9 | 2680117.0605 | 1248635.0451
10 | 2680138.5818 | 1248671.187
11 | 2680131.85 | 1248659.8819
12 | 2680158.063 | 1248660.7872
13 | 2680130.066 | 1248584.9866
14 | 2680200.9051 | 1248531.3383
15 | 2680113.298 | 1248596.1837
16 | 2680216.4664 | 1248550.007
17 | 2680230.1865 | 1248512.0049
18 | 2680070.0067 | 1248694.3887
19 | 2680124.4208 | 1248647.4058
20 | 2680160.0202 | 1248651.523
21 | 2680143.7135 | 1248627.7938
22 | 2680217.8767 | 1248551.6897
23 | 2680199.0551 | 1248564.2533
24 | 2680180.9052 | 1248579.0438
25 | 2680192.5638 | 1248569.5646
26 | 2680169.144 | 1248588.6063
27 | 2680209.8673 | 1248589.5945
28 | 2680234.0463 | 1248617.5832
29 | 2680210.4453 | 1248637.0425
30 | 2680225.6801 | 1248664.8935
31 | 2680197.9434 | 1248652.5093
32 | 2680192.5638 | 1248569.5646

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98121 | -0.36186 | 0.0127 | 0.003183
1 | 0.9809 | -0.36802 | 0.0077852 | 0.0019512
2 | 0.98138 | -0.35849 | 0 | 0
3 | 0.98064 | -0.37304 | 0 | 0
4 | 0.98103 | -0.36549 | 0.0075446 | 0.0018909
5 | 0.98194 | -0.34759 | 0 | 0
6 | 0.98047 | -0.37637 | 0 | 0
7 | 0.98075 | -0.37086 | 0.011139 | 0.0027918
8 | 0.98246 | -0.3375 | 0 | 0
9 | 0.98123 | -0.36143 | 0.0045355 | 0.0011367
10 | 0.98065 | -0.37294 | 0 | 0
11 | 0.98078 | -0.3704 | 0.004598 | 0.0011524
12 | 0.98043 | -0.37721 | 0 | 0
13 | 0.98436 | -0.30029 | 0 | 0
14 | 0.99091 | -0.17367 | 0 | 0
15 | 0.98288 | -0.32917 | 0.013611 | 0.0034113
16 | 0.99367 | -0.12083 | 0 | 0
17 | 0.98952 | -0.20077 | 0.043444 | 0.010888
18 | 0.98029 | -0.37996 | 0.003197 | 0.00080123
19 | 0.98098 | -0.36638 | 0.0037263 | 0.0009339
20 | 0.98032 | -0.37934 | 0.00609 | 0.0015263
21 | 0.9802 | -0.38173 | 0.0045861 | 0.0011494
22 | 0.99366 | -0.12103 | 0.0052865 | 0.0013249
23 | 0.99633 | -0.070026 | 0.049748 | 0.012468
24 | 0.99836 | -0.031151 | 0.059248 | 0.014849
25 | 0.99701 | -0.056927 | 0 | 0
26 | 1 | 0 | -0.35813 | -0.090639
27 | 0.9942 | -0.11086 | 0.03221 | 0.0080725
28 | 0.99135 | -0.16559 | 0 | 0
29 | 0.98899 | -0.21109 | 0.017058 | 0.0042751
30 | 0.98529 | -0.28316 | 0.066611 | 0.016694
31 | 0.98754 | -0.23939 | 0 | 0
32 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.010987 | 0.0027526 | -0.010984 | -0.002751 | 3.2254e-06 | 1.673e-06 | 0.016662 | 0.016662 | 0.016662 | 0.98121 | -0.36186 | 0.9809 | -0.36802 | 4.5775
1 | -0.023687 | -0.0059356 | 0.023691 | 0.005938 | 3.8038e-06 | 2.3351e-06 | 0.035922 | 0.035922 | 0.035922 | 0.98121 | -0.36186 | 0.98138 | -0.35849 | 9.8687
2 | 0.0031988 | 0.0007998 | -0.003198 | -0.0008004 | 7.6419e-07 | -6.0327e-07 | 0.0048519 | 0.0048522 | 0.0048522 | 0.9809 | -0.36802 | 0.98064 | -0.37304 | 1.333
3 | 0.018693 | 0.0046879 | -0.018687 | -0.0046841 | 6.2382e-06 | 3.7309e-06 | 0.028344 | 0.028344 | 0.028344 | 0.98138 | -0.35849 | 0.98103 | -0.36549 | 7.7869
4 | -0.042384 | -0.010626 | 0.042406 | 0.01064 | 2.2014e-05 | 1.3909e-05 | 0.064266 | 0.064266 | 0.064266 | 0.98138 | -0.35849 | 0.98194 | -0.34759 | 17.6555
5 | 0.003198 | 0.0008004 | -0.0031975 | -0.0008008 | 5.0596e-07 | -3.9901e-07 | 0.0048522 | 0.0048525 | 0.0048525 | 0.98064 | -0.37304 | 0.98047 | -0.37637 | 1.3331
6 | 0.011142 | 0.0027933 | -0.011139 | -0.0027918 | 2.8489e-06 | 1.4876e-06 | 0.016901 | 0.016901 | 0.016901 | 0.98103 | -0.36549 | 0.98075 | -0.37086 | 4.6431
7 | -0.06597 | -0.016555 | 0.066002 | 0.016575 | 3.176e-05 | 2.0219e-05 | 0.099978 | 0.099978 | 0.099978 | 0.98194 | -0.34759 | 0.98246 | -0.3375 | 27.4664
8 | 0.023564 | 0.0059149 | -0.023548 | -0.0059053 | 1.554e-05 | 9.5351e-06 | 0.035712 | 0.035712 | 0.035712 | 0.98194 | -0.34759 | 0.98123 | -0.36143 | 9.8109
9 | 0.0031975 | 0.0008008 | -0.003197 | -0.00080123 | 5.4642e-07 | -4.3055e-07 | 0.0048525 | 0.0048528 | 0.0048528 | 0.98047 | -0.37637 | 0.98029 | -0.37996 | 1.3332
10 | -0.066002 | -0.016575 | 0.066028 | 0.016592 | 2.6233e-05 | 1.67e-05 | 0.099978 | 0.099978 | 0.099978 | 0.98246 | -0.3375 | 0.98288 | -0.32917 | 27.4664
11 | 0.019013 | 0.0047686 | -0.019008 | -0.0047659 | 4.4852e-06 | 2.6889e-06 | 0.028834 | 0.028834 | 0.028834 | 0.98123 | -0.36143 | 0.98098 | -0.36638 | 7.9214
12 | -0.01068 | -0.0026773 | 0.010681 | 0.002678 | 1.2958e-06 | 6.633e-07 | 0.016206 | 0.016206 | 0.016206 | 0.98065 | -0.37294 | 0.98078 | -0.3704 | 4.4521
13 | 0.01068 | 0.0026773 | -0.010678 | -0.0026762 | 2.17e-06 | 1.1109e-06 | 0.016206 | 0.016206 | 0.016206 | 0.98065 | -0.37294 | 0.98043 | -0.37721 | 4.4521
14 | -0.015279 | -0.0038304 | 0.015282 | 0.003832 | 2.9262e-06 | 1.6895e-06 | 0.023182 | 0.023182 | 0.023182 | 0.98078 | -0.3704 | 0.98098 | -0.36638 | 6.3686
15 | 0.010678 | 0.0026762 | -0.010677 | -0.0026756 | 1.0824e-06 | 5.5415e-07 | 0.016206 | 0.016206 | 0.016206 | 0.98043 | -0.37721 | 0.98032 | -0.37934 | 4.4522
16 | -0.07975 | -0.020073 | 0.080235 | 0.020383 | 0.00048583 | 0.00030979 | 0.12058 | 0.12058 | 0.12058 | 0.98436 | -0.30029 | 0.99091 | -0.17367 | 33.1275
17 | 0.07975 | 0.020073 | -0.07964 | -0.020003 | 0.00010994 | 7.0107e-05 | 0.12058 | 0.12058 | 0.12058 | 0.98436 | -0.30029 | 0.98288 | -0.32917 | 33.1276
18 | -0.12374 | -0.031306 | 0.12405 | 0.031507 | 0.00031464 | 0.00020106 | 0.18591 | 0.18591 | 0.18591 | 0.99091 | -0.17367 | 0.99367 | -0.12083 | 51.0753
19 | 0.0435 | 0.010924 | -0.043444 | -0.010888 | 5.6159e-05 | 3.5491e-05 | 0.06533 | 0.06533 | 0.06533 | 0.99091 | -0.17367 | 0.98952 | -0.20077 | 17.9479
20 | 0.0052865 | 0.0013249 | -0.0052865 | -0.0013249 | 5.16e-08 | 4.5838e-09 | 0.0079166 | 0.0079166 | 0.0079166 | 0.99367 | -0.12083 | 0.99366 | -0.12103 | 2.1749
21 | -0.12934 | -0.032832 | 0.12965 | 0.033035 | 0.00031695 | 0.00020256 | 0.19383 | 0.19383 | 0.19383 | 0.99367 | -0.12083 | 0.99633 | -0.070026 | 53.2501
22 | 0.0045866 | 0.0011494 | -0.0045861 | -0.0011494 | 5.2332e-07 | -2.8039e-08 | 0.0069619 | 0.006962 | 0.006962 | 0.98032 | -0.37934 | 0.9802 | -0.38173 | 1.9126
23 | -0.1794 | -0.045503 | 0.17951 | 0.045575 | 0.00011306 | 7.2141e-05 | 0.26813 | 0.26813 | 0.26813 | 0.99633 | -0.070026 | 0.99701 | -0.056927 | 36.8309
24 | 0.2967 | 0.075449 | -0.29633 | -0.075214 | 0.00036794 | 0.00023489 | 0.4426 | 0.4426 | 0.4426 | 0.99836 | -0.031151 | 0.99701 | -0.056927 | 40.5311
25 | -0.35595 | -0.090298 | 0.35648 | 0.090639 | 0.00053406 | 0.0003412 | 0.53091 | 0.53091 | 0.53091 | 0.99836 | -0.031151 | 1 | 0 | 48.6178
26 | 0.11681 | 0.029639 | -0.11651 | -0.029446 | 0.00030215 | 0.00019303 | 0.17447 | 0.17447 | 0.17447 | 0.99701 | -0.056927 | 0.9942 | -0.11086 | 47.9316
27 | 0.084303 | 0.021373 | -0.084082 | -0.021232 | 0.00022112 | 0.00014104 | 0.12626 | 0.12626 | 0.12626 | 0.9942 | -0.11086 | 0.99135 | -0.16559 | 34.6877
28 | 0.084082 | 0.021232 | -0.083899 | -0.021116 | 0.00018287 | 0.00011664 | 0.12626 | 0.12626 | 0.12626 | 0.99135 | -0.16559 | 0.98899 | -0.21109 | 34.6877
29 | 0.066841 | 0.016841 | -0.066751 | -0.016783 | 9.0351e-05 | 5.752e-05 | 0.1006 | 0.1006 | 0.1006 | 0.98899 | -0.21109 | 0.98754 | -0.23939 | 27.637
30 | -0.066611 | -0.016694 | 0.066751 | 0.016783 | 0.00013921 | 8.8625e-05 | 0.1006 | 0.1006 | 0.1006 | 0.98529 | -0.28316 | 0.98754 | -0.23939 | 27.637

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.42091 | 0.10637

## res_load
| p_mw | q_mvar
0 | 0.0127 | 0.003183
1 | 0.0077852 | 0.0019512
2 | 0.0075446 | 0.0018909
3 | 0.011139 | 0.0027918
4 | 0.0045355 | 0.0011367
5 | 0.004598 | 0.0011524
6 | 0.013611 | 0.0034113
7 | 0.043444 | 0.010888
8 | 0.003197 | 0.00080123
9 | 0.0037263 | 0.0009339
10 | 0.00609 | 0.0015263
11 | 0.0045861 | 0.0011494
12 | 0.0052865 | 0.0013249
13 | 0.049748 | 0.012468
14 | 0.059248 | 0.014849
15 | 0.062778 | 0.015734
16 | 0.03221 | 0.0080725
17 | 0.017058 | 0.0042751
18 | 0.066611 | 0.016694

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1