## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-600_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-600_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-600_0_4_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_261-600_0_4_node_18 | 0.4 | n |  | TRUE
4 | bus_LV_261-600_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_261-600_0_4_node_21 | 0.4 | n |  | TRUE
6 | bus_LV_261-600_0_4_node_5 | 0.4 | n |  | TRUE
7 | bus_LV_261-600_0_4_node_45 | 0.4 | n |  | TRUE
8 | bus_LV_261-600_0_4_node_55 | 0.4 | n |  | TRUE
9 | bus_LV_261-600_0_4_node_54 | 0.4 | n |  | TRUE
10 | bus_LV_261-600_0_4_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_261-600_0_4_node_8 | 0.4 | n |  | TRUE
12 | bus_LV_261-600_0_4_node_56 | 0.4 | n |  | TRUE
13 | bus_LV_261-600_0_4_node_22 | 0.4 | n |  | TRUE
14 | bus_LV_261-600_0_4_node_57 | 0.4 | n |  | TRUE
15 | bus_LV_261-600_0_4_node_11 | 0.4 | n |  | TRUE
16 | bus_LV_261-600_0_4_node_44 | 0.4 | n |  | TRUE
17 | bus_LV_261-600_0_4_node_12 | 0.4 | n |  | TRUE
18 | bus_LV_261-600_0_4_node_40 | 0.4 | n |  | TRUE
19 | bus_LV_261-600_0_4_node_41 | 0.4 | n |  | TRUE
20 | bus_LV_261-600_0_4_node_39 | 0.4 | n |  | TRUE
21 | bus_LV_261-600_0_4_node_13 | 0.4 | n |  | TRUE
22 | bus_LV_261-600_0_4_node_27 | 0.4 | n |  | TRUE
23 | bus_LV_261-600_0_4_node_38 | 0.4 | n |  | TRUE
24 | bus_LV_261-600_0_4_node_14 | 0.4 | n |  | TRUE
25 | bus_LV_261-600_0_4_node_20 | 0.4 | n |  | TRUE
26 | bus_LV_261-600_0_4_node_35 | 0.4 | n |  | TRUE
27 | bus_LV_261-600_0_4_node_16 | 0.4 | n |  | TRUE
28 | bus_LV_261-600_0_4_node_19 | 0.4 | n |  | TRUE
29 | bus_LV_261-600_0_4_node_42 | 0.4 | n |  | TRUE
30 | bus_LV_261-600_0_4_node_17 | 0.4 | n |  | TRUE
31 | bus_LV_261-600_0_4_node_28 | 0.4 | n |  | TRUE
32 | bus_LV_261-600_0_4_node_43 | 0.4 | n |  | TRUE
33 | bus_LV_261-600_0_4_node_53 | 0.4 | n |  | TRUE
34 | bus_LV_261-600_0_4_node_33 | 0.4 | n |  | TRUE
35 | bus_LV_261-600_0_4_node_23 | 0.4 | n |  | TRUE
36 | bus_LV_261-600_0_4_node_36 | 0.4 | n |  | TRUE
37 | bus_LV_261-600_0_4_node_34 | 0.4 | n |  | TRUE
38 | bus_LV_261-600_0_4_node_49 | 0.4 | n |  | TRUE
39 | bus_LV_261-600_0_4_node_47 | 0.4 | n |  | TRUE
40 | bus_LV_261-600_0_4_node_46 | 0.4 | n |  | TRUE
41 | bus_LV_261-600_0_4_node_37 | 0.4 | n |  | TRUE
42 | bus_LV_261-600_0_4_node_24 | 0.4 | n |  | TRUE
43 | bus_LV_261-600_0_4_node_25 | 0.4 | n |  | TRUE
44 | bus_LV_261-600_0_4_node_52 | 0.4 | n |  | TRUE
45 | bus_LV_261-600_0_4_node_51 | 0.4 | n |  | TRUE
46 | bus_LV_261-600_0_4_node_26 | 0.4 | n |  | TRUE
47 | bus_LV_261-600_0_4_node_50 | 0.4 | n |  | TRUE
48 | bus_LV_261-600_0_4_node_48 | 0.4 | n |  | TRUE
49 | bus_MV_533_0_node_107 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-600_0_4_load_0 | 0 | 0.013591 | 0.0034062 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-600_0_4_load_1 | 1 | 0.0034245 | 0.00085827 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-600_0_4_load_3 | 2 | 0.010206 | 0.0025578 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-600_0_4_load_45 | 7 | 0.012541 | 0.0031432 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-600_0_4_load_55 | 8 | 0.021802 | 0.0054641 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-600_0_4_load_54 | 9 | 0.023748 | 0.0059519 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-600_0_4_load_56 | 12 | 0.048391 | 0.012128 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-600_0_4_load_57 | 14 | 0.0096225 | 0.0024116 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-600_0_4_load_44 | 16 | 0.015694 | 0.0039333 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-600_0_4_load_40 | 18 | 0.031857 | 0.007984 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-600_0_4_load_41 | 19 | 0.022352 | 0.0056019 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-600_0_4_load_39 | 20 | 0.0089226 | 0.0022362 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-600_0_4_load_38 | 23 | 0.025892 | 0.0064891 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-600_0_4_load_35 | 26 | 0.006708 | 0.0016812 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-600_0_4_load_42 | 29 | 0.008056 | 0.002019 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-600_0_4_load_43 | 32 | 0.018777 | 0.004706 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-600_0_4_load_53 | 33 | 0.007763 | 0.0019456 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_261-600_0_4_load_33 | 34 | 0.010296 | 0.0025803 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_261-600_0_4_load_36 | 36 | 0.01218 | 0.0030526 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_261-600_0_4_load_34 | 37 | 0.010355 | 0.0025951 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_261-600_0_4_load_49 | 38 | 0.0079989 | 0.0020047 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_261-600_0_4_load_47 | 39 | 0.009127 | 0.0022874 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_261-600_0_4_load_46 | 40 | 0.015368 | 0.0038515 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_261-600_0_4_load_37 | 41 | 0.012768 | 0.0032 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_261-600_0_4_load_24 | 42 | 0.011934 | 0.0029909 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_261-600_0_4_load_25 | 43 | 0.0029382 | 0.00073638 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_261-600_0_4_load_52 | 44 | 0.0035457 | 0.00088864 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_261-600_0_4_load_51 | 45 | 0.010385 | 0.0026028 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_261-600_0_4_load_26 | 46 | 0.009905 | 0.0024824 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_261-600_0_4_load_50 | 47 | 0.0080903 | 0.0020276 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_261-600_0_4_load_48 | 48 | 0.011737 | 0.0029415 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 15 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-600_0_4_line_0 |  | 0 | 1 | 0.012736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-600_0_4_line_1 |  | 1 | 2 | 0.012348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-600_0_4_line_2 |  | 2 | 3 | 0.012213 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-600_0_4_line_3 |  | 3 | 25 | 0.020053 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-600_0_4_line_4 |  | 4 | 5 | 0.003113 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_261-600_0_4_line_5 |  | 4 | 6 | 0.01102 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_261-600_0_4_line_6 |  | 4 | 7 | 0.017277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_261-600_0_4_line_7 |  | 5 | 13 | 0.010671 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_261-600_0_4_line_8 |  | 5 | 33 | 0.008168 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_261-600_0_4_line_9 |  | 6 | 8 | 0.012606 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
10 | LV_261-600_0_4_line_10 |  | 6 | 9 | 0.026627 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_261-600_0_4_line_11 |  | 8 | 19 | 0.016022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
12 | LV_261-600_0_4_line_12 |  | 10 | 11 | 0.009317 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-600_0_4_line_13 |  | 10 | 12 | 0.019081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_261-600_0_4_line_14 |  | 11 | 13 | 0.003355 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_261-600_0_4_line_15 |  | 11 | 14 | 0.025592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_261-600_0_4_line_16 |  | 13 | 34 | 0.0069752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_261-600_0_4_line_17 |  | 15 | 16 | 0.0098366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_261-600_0_4_line_18 |  | 15 | 17 | 0.011061 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
19 | LV_261-600_0_4_line_19 |  | 16 | 40 | 0.0048688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_261-600_0_4_line_20 |  | 17 | 18 | 0.020417 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_261-600_0_4_line_21 |  | 17 | 19 | 0.013155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
22 | LV_261-600_0_4_line_22 |  | 17 | 20 | 0.022313 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_261-600_0_4_line_23 |  | 18 | 30 | 0.013608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_261-600_0_4_line_24 |  | 21 | 22 | 0.011019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_261-600_0_4_line_25 |  | 21 | 23 | 0.0098335 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_261-600_0_4_line_26 |  | 22 | 31 | 0.004878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_261-600_0_4_line_27 |  | 22 | 38 | 0.013729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_261-600_0_4_line_28 |  | 23 | 41 | 0.020302 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_261-600_0_4_line_29 |  | 24 | 25 | 0.017653 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_261-600_0_4_line_30 |  | 24 | 26 | 0.018083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_261-600_0_4_line_31 |  | 26 | 37 | 0.009697 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_261-600_0_4_line_32 |  | 27 | 28 | 0.003837 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_261-600_0_4_line_33 |  | 27 | 29 | 0.018459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_261-600_0_4_line_34 |  | 28 | 32 | 0.00995 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_261-600_0_4_line_35 |  | 28 | 30 | 0.013648 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_261-600_0_4_line_36 |  | 30 | 31 | 0.01154 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_261-600_0_4_line_37 |  | 31 | 39 | 0.0066533 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_261-600_0_4_line_38 |  | 33 | 45 | 0.018579 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_261-600_0_4_line_39 |  | 34 | 46 | 0.01587 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_261-600_0_4_line_40 |  | 35 | 36 | 0.01951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_261-600_0_4_line_41 |  | 35 | 37 | 0.010602 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_261-600_0_4_line_42 |  | 36 | 40 | 0.013473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_261-600_0_4_line_43 |  | 38 | 47 | 0.01079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_261-600_0_4_line_44 |  | 39 | 48 | 0.014548 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_261-600_0_4_line_45 |  | 42 | 43 | 0.018588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_261-600_0_4_line_46 |  | 43 | 46 | 0.0029422 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_261-600_0_4_line_47 |  | 44 | 45 | 0.015277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-600_0_4_trafo_11 | 0.63 MVA 20/0.4 kV | 49 | 15 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2681784.3474 | 1247266.992 | 2681776.0511 | 1247276.6557
1 | 2681768.0081 | 1247286.0244 | 2681776.0511 | 1247276.6557
2 | 2681760.053 | 1247295.2907 | 2681768.0081 | 1247286.0244
3 | 2681752.8103 | 1247303.4079 | 2681756.863 | 1247305.8656 | 2681759.9268 | 1247302.2496 | 2681763.888 | 1247297.6453 | 2681760.053 | 1247295.2907
4 | 2681699.8432 | 1247270.0203 | 2681697.2305 | 1247268.3164
5 | 2681688.0151 | 1247262.2739 | 2681692.3721 | 1247265.1249 | 2681697.2305 | 1247268.3164
6 | 2681697.2305 | 1247268.3164 | 2681685.9342 | 1247281.3887
7 | 2681699.8432 | 1247270.0203 | 2681702.0377 | 1247266.4479 | 2681705.4224 | 1247260.9238
8 | 2681699.8432 | 1247270.0203 | 2681706.7489 | 1247274.3824
9 | 2681688.0151 | 1247262.2739 | 2681679.82 | 1247271.8527
10 | 2681688.0151 | 1247262.2739 | 2681684.5041 | 1247259.9683 | 2681665.803 | 1247247.5899
11 | 2681679.82 | 1247271.8527 | 2681669.4043 | 1247284.0272
12 | 2681694.5751 | 1247254.3585 | 2681698.1859 | 1247256.5431 | 2681702.5458 | 1247259.1829
13 | 2681694.5751 | 1247254.3585 | 2681691.5486 | 1247252.5265 | 2681679.1862 | 1247243.1048
14 | 2681705.4224 | 1247260.9238 | 2681702.5458 | 1247259.1829
15 | 2681702.5458 | 1247259.1829 | 2681715.3747 | 1247237.0386
16 | 2681705.4224 | 1247260.9238 | 2681711.3261 | 1247264.6387
17 | 2681670.7477 | 1247298.963 | 2681679.628 | 1247303.1936
18 | 2681660.8524 | 1247294.0231 | 2681665.5853 | 1247296.4567 | 2681670.7477 | 1247298.963
19 | 2681679.628 | 1247303.1936 | 2681684.0235 | 1247305.2877
20 | 2681660.8524 | 1247294.0231 | 2681656.3842 | 1247299.2432 | 2681652.4624 | 1247300.4456 | 2681646.3353 | 1247307.6313
21 | 2681660.8524 | 1247294.0231 | 2681669.4043 | 1247284.0272
22 | 2681660.8524 | 1247294.0231 | 2681658.4373 | 1247292.7778 | 2681640.9932 | 1247283.8508
23 | 2681637.5062 | 1247317.9859 | 2681646.3353 | 1247307.6313
24 | 2681630.1511 | 1247329.8934 | 2681634.2621 | 1247333.0523 | 2681638.8888 | 1247336.6074
25 | 2681638.8888 | 1247336.6074 | 2681637.6899 | 1247337.5472 | 2681632.3048 | 1247343.8765
26 | 2681629.5121 | 1247325.2812 | 2681630.2798 | 1247326.5816 | 2681630.5254 | 1247327.9415 | 2681630.1511 | 1247329.8934
27 | 2681630.1511 | 1247329.8934 | 2681628.9882 | 1247331.5119 | 2681621.3574 | 1247340.4291
28 | 2681632.3048 | 1247343.8765 | 2681619.1493 | 1247359.3388
29 | 2681741.362 | 1247316.8711 | 2681752.8103 | 1247303.4079
30 | 2681741.362 | 1247316.8711 | 2681732.2411 | 1247312.2087 | 2681730.2148 | 1247312.8923 | 2681725.1801 | 1247310.2182
31 | 2681725.1801 | 1247310.2182 | 2681721.0588 | 1247308.0293 | 2681718.4015 | 1247312.3006
32 | 2681649.7391 | 1247329.7963 | 2681648.6275 | 1247328.2354 | 2681648.2986 | 1247326.3406
33 | 2681649.7391 | 1247329.7963 | 2681663.9011 | 1247341.6353
34 | 2681648.2986 | 1247326.3406 | 2681648.5657 | 1247325.0433 | 2681649.2085 | 1247323.8957 | 2681653.9874 | 1247318.3639
35 | 2681637.5062 | 1247317.9859 | 2681643.3059 | 1247322.4801 | 2681648.2986 | 1247326.3406
36 | 2681629.5121 | 1247325.2812 | 2681631.7727 | 1247322.388 | 2681635.1405 | 1247318.0867 | 2681636.3166 | 1247318.2475 | 2681637.5062 | 1247317.9859
37 | 2681629.5121 | 1247325.2812 | 2681628.6709 | 1247324.3801 | 2681624.523 | 1247320.8905
38 | 2681722.4568 | 1247284.3048 | 2681706.7489 | 1247274.3824
39 | 2681711.3261 | 1247264.6387 | 2681724.7581 | 1247273.091
40 | 2681712.8009 | 1247321.303 | 2681696.8256 | 1247311.3868 | 2681696.1867 | 1247311.0824
41 | 2681712.8009 | 1247321.303 | 2681718.4015 | 1247312.3006
42 | 2681696.1867 | 1247311.0824 | 2681684.0235 | 1247305.2877
43 | 2681621.3574 | 1247340.4291 | 2681614.3419 | 1247348.6275
44 | 2681624.523 | 1247320.8905 | 2681613.3908 | 1247311.525
45 | 2681742.9807 | 1247284.5577 | 2681727.2483 | 1247274.658
46 | 2681724.7581 | 1247273.091 | 2681727.2483 | 1247274.658
47 | 2681722.4568 | 1247284.3048 | 2681735.3725 | 1247292.4634

## bus_geodata
| x | y | coords
0 | 2681784.3474 | 1247266.992
1 | 2681776.0511 | 1247276.6557
2 | 2681768.0081 | 1247286.0244
3 | 2681760.053 | 1247295.2907
4 | 2681697.2305 | 1247268.3164
5 | 2681699.8432 | 1247270.0203
6 | 2681688.0151 | 1247262.2739
7 | 2681685.9342 | 1247281.3887
8 | 2681679.82 | 1247271.8527
9 | 2681665.803 | 1247247.5899
10 | 2681694.5751 | 1247254.3585
11 | 2681702.5458 | 1247259.1829
12 | 2681679.1862 | 1247243.1048
13 | 2681705.4224 | 1247260.9238
14 | 2681715.3747 | 1247237.0386
15 | 2681670.7477 | 1247298.963
16 | 2681679.628 | 1247303.1936
17 | 2681660.8524 | 1247294.0231
18 | 2681646.3353 | 1247307.6313
19 | 2681669.4043 | 1247284.0272
20 | 2681640.9932 | 1247283.8508
21 | 2681638.8888 | 1247336.6074
22 | 2681630.1511 | 1247329.8934
23 | 2681632.3048 | 1247343.8765
24 | 2681741.362 | 1247316.8711
25 | 2681752.8103 | 1247303.4079
26 | 2681725.1801 | 1247310.2182
27 | 2681649.7391 | 1247329.7963
28 | 2681648.2986 | 1247326.3406
29 | 2681663.9011 | 1247341.6353
30 | 2681637.5062 | 1247317.9859
31 | 2681629.5121 | 1247325.2812
32 | 2681653.9874 | 1247318.3639
33 | 2681706.7489 | 1247274.3824
34 | 2681711.3261 | 1247264.6387
35 | 2681712.8009 | 1247321.303
36 | 2681696.1867 | 1247311.0824
37 | 2681718.4015 | 1247312.3006
38 | 2681621.3574 | 1247340.4291
39 | 2681624.523 | 1247320.8905
40 | 2681684.0235 | 1247305.2877
41 | 2681619.1493 | 1247359.3388
42 | 2681742.9807 | 1247284.5577
43 | 2681727.2483 | 1247274.658
44 | 2681735.3724 | 1247292.4634
45 | 2681722.4568 | 1247284.3048
46 | 2681724.7581 | 1247273.091
47 | 2681614.3419 | 1247348.6275
48 | 2681613.3908 | 1247311.525
49 | 2681665.5853 | 1247296.4567

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99466 | -0.10284 | 0.013591 | 0.0034062
1 | 0.99481 | -0.099788 | 0.0034245 | 0.00085827
2 | 0.99501 | -0.096088 | 0.010206 | 0.0025578
3 | 0.99531 | -0.090237 | 0 | 0
4 | 0.99509 | -0.094279 | 0 | 0
5 | 0.99476 | -0.10057 | 0 | 0
6 | 0.99637 | -0.069613 | 0 | 0
7 | 0.99489 | -0.098094 | 0.012541 | 0.0031432
8 | 0.99724 | -0.05291 | 0.021802 | 0.0054641
9 | 0.99579 | -0.080722 | 0.023748 | 0.0059519
10 | 0.99327 | -0.12948 | 0 | 0
11 | 0.99368 | -0.12152 | 0 | 0
12 | 0.99242 | -0.14581 | 0.048391 | 0.012128
13 | 0.99386 | -0.11808 | 0 | 0
14 | 0.99345 | -0.12587 | 0.0096225 | 0.0024116
15 | 1 | 0 | -0.42952 | -0.10796
16 | 0.99922 | -0.015019 | 0.015694 | 0.0039333
17 | 0.99886 | -0.021774 | 0 | 0
18 | 0.99636 | -0.069797 | 0.031857 | 0.007984
19 | 0.99808 | -0.036741 | 0.022352 | 0.0056019
20 | 0.99868 | -0.025253 | 0.0089226 | 0.0022362
21 | 0.99366 | -0.1219 | 0 | 0
22 | 0.99405 | -0.11439 | 0 | 0
23 | 0.99331 | -0.12862 | 0.025892 | 0.0064891
24 | 0.99624 | -0.072194 | 0 | 0
25 | 0.99581 | -0.080637 | 0 | 0
26 | 0.99669 | -0.063553 | 0.006708 | 0.0016812
27 | 0.99473 | -0.1013 | 0 | 0
28 | 0.99476 | -0.10075 | 0 | 0
29 | 0.99459 | -0.10392 | 0.008056 | 0.002019
30 | 0.99509 | -0.094305 | 0 | 0
31 | 0.99429 | -0.10968 | 0 | 0
32 | 0.99459 | -0.10405 | 0.018777 | 0.004706
33 | 0.9946 | -0.10369 | 0.007763 | 0.0019456
34 | 0.99363 | -0.1224 | 0.010296 | 0.0025803
35 | 0.99742 | -0.049551 | 0 | 0
36 | 0.99821 | -0.034425 | 0.01218 | 0.0030526
37 | 0.99699 | -0.057781 | 0.010355 | 0.0025951
38 | 0.99385 | -0.11828 | 0.0079989 | 0.0020047
39 | 0.99417 | -0.11212 | 0.009127 | 0.0022874
40 | 0.9989 | -0.021126 | 0.015368 | 0.0038515
41 | 0.99308 | -0.1332 | 0.012768 | 0.0032
42 | 0.99303 | -0.13404 | 0.011934 | 0.0029909
43 | 0.99323 | -0.13012 | 0.0029382 | 0.00073638
44 | 0.99432 | -0.10921 | 0.0035457 | 0.00088864
45 | 0.99437 | -0.10825 | 0.010385 | 0.0026028
46 | 0.99327 | -0.12935 | 0.009905 | 0.0024824
47 | 0.99377 | -0.11982 | 0.0080903 | 0.0020276
48 | 0.99401 | -0.11514 | 0.011737 | 0.0029415
49 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.013591 | -0.0034062 | 0.013593 | 0.0034073 | 1.9744e-06 | 1.0983e-06 | 0.020332 | 0.020332 | 0.020332 | 0.99466 | -0.10284 | 0.99481 | -0.099788 | 5.5858
1 | -0.017017 | -0.0042656 | 0.01702 | 0.0042673 | 3.0002e-06 | 1.7597e-06 | 0.025455 | 0.025454 | 0.025455 | 0.99481 | -0.099788 | 0.99501 | -0.096088 | 6.993
2 | -0.027226 | -0.0068251 | 0.027234 | 0.0068298 | 7.5926e-06 | 4.7006e-06 | 0.040717 | 0.040717 | 0.040717 | 0.99501 | -0.096088 | 0.99531 | -0.090237 | 11.186
3 | -0.027234 | -0.0068298 | 0.027246 | 0.0068376 | 1.2467e-05 | 7.7181e-06 | 0.040717 | 0.040717 | 0.040717 | 0.99531 | -0.090237 | 0.99581 | -0.080637 | 11.186
4 | 0.11498 | 0.028896 | -0.11495 | -0.028873 | 3.4524e-05 | 2.2055e-05 | 0.17197 | 0.17197 | 0.17197 | 0.99509 | -0.094279 | 0.99476 | -0.10057 | 47.2448
5 | -0.12753 | -0.03204 | 0.12768 | 0.032136 | 0.00015033 | 9.6065e-05 | 0.19073 | 0.19073 | 0.19073 | 0.99509 | -0.094279 | 0.99637 | -0.069613 | 52.398
6 | 0.012544 | 0.0031444 | -0.012541 | -0.0031432 | 2.2796e-06 | 1.2345e-06 | 0.018758 | 0.018758 | 0.018758 | 0.99509 | -0.094279 | 0.99489 | -0.098094 | 5.1532
7 | 0.09325 | 0.023433 | -0.093172 | -0.023383 | 7.7885e-05 | 4.9708e-05 | 0.13951 | 0.13951 | 0.13951 | 0.99476 | -0.10057 | 0.99386 | -0.11808 | 38.3269
8 | 0.0217 | 0.0054406 | -0.021697 | -0.0054386 | 3.2276e-06 | 1.9596e-06 | 0.032461 | 0.032461 | 0.032461 | 0.99476 | -0.10057 | 0.9946 | -0.10369 | 8.9179
9 | -0.15144 | -0.038096 | 0.15156 | 0.038173 | 0.00012096 | 7.7083e-05 | 0.22622 | 0.22622 | 0.22622 | 0.99637 | -0.069613 | 0.99724 | -0.05291 | 31.0735
10 | 0.023761 | 0.0059596 | -0.023748 | -0.0059519 | 1.2574e-05 | 7.7011e-06 | 0.035487 | 0.035487 | 0.035487 | 0.99637 | -0.069613 | 0.99579 | -0.080722 | 9.7492
11 | -0.17336 | -0.043637 | 0.1735 | 0.043722 | 0.00013408 | 8.5186e-05 | 0.25875 | 0.25875 | 0.25875 | 0.99724 | -0.05291 | 0.99808 | -0.036741 | 23.6948
12 | -0.048429 | -0.012152 | 0.048447 | 0.012163 | 1.8393e-05 | 1.1651e-05 | 0.072557 | 0.072556 | 0.072557 | 0.99327 | -0.12948 | 0.99368 | -0.12152 | 19.9331
13 | 0.048429 | 0.012152 | -0.048391 | -0.012128 | 3.7669e-05 | 2.3862e-05 | 0.072557 | 0.072557 | 0.072557 | 0.99327 | -0.12948 | 0.99242 | -0.14581 | 19.9331
14 | -0.058072 | -0.014576 | 0.058081 | 0.014582 | 9.516e-06 | 6.0468e-06 | 0.086969 | 0.086969 | 0.086969 | 0.99368 | -0.12152 | 0.99386 | -0.11808 | 23.8926
15 | 0.0096245 | 0.0024126 | -0.0096225 | -0.0024116 | 1.9936e-06 | 9.4443e-07 | 0.014413 | 0.014413 | 0.014413 | 0.99368 | -0.12152 | 0.99345 | -0.12587 | 3.9596
16 | 0.035091 | 0.0088011 | -0.035084 | -0.0087966 | 7.2208e-06 | 4.5309e-06 | 0.052541 | 0.052541 | 0.052541 | 0.99386 | -0.11808 | 0.99363 | -0.1224 | 14.4343
17 | 0.087751 | 0.022078 | -0.087689 | -0.022038 | 6.2922e-05 | 4.0141e-05 | 0.13061 | 0.13061 | 0.13061 | 1 | 0 | 0.99922 | -0.015019 | 35.8807
18 | 0.34012 | 0.085883 | -0.33976 | -0.085657 | 0.00035444 | 0.00022641 | 0.50632 | 0.50632 | 0.50632 | 1 | 0 | 0.99886 | -0.021774 | 46.3667
19 | 0.071995 | 0.018105 | -0.071974 | -0.018092 | 2.0995e-05 | 1.3373e-05 | 0.10723 | 0.10723 | 0.10723 | 0.99922 | -0.015019 | 0.9989 | -0.021126 | 29.4601
20 | 0.13485 | 0.034007 | -0.13454 | -0.033809 | 0.0003092 | 0.00019762 | 0.20096 | 0.20096 | 0.20096 | 0.99886 | -0.021774 | 0.99636 | -0.069797 | 55.2088
21 | 0.19599 | 0.049413 | -0.19585 | -0.049324 | 0.00014027 | 8.9259e-05 | 0.29207 | 0.29207 | 0.29207 | 0.99886 | -0.021774 | 0.99808 | -0.036741 | 26.7464
22 | 0.0089241 | 0.0022369 | -0.0089226 | -0.0022362 | 1.4789e-06 | 6.5446e-07 | 0.013294 | 0.013294 | 0.013294 | 0.99886 | -0.021774 | 0.99868 | -0.025253 | 3.6523
23 | 0.10268 | 0.025825 | -0.10256 | -0.025748 | 0.00012005 | 7.6658e-05 | 0.15338 | 0.15338 | 0.15338 | 0.99636 | -0.069797 | 0.99509 | -0.094305 | 42.1384
24 | -0.038675 | -0.0096984 | 0.038689 | 0.0097071 | 1.3862e-05 | 8.7287e-06 | 0.057918 | 0.057918 | 0.057918 | 0.99366 | -0.1219 | 0.99405 | -0.11439 | 15.9116
25 | 0.038675 | 0.0096984 | -0.038663 | -0.0096906 | 1.237e-05 | 7.7895e-06 | 0.057918 | 0.057918 | 0.057918 | 0.99366 | -0.1219 | 0.99331 | -0.12862 | 15.9116
26 | -0.054782 | -0.013741 | 0.054794 | 0.013749 | 1.2302e-05 | 7.8103e-06 | 0.082008 | 0.082008 | 0.082008 | 0.99405 | -0.11439 | 0.99429 | -0.10968 | 22.5297
27 | 0.016093 | 0.0040343 | -0.01609 | -0.0040326 | 2.9879e-06 | 1.7343e-06 | 0.02409 | 0.02409 | 0.02409 | 0.99405 | -0.11439 | 0.99385 | -0.11828 | 6.6182
28 | 0.012771 | 0.0032016 | -0.012768 | -0.0032 | 2.7866e-06 | 1.5207e-06 | 0.019132 | 0.019132 | 0.019132 | 0.99331 | -0.12862 | 0.99308 | -0.1332 | 5.256
29 | 0.027257 | 0.0068444 | -0.027246 | -0.0068376 | 1.0975e-05 | 6.7941e-06 | 0.040717 | 0.040717 | 0.040717 | 0.99624 | -0.072194 | 0.99581 | -0.080637 | 11.186
30 | -0.027257 | -0.0068444 | 0.027269 | 0.0068513 | 1.1242e-05 | 6.9593e-06 | 0.040717 | 0.040717 | 0.040717 | 0.99624 | -0.072194 | 0.99669 | -0.063553 | 11.1859
31 | -0.033977 | -0.0085325 | 0.033986 | 0.0085384 | 9.3588e-06 | 5.8632e-06 | 0.050731 | 0.050731 | 0.050731 | 0.99669 | -0.063553 | 0.99699 | -0.057781 | 13.9372
32 | -0.008057 | -0.0020194 | 0.0080572 | 0.0020195 | 2.0901e-07 | 8.3959e-08 | 0.012052 | 0.012052 | 0.012052 | 0.99473 | -0.1013 | 0.99476 | -0.10075 | 3.3111
33 | 0.008057 | 0.0020194 | -0.008056 | -0.002019 | 1.0055e-06 | 4.0395e-07 | 0.012052 | 0.012053 | 0.012053 | 0.99473 | -0.1013 | 0.99459 | -0.10392 | 3.3111
34 | 0.01878 | 0.0047078 | -0.018777 | -0.004706 | 2.9447e-06 | 1.7555e-06 | 0.028093 | 0.028093 | 0.028093 | 0.99476 | -0.10075 | 0.99459 | -0.10405 | 7.7178
35 | -0.026837 | -0.0067273 | 0.026846 | 0.0067324 | 8.2486e-06 | 5.1018e-06 | 0.040145 | 0.040145 | 0.040145 | 0.99476 | -0.10075 | 0.99509 | -0.094305 | 11.0289
36 | 0.075717 | 0.019016 | -0.075662 | -0.018981 | 5.5489e-05 | 3.5363e-05 | 0.11324 | 0.11324 | 0.11324 | 0.99509 | -0.094305 | 0.99429 | -0.10968 | 31.1095
37 | 0.020868 | 0.0052313 | -0.020865 | -0.0052298 | 2.4335e-06 | 1.4711e-06 | 0.03123 | 0.03123 | 0.03123 | 0.99429 | -0.10968 | 0.99417 | -0.11212 | 8.5798
38 | 0.013934 | 0.003493 | -0.013931 | -0.0034914 | 3.028e-06 | 1.6969e-06 | 0.020847 | 0.020847 | 0.020847 | 0.9946 | -0.10369 | 0.99437 | -0.10825 | 5.7273
39 | 0.024788 | 0.0062162 | -0.02478 | -0.0062112 | 8.2014e-06 | 5.0434e-06 | 0.037123 | 0.037123 | 0.037123 | 0.99363 | -0.1224 | 0.99327 | -0.12935 | 10.1985
40 | -0.044358 | -0.011144 | 0.04439 | 0.011165 | 3.205e-05 | 2.0257e-05 | 0.066186 | 0.066186 | 0.066186 | 0.99742 | -0.049551 | 0.99821 | -0.034425 | 18.1829
41 | 0.044358 | 0.011144 | -0.044341 | -0.011133 | 1.7417e-05 | 1.1008e-05 | 0.066186 | 0.066186 | 0.066186 | 0.99742 | -0.049551 | 0.99699 | -0.057781 | 18.1829
42 | -0.05657 | -0.014217 | 0.056606 | 0.01424 | 3.5941e-05 | 2.2826e-05 | 0.084342 | 0.084342 | 0.084342 | 0.99821 | -0.034425 | 0.9989 | -0.021126 | 23.171
43 | 0.0080909 | 0.0020279 | -0.0080903 | -0.0020276 | 5.9379e-07 | 2.4022e-07 | 0.012114 | 0.012114 | 0.012114 | 0.99385 | -0.11828 | 0.99377 | -0.11982 | 3.328
44 | 0.011738 | 0.0029424 | -0.011737 | -0.0029415 | 1.6841e-06 | 8.892e-07 | 0.01757 | 0.01757 | 0.01757 | 0.99417 | -0.11212 | 0.99401 | -0.11514 | 4.8269
45 | -0.011934 | -0.0029909 | 0.011936 | 0.0029921 | 2.229e-06 | 1.186e-06 | 0.017882 | 0.017882 | 0.017882 | 0.99303 | -0.13404 | 0.99323 | -0.13012 | 4.9127
46 | -0.014874 | -0.0037285 | 0.014875 | 0.0037288 | 5.4789e-07 | 3.1257e-07 | 0.022284 | 0.022284 | 0.022284 | 0.99323 | -0.13012 | 0.99327 | -0.12935 | 6.122
47 | -0.0035457 | -0.00088864 | 0.0035459 | 0.00088855 | 1.613e-07 | -9.4926e-08 | 0.0053063 | 0.0053062 | 0.0053063 | 0.99432 | -0.10921 | 0.99437 | -0.10825 | 1.4578

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.42952 | 0.10796

## res_load
| p_mw | q_mvar
0 | 0.013591 | 0.0034062
1 | 0.0034245 | 0.00085827
2 | 0.010206 | 0.0025578
3 | 0.012541 | 0.0031432
4 | 0.021802 | 0.0054641
5 | 0.023748 | 0.0059519
6 | 0.048391 | 0.012128
7 | 0.0096225 | 0.0024116
8 | 0.015694 | 0.0039333
9 | 0.031857 | 0.007984
10 | 0.022352 | 0.0056019
11 | 0.0089226 | 0.0022362
12 | 0.025892 | 0.0064891
13 | 0.006708 | 0.0016812
14 | 0.008056 | 0.002019
15 | 0.018777 | 0.004706
16 | 0.007763 | 0.0019456
17 | 0.010296 | 0.0025803
18 | 0.01218 | 0.0030526
19 | 0.010355 | 0.0025951
20 | 0.0079989 | 0.0020047
21 | 0.009127 | 0.0022874
22 | 0.015368 | 0.0038515
23 | 0.012768 | 0.0032
24 | 0.011934 | 0.0029909
25 | 0.0029382 | 0.00073638
26 | 0.0035457 | 0.00088864
27 | 0.010385 | 0.0026028
28 | 0.009905 | 0.0024824
29 | 0.0080903 | 0.0020276
30 | 0.011737 | 0.0029415

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1