## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-603_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-603_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-603_0_4_node_5 | 0.4 | n |  | TRUE
3 | bus_LV_261-603_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_261-603_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_261-603_0_4_node_6 | 0.4 | n |  | TRUE
6 | bus_LV_261-603_0_4_node_29 | 0.4 | n |  | TRUE
7 | bus_LV_261-603_0_4_node_24 | 0.4 | n |  | TRUE
8 | bus_LV_261-603_0_4_node_8 | 0.4 | n |  | TRUE
9 | bus_LV_261-603_0_4_node_21 | 0.4 | n |  | TRUE
10 | bus_LV_261-603_0_4_node_32 | 0.4 | n |  | TRUE
11 | bus_LV_261-603_0_4_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_261-603_0_4_node_33 | 0.4 | n |  | TRUE
13 | bus_LV_261-603_0_4_node_16 | 0.4 | n |  | TRUE
14 | bus_LV_261-603_0_4_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_261-603_0_4_node_18 | 0.4 | n |  | TRUE
16 | bus_LV_261-603_0_4_node_31 | 0.4 | n |  | TRUE
17 | bus_LV_261-603_0_4_node_10 | 0.4 | n |  | TRUE
18 | bus_LV_261-603_0_4_node_25 | 0.4 | n |  | TRUE
19 | bus_LV_261-603_0_4_node_26 | 0.4 | n |  | TRUE
20 | bus_LV_261-603_0_4_node_11 | 0.4 | n |  | TRUE
21 | bus_LV_261-603_0_4_node_20 | 0.4 | n |  | TRUE
22 | bus_LV_261-603_0_4_node_14 | 0.4 | n |  | TRUE
23 | bus_LV_261-603_0_4_node_17 | 0.4 | n |  | TRUE
24 | bus_LV_261-603_0_4_node_28 | 0.4 | n |  | TRUE
25 | bus_LV_261-603_0_4_node_23 | 0.4 | n |  | TRUE
26 | bus_LV_261-603_0_4_node_22 | 0.4 | n |  | TRUE
27 | bus_LV_261-603_0_4_node_27 | 0.4 | n |  | TRUE
28 | bus_LV_261-603_0_4_node_19 | 0.4 | n |  | TRUE
29 | bus_LV_261-603_0_4_node_30 | 0.4 | n |  | TRUE
30 | bus_MV_549_0_node_12 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-603_0_4_load_0 | 0 | 0.062139 | 0.015573 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-603_0_4_load_29 | 6 | 0.019698 | 0.0049368 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-603_0_4_load_24 | 7 | 0.0071752 | 0.0017983 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-603_0_4_load_21 | 9 | 0.0055835 | 0.0013994 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-603_0_4_load_32 | 10 | 0.021381 | 0.0053585 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-603_0_4_load_33 | 12 | 0.030547 | 0.0076559 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-603_0_4_load_16 | 13 | 0.023042 | 0.0057747 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-603_0_4_load_31 | 16 | 0.037026 | 0.0092797 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-603_0_4_load_26 | 19 | 0.016477 | 0.0041295 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-603_0_4_load_20 | 21 | 0.0066247 | 0.0016603 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-603_0_4_load_17 | 23 | 0.010857 | 0.002721 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-603_0_4_load_28 | 24 | 0.034386 | 0.008618 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-603_0_4_load_23 | 25 | 0.025201 | 0.0063159 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-603_0_4_load_22 | 26 | 0.012943 | 0.0032437 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-603_0_4_load_27 | 27 | 0.045926 | 0.01151 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-603_0_4_load_19 | 28 | 0.036376 | 0.0091166 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-603_0_4_load_30 | 29 | 0.089346 | 0.022392 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 26 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-603_0_4_line_0 |  | 0 | 1 | 0.039015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-603_0_4_line_1 |  | 1 | 2 | 0.020647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-603_0_4_line_2 |  | 2 | 8 | 0.013952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
3 | LV_261-603_0_4_line_3 |  | 2 | 9 | 0.073575 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
4 | LV_261-603_0_4_line_4 |  | 3 | 4 | 0.10438 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
5 | LV_261-603_0_4_line_5 |  | 3 | 5 | 0.091987 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_261-603_0_4_line_6 |  | 3 | 6 | 0.041661 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
7 | LV_261-603_0_4_line_7 |  | 4 | 7 | 0.090427 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
8 | LV_261-603_0_4_line_8 |  | 5 | 10 | 0.10034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_261-603_0_4_line_9 |  | 6 | 24 | 0.046404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_261-603_0_4_line_10 |  | 7 | 25 | 0.027928 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
11 | LV_261-603_0_4_line_11 |  | 8 | 13 | 0.012639 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
12 | LV_261-603_0_4_line_12 |  | 8 | 11 | 0.02831 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-603_0_4_line_13 |  | 9 | 26 | 0.01602 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
14 | LV_261-603_0_4_line_14 |  | 11 | 12 | 0.02589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_261-603_0_4_line_15 |  | 13 | 22 | 0.021852 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
16 | LV_261-603_0_4_line_16 |  | 14 | 15 | 0.04348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_261-603_0_4_line_17 |  | 14 | 16 | 0.028525 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_261-603_0_4_line_18 |  | 15 | 19 | 0.034341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_261-603_0_4_line_19 |  | 15 | 22 | 0.03601 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
20 | LV_261-603_0_4_line_20 |  | 17 | 18 | 0.035258 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_261-603_0_4_line_21 |  | 17 | 19 | 0.043817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_261-603_0_4_line_22 |  | 18 | 27 | 0.022849 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_261-603_0_4_line_23 |  | 18 | 20 | 0.021425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_261-603_0_4_line_24 |  | 20 | 21 | 0.0097014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_261-603_0_4_line_25 |  | 21 | 28 | 0.023055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_261-603_0_4_line_26 |  | 22 | 23 | 0.017635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_261-603_0_4_line_27 |  | 24 | 29 | 0.011242 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_261-603_0_4_line_28 |  | 25 | 26 | 0.030523 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-603_0_4_trafo_22 | 0.63 MVA 20/0.4 kV | 30 | 26 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13
0 | 2679699.2552 | 1249002.6195 | 2679686.2113 | 1248977.5369 | 2679681.4946 | 1248967.8847
1 | 2679683.1026 | 1249013.288 | 2679686.5906 | 1249011.0999 | 2679687.4984 | 1249009.2886 | 2679687.7458 | 1249007.1792 | 2679694.5482 | 1249004.4798 | 2679699.2552 | 1249002.6195
2 | 2679683.1026 | 1249013.288 | 2679685.8875 | 1249020.1415 | 2679688.3582 | 1249026.2125
3 | 2679683.1026 | 1249013.288 | 2679617.7744 | 1249047.1323
4 | 2679472.6233 | 1249031.6988 | 2679469.7666 | 1249034.1178 | 2679458.4685 | 1249039.8373 | 2679458.6706 | 1249042.7866 | 2679458.4876 | 1249061.4978 | 2679460.5261 | 1249078.9824 | 2679464.6395 | 1249085.8981 | 2679458.6027 | 1249088.9528 | 2679464.3704 | 1249111.5911 | 2679465.3425 | 1249115.1178 | 2679465.849 | 1249116.2032 | 2679466.6981 | 1249117.6378 | 2679468.3758 | 1249118.6722 | 2679470.2687 | 1249119.4203
5 | 2679435.0579 | 1248954.3165 | 2679438.4577 | 1248960.9558 | 2679441.3203 | 1248966.5427 | 2679442.5568 | 1248968.9388 | 2679445.493 | 1248974.6712 | 2679448.466 | 1248980.4709 | 2679452.609 | 1248991.9459 | 2679455.014 | 1249006.3109 | 2679456.6287 | 1249015.984 | 2679457.3692 | 1249025.5232 | 2679472.6233 | 1249031.6988
6 | 2679472.6233 | 1249031.6988 | 2679509.7555 | 1249012.8094
7 | 2679470.2687 | 1249119.4203 | 2679473.8284 | 1249119.7572 | 2679479.8879 | 1249117.8148 | 2679496.9558 | 1249109.7933 | 2679551.6531 | 1249081.3964
8 | 2679435.0579 | 1248954.3165 | 2679437.4304 | 1248954.2149 | 2679456.9913 | 1248945.0258 | 2679468.4461 | 1248938.8971 | 2679480.6018 | 1248933.4338 | 2679493.1103 | 1248927.575 | 2679510.8561 | 1248919.1623 | 2679525.2998 | 1248911.0048
9 | 2679509.7555 | 1249012.8094 | 2679524.288 | 1249005.4167 | 2679543.3102 | 1249011.5986 | 2679552.4561 | 1249007.3198
10 | 2679551.6531 | 1249081.3964 | 2679559.798 | 1249077.1678 | 2679576.4475 | 1249068.5423
11 | 2679688.3582 | 1249026.2125 | 2679683.1156 | 1249028.0434 | 2679676.6365 | 1249030.9132
12 | 2679688.3582 | 1249026.2125 | 2679691.6202 | 1249026.2342 | 2679695.6954 | 1249028.6685 | 2679699.2707 | 1249032.3415 | 2679704.1823 | 1249037.1555 | 2679706.9319 | 1249038.2154 | 2679708.7725 | 1249038.9185 | 2679712.1448 | 1249039.1529
13 | 2679603.5499 | 1249054.5015 | 2679617.7744 | 1249047.1323
14 | 2679698.5879 | 1249057.2728 | 2679706.6496 | 1249055.2686 | 2679710.2001 | 1249051.2356 | 2679712.1448 | 1249039.1529
15 | 2679656.6564 | 1249039.7631 | 2679676.6365 | 1249030.9132
16 | 2679658.7413 | 1249068.9125 | 2679659.8912 | 1249071.0073 | 2679662.3759 | 1249073.7871 | 2679665.9424 | 1249075.8699 | 2679679.504 | 1249106.2411
17 | 2679679.504 | 1249106.2411 | 2679653.9747 | 1249118.9674
18 | 2679658.7413 | 1249068.9125 | 2679647.8516 | 1249074.0144 | 2679627.7835 | 1249083.7743
19 | 2679656.6564 | 1249039.7631 | 2679661.8431 | 1249049.9514 | 2679667.22 | 1249062.2882 | 2679664.3799 | 1249066.2752 | 2679658.7413 | 1249068.9125
20 | 2679568.7353 | 1249085.3048 | 2679600.0591 | 1249068.9466
21 | 2679600.0591 | 1249068.9466 | 2679611.2754 | 1249091.8029 | 2679627.7835 | 1249083.7743
22 | 2679568.7353 | 1249085.3048 | 2679579.4344 | 1249105.4942
23 | 2679568.7353 | 1249085.3048 | 2679549.7008 | 1249095.2456
24 | 2679549.7008 | 1249095.2456 | 2679554.0972 | 1249103.8937
25 | 2679554.0972 | 1249103.8937 | 2679558.3747 | 1249112.3078 | 2679546.222 | 1249118.4481
26 | 2679656.6564 | 1249039.7631 | 2679640.9826 | 1249047.8451
27 | 2679562.639 | 1249002.5559 | 2679552.4561 | 1249007.3198
28 | 2679603.5499 | 1249054.5015 | 2679576.4475 | 1249068.5423

## bus_geodata
| x | y | coords
0 | 2679681.4946 | 1248967.8847
1 | 2679699.2552 | 1249002.6195
2 | 2679683.1026 | 1249013.288
3 | 2679472.6233 | 1249031.6988
4 | 2679470.2687 | 1249119.4203
5 | 2679435.0579 | 1248954.3165
6 | 2679509.7555 | 1249012.8094
7 | 2679551.6531 | 1249081.3964
8 | 2679688.3582 | 1249026.2125
9 | 2679617.7744 | 1249047.1323
10 | 2679525.2998 | 1248911.0048
11 | 2679712.1448 | 1249039.1529
12 | 2679698.5879 | 1249057.2728
13 | 2679676.6365 | 1249030.9132
14 | 2679679.504 | 1249106.2411
15 | 2679658.7413 | 1249068.9125
16 | 2679653.9747 | 1249118.9674
17 | 2679600.0591 | 1249068.9466
18 | 2679568.7353 | 1249085.3048
19 | 2679627.7835 | 1249083.7743
20 | 2679549.7008 | 1249095.2456
21 | 2679554.0972 | 1249103.8937
22 | 2679656.6564 | 1249039.7631
23 | 2679640.9826 | 1249047.8451
24 | 2679552.4561 | 1249007.3198
25 | 2679576.4475 | 1249068.5423
26 | 2679603.5499 | 1249054.5015
27 | 2679579.4344 | 1249105.4942
28 | 2679546.222 | 1249118.4481
29 | 2679562.639 | 1249002.5559
30 | 2679683.1026 | 1249013.288

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98538 | -0.27955 | 0.062139 | 0.015573
1 | 0.98761 | -0.23613 | 0 | 0
2 | 0.98879 | -0.21323 | 0 | 0
3 | 0.97997 | -0.3818 | 0 | 0
4 | 0.988 | -0.22694 | 0 | 0
5 | 0.97814 | -0.41757 | 0 | 0
6 | 0.97718 | -0.43618 | 0.019698 | 0.0049368
7 | 0.99496 | -0.094802 | 0.0071752 | 0.0017983
8 | 0.98745 | -0.23899 | 0 | 0
9 | 0.99796 | -0.038418 | 0.0055835 | 0.0013994
10 | 0.97615 | -0.45674 | 0.021381 | 0.0053585
11 | 0.98665 | -0.25447 | 0 | 0
12 | 0.98593 | -0.26864 | 0.030547 | 0.0076559
13 | 0.98641 | -0.25894 | 0.023042 | 0.0057747
14 | 0.98098 | -0.3643 | 0 | 0
15 | 0.98247 | -0.33518 | 0 | 0
16 | 0.98 | -0.38345 | 0.037026 | 0.0092797
17 | 0.97545 | -0.47189 | 0 | 0
18 | 0.97252 | -0.52949 | 0 | 0
19 | 0.97909 | -0.40077 | 0.016477 | 0.0041295
20 | 0.97166 | -0.54649 | 0 | 0
21 | 0.97127 | -0.55419 | 0.0066247 | 0.0016603
22 | 0.98485 | -0.28899 | 0 | 0
23 | 0.98468 | -0.29243 | 0.010857 | 0.002721
24 | 0.97182 | -0.54156 | 0.034386 | 0.008618
25 | 0.9972 | -0.052607 | 0.025201 | 0.0063159
26 | 1 | 0 | -0.48293 | -0.1243
27 | 0.97154 | -0.54885 | 0.045926 | 0.01151
28 | 0.97049 | -0.5697 | 0.036376 | 0.0091166
29 | 0.97088 | -0.56012 | 0.089346 | 0.022392
30 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.062139 | -0.015573 | 0.062268 | 0.015655 | 0.00012882 | 8.1948e-05 | 0.093836 | 0.093835 | 0.093836 | 0.98538 | -0.27955 | 0.98761 | -0.23613 | 25.779
1 | -0.062268 | -0.015655 | 0.062336 | 0.015699 | 6.8175e-05 | 4.3367e-05 | 0.093835 | 0.093835 | 0.093835 | 0.98761 | -0.23613 | 0.98879 | -0.21323 | 25.7789
2 | 0.20898 | 0.053192 | -0.20873 | -0.053026 | 0.00025923 | 0.00016555 | 0.31479 | 0.31479 | 0.31479 | 0.98879 | -0.21323 | 0.98745 | -0.23899 | 43.2404
3 | -0.27132 | -0.068891 | 0.27362 | 0.070363 | 0.0023034 | 0.0014723 | 0.40863 | 0.40862 | 0.40863 | 0.98879 | -0.21323 | 0.99796 | -0.038418 | 56.1298
4 | -0.16597 | -0.042042 | 0.16721 | 0.042836 | 0.0012446 | 0.00079388 | 0.25217 | 0.25217 | 0.25217 | 0.97997 | -0.3818 | 0.988 | -0.22694 | 34.6393
5 | 0.021457 | 0.0054052 | -0.021421 | -0.0053829 | 3.6642e-05 | 2.2294e-05 | 0.032592 | 0.032592 | 0.032592 | 0.97997 | -0.3818 | 0.97814 | -0.41757 | 8.9538
6 | 0.14451 | 0.036637 | -0.14414 | -0.036397 | 0.00037664 | 0.00024 | 0.21958 | 0.21958 | 0.21958 | 0.97997 | -0.3818 | 0.97718 | -0.43618 | 30.1625
7 | -0.16721 | -0.042836 | 0.16829 | 0.043524 | 0.0010782 | 0.00068771 | 0.25217 | 0.25217 | 0.25217 | 0.988 | -0.22694 | 0.99496 | -0.094802 | 34.6392
8 | 0.021421 | 0.0053829 | -0.021381 | -0.0053585 | 3.9972e-05 | 2.4325e-05 | 0.032592 | 0.032592 | 0.032592 | 0.97814 | -0.41757 | 0.97615 | -0.45674 | 8.954
9 | 0.12444 | 0.03146 | -0.12381 | -0.031061 | 0.00062547 | 0.00039972 | 0.18959 | 0.18959 | 0.18959 | 0.97718 | -0.43618 | 0.97182 | -0.54156 | 52.0845
10 | -0.17547 | -0.045322 | 0.17583 | 0.045553 | 0.00036194 | 0.00023091 | 0.2629 | 0.2629 | 0.2629 | 0.99496 | -0.094802 | 0.9972 | -0.052607 | 36.113
11 | 0.17814 | 0.045343 | -0.17796 | -0.045234 | 0.00017109 | 0.00010917 | 0.26869 | 0.26869 | 0.26869 | 0.98745 | -0.23899 | 0.98641 | -0.25894 | 36.9076
12 | 0.03059 | 0.0076828 | -0.030568 | -0.0076687 | 2.2565e-05 | 1.408e-05 | 0.046103 | 0.046103 | 0.046103 | 0.98745 | -0.23899 | 0.98665 | -0.25447 | 12.6658
13 | -0.27921 | -0.071762 | 0.27973 | 0.072096 | 0.00052219 | 0.00033378 | 0.41695 | 0.41695 | 0.41695 | 0.99796 | -0.038418 | 1 | 0 | 57.2733
14 | 0.030568 | 0.0076687 | -0.030547 | -0.0076559 | 2.0636e-05 | 1.2877e-05 | 0.046103 | 0.046104 | 0.046104 | 0.98665 | -0.25447 | 0.98593 | -0.26864 | 12.6658
15 | 0.15492 | 0.039459 | -0.1547 | -0.039317 | 0.00022422 | 0.00014294 | 0.23393 | 0.23393 | 0.23393 | 0.98641 | -0.25894 | 0.98485 | -0.28899 | 32.1332
16 | -0.03706 | -0.009301 | 0.037112 | 0.0093334 | 5.1535e-05 | 3.2433e-05 | 0.05622 | 0.05622 | 0.05622 | 0.98098 | -0.3643 | 0.98247 | -0.33518 | 15.4451
17 | 0.03706 | 0.009301 | -0.037026 | -0.0092797 | 3.381e-05 | 2.1279e-05 | 0.05622 | 0.05622 | 0.05622 | 0.98098 | -0.3643 | 0.98 | -0.38345 | 15.4451
18 | 0.10641 | 0.027058 | -0.10607 | -0.026844 | 0.00033507 | 0.00021401 | 0.1613 | 0.1613 | 0.1613 | 0.98247 | -0.33518 | 0.97909 | -0.40077 | 44.3142
19 | -0.14352 | -0.036391 | 0.14384 | 0.036595 | 0.00031947 | 0.00020355 | 0.21752 | 0.21752 | 0.21752 | 0.98247 | -0.33518 | 0.98485 | -0.28899 | 29.8796
20 | 0.089291 | 0.022519 | -0.089046 | -0.022363 | 0.00024549 | 0.00015668 | 0.13626 | 0.13626 | 0.13626 | 0.97545 | -0.47189 | 0.97252 | -0.52949 | 37.4347
21 | -0.089291 | -0.022519 | 0.089596 | 0.022714 | 0.00030509 | 0.00019471 | 0.13626 | 0.13626 | 0.13626 | 0.97545 | -0.47189 | 0.97909 | -0.40077 | 37.4346
22 | 0.045968 | 0.011537 | -0.045926 | -0.01151 | 4.2394e-05 | 2.6849e-05 | 0.07034 | 0.07034 | 0.07034 | 0.97252 | -0.52949 | 0.97154 | -0.54885 | 19.3241
23 | 0.043078 | 0.010826 | -0.043043 | -0.010804 | 3.4916e-05 | 2.208e-05 | 0.065922 | 0.065923 | 0.065923 | 0.97252 | -0.52949 | 0.97166 | -0.54649 | 18.1106
24 | 0.043043 | 0.010804 | -0.043027 | -0.010794 | 1.581e-05 | 9.9984e-06 | 0.065923 | 0.065923 | 0.065923 | 0.97166 | -0.54649 | 0.97127 | -0.55419 | 18.1106
25 | 0.036402 | 0.0091335 | -0.036376 | -0.0091166 | 2.6894e-05 | 1.6927e-05 | 0.055773 | 0.055774 | 0.055774 | 0.97127 | -0.55419 | 0.97049 | -0.5697 | 15.3224
26 | 0.010859 | 0.0027219 | -0.010857 | -0.002721 | 1.7801e-06 | 9.1488e-07 | 0.016407 | 0.016407 | 0.016407 | 0.98485 | -0.28899 | 0.98468 | -0.29243 | 4.5073
27 | 0.089425 | 0.022443 | -0.089346 | -0.022392 | 7.9053e-05 | 5.0455e-05 | 0.13694 | 0.13694 | 0.13694 | 0.97182 | -0.54156 | 0.97088 | -0.56012 | 37.6199
28 | -0.20103 | -0.051869 | 0.20155 | 0.052199 | 0.00051682 | 0.00032997 | 0.30051 | 0.30051 | 0.30051 | 0.9972 | -0.052607 | 1 | 0 | 41.2783

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.49587 | 0.12754

## res_load
| p_mw | q_mvar
0 | 0.062139 | 0.015573
1 | 0.019698 | 0.0049368
2 | 0.0071752 | 0.0017983
3 | 0.0055835 | 0.0013994
4 | 0.021381 | 0.0053585
5 | 0.030547 | 0.0076559
6 | 0.023042 | 0.0057747
7 | 0.037026 | 0.0092797
8 | 0.016477 | 0.0041295
9 | 0.0066247 | 0.0016603
10 | 0.010857 | 0.002721
11 | 0.034386 | 0.008618
12 | 0.025201 | 0.0063159
13 | 0.012943 | 0.0032437
14 | 0.045926 | 0.01151
15 | 0.036376 | 0.0091166
16 | 0.089346 | 0.022392

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1