## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-60_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-60_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-60_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_261-60_0_5_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_261-60_0_5_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_261-60_0_5_node_67 | 0.4 | n |  | TRUE
6 | bus_LV_261-60_0_5_node_5 | 0.4 | n |  | TRUE
7 | bus_LV_261-60_0_5_node_68 | 0.4 | n |  | TRUE
8 | bus_LV_261-60_0_5_node_27 | 0.4 | n |  | TRUE
9 | bus_LV_261-60_0_5_node_126 | 0.4 | n |  | TRUE
10 | bus_LV_261-60_0_5_node_127 | 0.4 | n |  | TRUE
11 | bus_LV_261-60_0_5_node_29 | 0.4 | n |  | TRUE
12 | bus_LV_261-60_0_5_node_132 | 0.4 | n |  | TRUE
13 | bus_LV_261-60_0_5_node_35 | 0.4 | n |  | TRUE
14 | bus_LV_261-60_0_5_node_15 | 0.4 | n |  | TRUE
15 | bus_LV_261-60_0_5_node_128 | 0.4 | n |  | TRUE
16 | bus_LV_261-60_0_5_node_12 | 0.4 | n |  | TRUE
17 | bus_LV_261-60_0_5_node_34 | 0.4 | n |  | TRUE
18 | bus_LV_261-60_0_5_node_77 | 0.4 | n |  | TRUE
19 | bus_LV_261-60_0_5_node_84 | 0.4 | n |  | TRUE
20 | bus_LV_261-60_0_5_node_75 | 0.4 | n |  | TRUE
21 | bus_LV_261-60_0_5_node_37 | 0.4 | n |  | TRUE
22 | bus_LV_261-60_0_5_node_114 | 0.4 | n |  | TRUE
23 | bus_LV_261-60_0_5_node_61 | 0.4 | n |  | TRUE
24 | bus_LV_261-60_0_5_node_38 | 0.4 | n |  | TRUE
25 | bus_LV_261-60_0_5_node_91 | 0.4 | n |  | TRUE
26 | bus_LV_261-60_0_5_node_96 | 0.4 | n |  | TRUE
27 | bus_LV_261-60_0_5_node_28 | 0.4 | n |  | TRUE
28 | bus_LV_261-60_0_5_node_20 | 0.4 | n |  | TRUE
29 | bus_LV_261-60_0_5_node_26 | 0.4 | n |  | TRUE
30 | bus_LV_261-60_0_5_node_89 | 0.4 | n |  | TRUE
31 | bus_LV_261-60_0_5_node_86 | 0.4 | n |  | TRUE
32 | bus_LV_261-60_0_5_node_23 | 0.4 | n |  | TRUE
33 | bus_LV_261-60_0_5_node_90 | 0.4 | n |  | TRUE
34 | bus_LV_261-60_0_5_node_36 | 0.4 | n |  | TRUE
35 | bus_LV_261-60_0_5_node_97 | 0.4 | n |  | TRUE
36 | bus_LV_261-60_0_5_node_24 | 0.4 | n |  | TRUE
37 | bus_LV_261-60_0_5_node_48 | 0.4 | n |  | TRUE
38 | bus_LV_261-60_0_5_node_14 | 0.4 | n |  | TRUE
39 | bus_LV_261-60_0_5_node_19 | 0.4 | n |  | TRUE
40 | bus_LV_261-60_0_5_node_131 | 0.4 | n |  | TRUE
41 | bus_LV_261-60_0_5_node_18 | 0.4 | n |  | TRUE
42 | bus_LV_261-60_0_5_node_41 | 0.4 | n |  | TRUE
43 | bus_LV_261-60_0_5_node_122 | 0.4 | n |  | TRUE
44 | bus_LV_261-60_0_5_node_13 | 0.4 | n |  | TRUE
45 | bus_LV_261-60_0_5_node_9 | 0.4 | n |  | TRUE
46 | bus_LV_261-60_0_5_node_17 | 0.4 | n |  | TRUE
47 | bus_LV_261-60_0_5_node_124 | 0.4 | n |  | TRUE
48 | bus_LV_261-60_0_5_node_121 | 0.4 | n |  | TRUE
49 | bus_LV_261-60_0_5_node_45 | 0.4 | n |  | TRUE
50 | bus_LV_261-60_0_5_node_44 | 0.4 | n |  | TRUE
51 | bus_LV_261-60_0_5_node_46 | 0.4 | n |  | TRUE
52 | bus_LV_261-60_0_5_node_123 | 0.4 | n |  | TRUE
53 | bus_LV_261-60_0_5_node_130 | 0.4 | n |  | TRUE
54 | bus_LV_261-60_0_5_node_8 | 0.4 | n |  | TRUE
55 | bus_LV_261-60_0_5_node_10 | 0.4 | n |  | TRUE
56 | bus_LV_261-60_0_5_node_11 | 0.4 | n |  | TRUE
57 | bus_LV_261-60_0_5_node_16 | 0.4 | n |  | TRUE
58 | bus_LV_261-60_0_5_node_6 | 0.4 | n |  | TRUE
59 | bus_LV_261-60_0_5_node_50 | 0.4 | n |  | TRUE
60 | bus_LV_261-60_0_5_node_49 | 0.4 | n |  | TRUE
61 | bus_LV_261-60_0_5_node_66 | 0.4 | n |  | TRUE
62 | bus_LV_261-60_0_5_node_21 | 0.4 | n |  | TRUE
63 | bus_LV_261-60_0_5_node_22 | 0.4 | n |  | TRUE
64 | bus_LV_261-60_0_5_node_59 | 0.4 | n |  | TRUE
65 | bus_LV_261-60_0_5_node_73 | 0.4 | n |  | TRUE
66 | bus_LV_261-60_0_5_node_32 | 0.4 | n |  | TRUE
67 | bus_LV_261-60_0_5_node_47 | 0.4 | n |  | TRUE
68 | bus_LV_261-60_0_5_node_72 | 0.4 | n |  | TRUE
69 | bus_LV_261-60_0_5_node_42 | 0.4 | n |  | TRUE
70 | bus_LV_261-60_0_5_node_39 | 0.4 | n |  | TRUE
71 | bus_LV_261-60_0_5_node_40 | 0.4 | n |  | TRUE
72 | bus_LV_261-60_0_5_node_69 | 0.4 | n |  | TRUE
73 | bus_LV_261-60_0_5_node_7 | 0.4 | n |  | TRUE
74 | bus_LV_261-60_0_5_node_71 | 0.4 | n |  | TRUE
75 | bus_LV_261-60_0_5_node_70 | 0.4 | n |  | TRUE
76 | bus_LV_261-60_0_5_node_108 | 0.4 | n |  | TRUE
77 | bus_LV_261-60_0_5_node_87 | 0.4 | n |  | TRUE
78 | bus_LV_261-60_0_5_node_53 | 0.4 | n |  | TRUE
79 | bus_LV_261-60_0_5_node_55 | 0.4 | n |  | TRUE
80 | bus_LV_261-60_0_5_node_56 | 0.4 | n |  | TRUE
81 | bus_LV_261-60_0_5_node_51 | 0.4 | n |  | TRUE
82 | bus_LV_261-60_0_5_node_58 | 0.4 | n |  | TRUE
83 | bus_LV_261-60_0_5_node_74 | 0.4 | n |  | TRUE
84 | bus_LV_261-60_0_5_node_94 | 0.4 | n |  | TRUE
85 | bus_LV_261-60_0_5_node_129 | 0.4 | n |  | TRUE
86 | bus_LV_261-60_0_5_node_64 | 0.4 | n |  | TRUE
87 | bus_LV_261-60_0_5_node_63 | 0.4 | n |  | TRUE
88 | bus_LV_261-60_0_5_node_60 | 0.4 | n |  | TRUE
89 | bus_LV_261-60_0_5_node_57 | 0.4 | n |  | TRUE
90 | bus_LV_261-60_0_5_node_54 | 0.4 | n |  | TRUE
91 | bus_LV_261-60_0_5_node_76 | 0.4 | n |  | TRUE
92 | bus_LV_261-60_0_5_node_82 | 0.4 | n |  | TRUE
93 | bus_LV_261-60_0_5_node_115 | 0.4 | n |  | TRUE
94 | bus_LV_261-60_0_5_node_120 | 0.4 | n |  | TRUE
95 | bus_LV_261-60_0_5_node_125 | 0.4 | n |  | TRUE
96 | bus_LV_261-60_0_5_node_52 | 0.4 | n |  | TRUE
97 | bus_LV_261-60_0_5_node_65 | 0.4 | n |  | TRUE
98 | bus_LV_261-60_0_5_node_62 | 0.4 | n |  | TRUE
99 | bus_LV_261-60_0_5_node_100 | 0.4 | n |  | TRUE
100 | bus_LV_261-60_0_5_node_93 | 0.4 | n |  | TRUE
101 | bus_LV_261-60_0_5_node_95 | 0.4 | n |  | TRUE
102 | bus_LV_261-60_0_5_node_98 | 0.4 | n |  | TRUE
103 | bus_LV_261-60_0_5_node_92 | 0.4 | n |  | TRUE
104 | bus_LV_261-60_0_5_node_80 | 0.4 | n |  | TRUE
105 | bus_LV_261-60_0_5_node_78 | 0.4 | n |  | TRUE
106 | bus_LV_261-60_0_5_node_79 | 0.4 | n |  | TRUE
107 | bus_LV_261-60_0_5_node_109 | 0.4 | n |  | TRUE
108 | bus_LV_261-60_0_5_node_111 | 0.4 | n |  | TRUE
109 | bus_LV_261-60_0_5_node_113 | 0.4 | n |  | TRUE
110 | bus_LV_261-60_0_5_node_110 | 0.4 | n |  | TRUE
111 | bus_LV_261-60_0_5_node_81 | 0.4 | n |  | TRUE
112 | bus_LV_261-60_0_5_node_83 | 0.4 | n |  | TRUE
113 | bus_LV_261-60_0_5_node_85 | 0.4 | n |  | TRUE
114 | bus_LV_261-60_0_5_node_102 | 0.4 | n |  | TRUE
115 | bus_LV_261-60_0_5_node_103 | 0.4 | n |  | TRUE
116 | bus_LV_261-60_0_5_node_88 | 0.4 | n |  | TRUE
117 | bus_LV_261-60_0_5_node_104 | 0.4 | n |  | TRUE
118 | bus_LV_261-60_0_5_node_99 | 0.4 | n |  | TRUE
119 | bus_LV_261-60_0_5_node_101 | 0.4 | n |  | TRUE
120 | bus_LV_261-60_0_5_node_105 | 0.4 | n |  | TRUE
121 | bus_LV_261-60_0_5_node_106 | 0.4 | n |  | TRUE
122 | bus_LV_261-60_0_5_node_107 | 0.4 | n |  | TRUE
123 | bus_LV_261-60_0_5_node_112 | 0.4 | n |  | TRUE
124 | bus_LV_261-60_0_5_node_116 | 0.4 | n |  | TRUE
125 | bus_LV_261-60_0_5_node_117 | 0.4 | n |  | TRUE
126 | bus_LV_261-60_0_5_node_118 | 0.4 | n |  | TRUE
127 | bus_LV_261-60_0_5_node_119 | 0.4 | n |  | TRUE
128 | bus_MV_359_0_node_156 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-60_0_5_load_0 | 0 | 0.0047596 | 0.0011929 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-60_0_5_load_1 | 1 | 0.0047511 | 0.0011907 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-60_0_5_load_3 | 3 | 0.0097094 | 0.0024334 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-60_0_5_load_67 | 5 | 0.0069934 | 0.0017527 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-60_0_5_load_5 | 6 | 0.010224 | 0.0025624 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-60_0_5_load_68 | 7 | 0.0036251 | 0.00090854 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-60_0_5_load_127 | 10 | 0.0037405 | 0.00093745 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-60_0_5_load_132 | 12 | 0.0058293 | 0.001461 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-60_0_5_load_128 | 15 | 0.003384 | 0.00084811 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-60_0_5_load_77 | 18 | 0.0049394 | 0.0012379 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-60_0_5_load_84 | 19 | 0.0035167 | 0.00088136 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-60_0_5_load_75 | 20 | 0.0044842 | 0.0011239 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-60_0_5_load_114 | 22 | 0.0040932 | 0.0010259 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-60_0_5_load_61 | 23 | 0.0043479 | 0.0010897 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-60_0_5_load_91 | 25 | 0.0045715 | 0.0011457 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-60_0_5_load_96 | 26 | 0.0060965 | 0.0015279 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-60_0_5_load_89 | 30 | 0.006493 | 0.0016273 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_261-60_0_5_load_86 | 31 | 0.0056398 | 0.0014135 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_261-60_0_5_load_90 | 33 | 0.0088397 | 0.0022154 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_261-60_0_5_load_97 | 35 | 0.0050175 | 0.0012575 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_261-60_0_5_load_48 | 37 | 0.0040822 | 0.0010231 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_261-60_0_5_load_131 | 40 | 0.0037636 | 0.00094324 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_261-60_0_5_load_122 | 43 | 0.0033929 | 0.00085033 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_261-60_0_5_load_9 | 45 | 0.0033621 | 0.00084263 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_261-60_0_5_load_124 | 47 | 0.0037956 | 0.00095128 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_261-60_0_5_load_121 | 48 | 0.0018468 | 0.00046286 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_261-60_0_5_load_130 | 53 | 0.0033782 | 0.00084665 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_261-60_0_5_load_11 | 56 | 0.015737 | 0.003944 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_261-60_0_5_load_6 | 58 | 0.0037923 | 0.00095045 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_261-60_0_5_load_50 | 59 | 0.0024305 | 0.00060913 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_261-60_0_5_load_49 | 60 | 0.0015575 | 0.00039036 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_261-60_0_5_load_66 | 61 | 0.057075 | 0.014304 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_261-60_0_5_load_59 | 64 | 0.0038644 | 0.00096852 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_261-60_0_5_load_73 | 65 | 0.0069912 | 0.0017522 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_261-60_0_5_load_47 | 67 | 0.0047741 | 0.0011965 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_261-60_0_5_load_72 | 68 | 0.023473 | 0.0058829 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_261-60_0_5_load_69 | 72 | 0.009155 | 0.0022945 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_261-60_0_5_load_7 | 73 | 0.0068221 | 0.0017098 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_261-60_0_5_load_71 | 74 | 0.00683 | 0.0017117 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_261-60_0_5_load_70 | 75 | 0.0045235 | 0.0011337 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_261-60_0_5_load_108 | 76 | 0.006588 | 0.0016511 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_261-60_0_5_load_87 | 77 | 0.0040857 | 0.001024 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_261-60_0_5_load_56 | 80 | 0.0057134 | 0.0014319 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_261-60_0_5_load_51 | 81 | 0.0074074 | 0.0018565 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_261-60_0_5_load_58 | 82 | 0.0081761 | 0.0020491 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_261-60_0_5_load_74 | 83 | 0.0070155 | 0.0017582 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_261-60_0_5_load_129 | 85 | 0.0062893 | 0.0015762 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_261-60_0_5_load_60 | 88 | 0.0062774 | 0.0015733 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_261-60_0_5_load_57 | 89 | 0.0023478 | 0.00058842 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_261-60_0_5_load_54 | 90 | 0.0021831 | 0.00054714 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_261-60_0_5_load_76 | 91 | 0.0050426 | 0.0012638 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_261-60_0_5_load_82 | 92 | 0.0036894 | 0.00092464 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_261-60_0_5_load_115 | 93 | 0.0041837 | 0.0010485 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_261-60_0_5_load_120 | 94 | 0.0014741 | 0.00036944 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_261-60_0_5_load_125 | 95 | 0.0033896 | 0.00084952 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_261-60_0_5_load_52 | 96 | 0.0023197 | 0.00058137 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_261-60_0_5_load_62 | 98 | 0.0037015 | 0.00092769 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_261-60_0_5_load_100 | 99 | 0.0032681 | 0.00081907 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_261-60_0_5_load_95 | 101 | 0.0047447 | 0.0011891 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_261-60_0_5_load_98 | 102 | 0.0050512 | 0.0012659 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_261-60_0_5_load_92 | 103 | 0.0030904 | 0.00077452 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_261-60_0_5_load_80 | 104 | 0.0032691 | 0.00081933 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_261-60_0_5_load_78 | 105 | 0.0017741 | 0.00044464 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_261-60_0_5_load_109 | 107 | 0.0054001 | 0.0013534 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_261-60_0_5_load_113 | 109 | 0.015008 | 0.0037614 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_261-60_0_5_load_110 | 110 | 0.0099393 | 0.002491 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_261-60_0_5_load_81 | 111 | 0.0053984 | 0.001353 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_261-60_0_5_load_83 | 112 | 0.0039213 | 0.00098277 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_261-60_0_5_load_85 | 113 | 0.0027498 | 0.00068916 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_261-60_0_5_load_102 | 114 | 0.0063194 | 0.0015838 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_261-60_0_5_load_103 | 115 | 0.0060072 | 0.0015055 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_261-60_0_5_load_88 | 116 | 0.0041725 | 0.0010457 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_261-60_0_5_load_99 | 118 | 0.0033136 | 0.00083046 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_261-60_0_5_load_101 | 119 | 0.003077 | 0.00077116 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_261-60_0_5_load_105 | 120 | 0.0040568 | 0.0010167 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_261-60_0_5_load_106 | 121 | 0.0028795 | 0.00072168 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_261-60_0_5_load_107 | 122 | 0.002979 | 0.00074661 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_261-60_0_5_load_112 | 123 | 0.0037373 | 0.00093666 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_261-60_0_5_load_116 | 124 | 0.0014246 | 0.00035704 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_261-60_0_5_load_117 | 125 | 0.001429 | 0.00035814 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_261-60_0_5_load_118 | 126 | 0.0014661 | 0.00036744 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_261-60_0_5_load_119 | 127 | 0.0015018 | 0.00037639 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 69 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-60_0_5_line_0 |  | 0 | 1 | 0.015073 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-60_0_5_line_1 |  | 0 | 2 | 0.0098705 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-60_0_5_line_2 |  | 1 | 3 | 0.033258 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-60_0_5_line_3 |  | 2 | 4 | 0.016561 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-60_0_5_line_4 |  | 4 | 5 | 0.016151 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_261-60_0_5_line_5 |  | 5 | 71 | 0.014556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_261-60_0_5_line_6 |  | 6 | 7 | 0.00074828 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_261-60_0_5_line_7 |  | 7 | 71 | 0.023667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_261-60_0_5_line_8 |  | 8 | 9 | 0.006295 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_261-60_0_5_line_9 |  | 8 | 10 | 0.013351 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_261-60_0_5_line_10 |  | 9 | 15 | 0.0093747 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_261-60_0_5_line_11 |  | 10 | 49 | 0.0026862 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_261-60_0_5_line_12 |  | 11 | 12 | 0.058096 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-60_0_5_line_13 |  | 11 | 13 | 0.061934 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_261-60_0_5_line_14 |  | 13 | 20 | 0.026797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_261-60_0_5_line_15 |  | 14 | 15 | 0.021088 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_261-60_0_5_line_16 |  | 14 | 16 | 0.040994 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_261-60_0_5_line_17 |  | 16 | 46 | 0.04967 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_261-60_0_5_line_18 |  | 16 | 47 | 0.011798 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_261-60_0_5_line_19 |  | 17 | 18 | 0.0041599 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_261-60_0_5_line_20 |  | 17 | 19 | 0.02092 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_261-60_0_5_line_21 |  | 18 | 91 | 0.01422 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_261-60_0_5_line_22 |  | 19 | 92 | 0.024273 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_261-60_0_5_line_23 |  | 20 | 83 | 0.027896 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_261-60_0_5_line_24 |  | 21 | 22 | 0.0068349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_261-60_0_5_line_25 |  | 21 | 23 | 0.0018347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_261-60_0_5_line_26 |  | 22 | 93 | 0.010374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_261-60_0_5_line_27 |  | 23 | 62 | 0.017555 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_261-60_0_5_line_28 |  | 24 | 25 | 0.0055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_261-60_0_5_line_29 |  | 24 | 26 | 0.025728 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
30 | LV_261-60_0_5_line_30 |  | 24 | 27 | 0.021195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
31 | LV_261-60_0_5_line_31 |  | 25 | 32 | 0.015413 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_261-60_0_5_line_32 |  | 26 | 35 | 0.020435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
33 | LV_261-60_0_5_line_33 |  | 27 | 66 | 0.00344 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_261-60_0_5_line_34 |  | 27 | 67 | 0.019541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
35 | LV_261-60_0_5_line_35 |  | 28 | 29 | 0.00671 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
36 | LV_261-60_0_5_line_36 |  | 28 | 30 | 0.019193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
37 | LV_261-60_0_5_line_37 |  | 28 | 31 | 0.013449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_261-60_0_5_line_38 |  | 29 | 34 | 0.021791 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
39 | LV_261-60_0_5_line_39 |  | 29 | 35 | 0.0061083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
40 | LV_261-60_0_5_line_40 |  | 30 | 76 | 0.0033746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
41 | LV_261-60_0_5_line_41 |  | 31 | 77 | 0.011681 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_261-60_0_5_line_42 |  | 32 | 33 | 0.038323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_261-60_0_5_line_43 |  | 34 | 69 | 0.027095 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
44 | LV_261-60_0_5_line_44 |  | 36 | 37 | 0.012697 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
45 | LV_261-60_0_5_line_45 |  | 36 | 38 | 0.005625 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
46 | LV_261-60_0_5_line_46 |  | 37 | 70 | 0.017142 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
47 | LV_261-60_0_5_line_47 |  | 38 | 44 | 0.10426 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_261-60_0_5_line_48 |  | 38 | 45 | 0.022309 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
49 | LV_261-60_0_5_line_49 |  | 39 | 40 | 0.0023 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_261-60_0_5_line_50 |  | 39 | 41 | 0.011897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_261-60_0_5_line_51 |  | 41 | 42 | 0.038362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_261-60_0_5_line_52 |  | 41 | 43 | 0.0071857 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_261-60_0_5_line_53 |  | 42 | 48 | 0.015988 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_261-60_0_5_line_54 |  | 43 | 51 | 0.03819 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_261-60_0_5_line_55 |  | 44 | 59 | 0.16976 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_261-60_0_5_line_56 |  | 45 | 73 | 0.033482 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
57 | LV_261-60_0_5_line_57 |  | 46 | 61 | 0.023811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_261-60_0_5_line_58 |  | 46 | 55 | 0.000735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_261-60_0_5_line_59 |  | 47 | 52 | 0.01001 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_261-60_0_5_line_60 |  | 48 | 94 | 0.0103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_261-60_0_5_line_61 |  | 49 | 50 | 0.009813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_261-60_0_5_line_62 |  | 50 | 53 | 0.003025 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_261-60_0_5_line_63 |  | 51 | 52 | 0.015778 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_261-60_0_5_line_64 |  | 52 | 95 | 0.009813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_261-60_0_5_line_65 |  | 54 | 55 | 0.024921 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_261-60_0_5_line_66 |  | 54 | 56 | 0.014763 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_261-60_0_5_line_67 |  | 54 | 57 | 0.077396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_261-60_0_5_line_68 |  | 54 | 58 | 0.026056 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
69 | LV_261-60_0_5_line_69 |  | 57 | 60 | 0.054699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_261-60_0_5_line_70 |  | 58 | 73 | 0.036085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
71 | LV_261-60_0_5_line_71 |  | 61 | 71 | 0.037435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_261-60_0_5_line_72 |  | 62 | 63 | 0.020781 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_261-60_0_5_line_73 |  | 62 | 64 | 0.015146 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_261-60_0_5_line_74 |  | 63 | 65 | 0.037731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_261-60_0_5_line_75 |  | 64 | 82 | 0.026547 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_261-60_0_5_line_76 |  | 65 | 83 | 0.032053 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_261-60_0_5_line_77 |  | 66 | 68 | 0.01669 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_261-60_0_5_line_78 |  | 67 | 70 | 0.010778 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
79 | LV_261-60_0_5_line_79 |  | 69 | 72 | 0.012384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_261-60_0_5_line_80 |  | 72 | 75 | 0.008067 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_261-60_0_5_line_81 |  | 74 | 75 | 0.0003134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_261-60_0_5_line_82 |  | 76 | 117 | 0.010967 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
83 | LV_261-60_0_5_line_83 |  | 77 | 116 | 0.0099203 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_261-60_0_5_line_84 |  | 78 | 79 | 0.022379 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_261-60_0_5_line_85 |  | 78 | 80 | 0.026803 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_261-60_0_5_line_86 |  | 78 | 81 | 0.015346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_261-60_0_5_line_87 |  | 79 | 97 | 0.022915 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_261-60_0_5_line_88 |  | 79 | 98 | 0.0016362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_261-60_0_5_line_89 |  | 80 | 99 | 0.016731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_261-60_0_5_line_90 |  | 81 | 96 | 0.019536 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_261-60_0_5_line_91 |  | 82 | 88 | 0.03126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_261-60_0_5_line_92 |  | 84 | 85 | 0.011764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_261-60_0_5_line_93 |  | 84 | 86 | 0.14431 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_261-60_0_5_line_94 |  | 86 | 87 | 0.003766 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_261-60_0_5_line_95 |  | 87 | 98 | 0.033028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_261-60_0_5_line_96 |  | 89 | 90 | 0.0065095 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_261-60_0_5_line_97 |  | 90 | 96 | 0.0064665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_261-60_0_5_line_98 |  | 91 | 105 | 0.012202 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_261-60_0_5_line_99 |  | 93 | 116 | 0.010321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_261-60_0_5_line_100 |  | 94 | 127 | 0.0092253 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_261-60_0_5_line_101 |  | 97 | 100 | 0.0144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_261-60_0_5_line_102 |  | 97 | 101 | 0.031282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_261-60_0_5_line_103 |  | 99 | 102 | 0.0062885 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_261-60_0_5_line_104 |  | 100 | 104 | 0.02431 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_261-60_0_5_line_105 |  | 100 | 103 | 0.014492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_261-60_0_5_line_106 |  | 102 | 118 | 0.0035444 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_261-60_0_5_line_107 |  | 104 | 105 | 0.016044 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_261-60_0_5_line_108 |  | 105 | 106 | 0.022851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_261-60_0_5_line_109 |  | 106 | 107 | 0.0086178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_261-60_0_5_line_110 |  | 107 | 110 | 0.013317 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_261-60_0_5_line_111 |  | 108 | 109 | 0.014475 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_261-60_0_5_line_112 |  | 108 | 110 | 0.011787 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_261-60_0_5_line_113 |  | 110 | 123 | 0.01175 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_261-60_0_5_line_114 |  | 111 | 112 | 0.0053779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_261-60_0_5_line_115 |  | 112 | 113 | 0.0087076 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_261-60_0_5_line_116 |  | 113 | 114 | 0.010466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_261-60_0_5_line_117 |  | 114 | 115 | 0.0013513 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_261-60_0_5_line_118 |  | 115 | 117 | 0.0055591 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_261-60_0_5_line_119 |  | 117 | 122 | 0.011826 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_261-60_0_5_line_120 |  | 118 | 119 | 0.0095145 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_261-60_0_5_line_121 |  | 119 | 120 | 0.0078045 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_261-60_0_5_line_122 |  | 120 | 121 | 0.0014552 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_261-60_0_5_line_123 |  | 121 | 122 | 0.016545 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_261-60_0_5_line_124 |  | 124 | 125 | 0.0090958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_261-60_0_5_line_125 |  | 125 | 126 | 0.0091998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_261-60_0_5_line_126 |  | 126 | 127 | 0.0092958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-60_0_5_trafo_42 | 0.63 MVA 20/0.4 kV | 128 | 69 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16
0 | 2682579.8147 | 1243770.3599 | 2682565.8211 | 1243764.7587
1 | 2682587.0244 | 1243776.5707 | 2682583.4852 | 1243771.8291 | 2682579.8147 | 1243770.3599
2 | 2682535.8801 | 1243760.1221 | 2682536.1899 | 1243759.5845 | 2682542.5887 | 1243755.4594 | 2682565.8211 | 1243764.7587
3 | 2682603.2317 | 1243780.1989 | 2682587.0244 | 1243776.5707
4 | 2682603.2317 | 1243780.1989 | 2682600.0771 | 1243796.0392
5 | 2682597.2342 | 1243810.315 | 2682600.0771 | 1243796.0392
6 | 2682577.2852 | 1243801.5703 | 2682577.0801 | 1243802.2899
7 | 2682597.2342 | 1243810.315 | 2682590.6968 | 1243808.6562 | 2682576.5104 | 1243804.2889 | 2682577.0801 | 1243802.2899
8 | 2682639.5436 | 1243817.4648 | 2682645.8054 | 1243816.6625
9 | 2682645.8054 | 1243816.6625 | 2682657.6885 | 1243816.5391 | 2682659.155 | 1243816.4927
10 | 2682639.5436 | 1243817.4648 | 2682636.5301 | 1243817.8453 | 2682630.2028 | 1243817.4895
11 | 2682661.8398 | 1243816.4079 | 2682659.155 | 1243816.4927
12 | 2682553.8924 | 1243722.048 | 2682558.1439 | 1243669.1132 | 2682558.0243 | 1243664.1301
13 | 2682498.4841 | 1243681.1812 | 2682515.4446 | 1243676.3246 | 2682526.7895 | 1243673.08 | 2682558.0243 | 1243664.1301
14 | 2682498.4841 | 1243681.1812 | 2682495.7232 | 1243682.4214 | 2682493.2397 | 1243684.3661 | 2682491.2905 | 1243688.1084 | 2682490.9492 | 1243692.5402 | 2682490.0784 | 1243704.4599
15 | 2682609.3704 | 1243814.2757 | 2682628.3812 | 1243817.3871 | 2682630.2028 | 1243817.4895
16 | 2682612.959 | 1243846.3934 | 2682603.3646 | 1243844.9922 | 2682609.3704 | 1243814.2757
17 | 2682585.272 | 1243870.381 | 2682591.1379 | 1243871.4078 | 2682596.8831 | 1243872.4218 | 2682603.3646 | 1243844.9922 | 2682612.959 | 1243846.3934
18 | 2682612.959 | 1243846.3934 | 2682624.59 | 1243848.3688
19 | 2682340.6531 | 1243873.7063 | 2682343.1035 | 1243870.3447
20 | 2682340.6531 | 1243873.7063 | 2682346.9366 | 1243878.408 | 2682359.2399 | 1243882.8254
21 | 2682351.4796 | 1243858.854 | 2682343.1035 | 1243870.3447
22 | 2682382.0855 | 1243891.0278 | 2682359.2399 | 1243882.8254
23 | 2682487.827 | 1243732.2641 | 2682489.2127 | 1243716.311 | 2682490.0784 | 1243704.4599
24 | 2682466.6288 | 1243823.8973 | 2682467.8374 | 1243830.6245
25 | 2682466.6288 | 1243823.8973 | 2682466.4353 | 1243822.0729
26 | 2682469.6718 | 1243840.8346 | 2682467.8374 | 1243830.6245
27 | 2682466.6628 | 1243804.606 | 2682465.6733 | 1243814.8886 | 2682466.4353 | 1243822.0729
28 | 2682494.7181 | 1243942.1068 | 2682495.9331 | 1243947.4709
29 | 2682494.7181 | 1243942.1068 | 2682488.1784 | 1243917.2235
30 | 2682494.7181 | 1243942.1068 | 2682498.1843 | 1243941.2321 | 2682501.0892 | 1243940.5053 | 2682504.0319 | 1243939.7679 | 2682508.4613 | 1243938.6509 | 2682511.7304 | 1243937.818 | 2682515.2724 | 1243936.9332
31 | 2682491.5429 | 1243959.0082 | 2682494.1063 | 1243958.3767 | 2682495.9943 | 1243957.4023 | 2682497.0592 | 1243956.3719 | 2682497.5354 | 1243955.2777 | 2682497.1107 | 1243952.6699 | 2682495.9331 | 1243947.4709
32 | 2682488.1784 | 1243917.2235 | 2682482.9841 | 1243897.4597
33 | 2682515.2724 | 1243936.9332 | 2682514.8134 | 1243933.5244
34 | 2682515.2724 | 1243936.9332 | 2682516.1761 | 1243946.3971 | 2682517.4388 | 1243954.5094 | 2682517.8911 | 1243956.2761
35 | 2682479.6243 | 1243885.089 | 2682481.4314 | 1243891.5521
36 | 2682479.6243 | 1243885.089 | 2682461.043 | 1243889.8963
37 | 2682479.6243 | 1243885.089 | 2682477.8404 | 1243878.0368 | 2682476.4101 | 1243872.0305
38 | 2682481.4314 | 1243891.5521 | 2682484.8221 | 1243890.6764 | 2682487.8562 | 1243889.8957 | 2682491.8233 | 1243888.8724 | 2682495.4871 | 1243887.9226 | 2682498.7198 | 1243886.9891 | 2682502.5334 | 1243886.1304
39 | 2682481.4314 | 1243891.5521 | 2682482.9841 | 1243897.4597
40 | 2682461.043 | 1243889.8963 | 2682457.7759 | 1243890.7415
41 | 2682476.4101 | 1243872.0305 | 2682473.7042 | 1243860.6677
42 | 2682491.5429 | 1243959.0082 | 2682454.5203 | 1243968.9067
43 | 2682502.5334 | 1243886.1304 | 2682507.1797 | 1243885.728 | 2682511.1142 | 1243883.2476 | 2682515.0216 | 1243865.8782
44 | 2682529.829 | 1243995.0445 | 2682528.776 | 1243993.0506 | 2682525.6138 | 1243983.0984
45 | 2682532.9075 | 1243999.7574 | 2682529.829 | 1243995.0445
46 | 2682520.5642 | 1243966.7173 | 2682524.475 | 1243979.5143 | 2682525.6138 | 1243983.0984
47 | 2682532.9075 | 1243999.7574 | 2682537.1863 | 1244010.5469 | 2682544.1557 | 1244015.9033 | 2682541.3802 | 1244019.8342 | 2682540.0673 | 1244025.1087 | 2682540.8262 | 1244033.025 | 2682550.9955 | 1244074.0073 | 2682553.4212 | 1244083.8037 | 2682555.2554 | 1244090.4896 | 2682561.6624 | 1244090.6344
48 | 2682532.9075 | 1243999.7574 | 2682542.6961 | 1243994.2562 | 2682549.0714 | 1243985.1936
49 | 2682619.6739 | 1243880.3337 | 2682620.4749 | 1243878.1766
50 | 2682619.6739 | 1243880.3337 | 2682624.3633 | 1243880.6326 | 2682630.849 | 1243883.8252
51 | 2682630.849 | 1243883.8252 | 2682632.5598 | 1243885.806 | 2682635.0922 | 1243890.6559 | 2682644.5197 | 1243889.9311 | 2682656.5389 | 1243891.4218 | 2682659.4288 | 1243891.7734 | 2682658.2613 | 1243897.4502
52 | 2682630.849 | 1243883.8252 | 2682635.4575 | 1243881.2542 | 2682637.3543 | 1243881.4658
53 | 2682658.2613 | 1243897.4502 | 2682655.0458 | 1243913.1113
54 | 2682646.421 | 1243855.4659 | 2682646.9738 | 1243857.5529 | 2682647.1518 | 1243860.5131 | 2682648.7186 | 1243865.7721 | 2682650.3887 | 1243869.587 | 2682649.0177 | 1243877.9295 | 2682647.2978 | 1243882.5756 | 2682637.3543 | 1243881.4658
55 | 2682561.6624 | 1244090.6344 | 2682567.3833 | 1244079.2613 | 2682571.7289 | 1244074.9297 | 2682576.3418 | 1244073.6597 | 2682589.5812 | 1244078.6809 | 2682594.1531 | 1244077.0989 | 2682596.4865 | 1244072.895 | 2682593.3171 | 1244055.7274 | 2682592.6645 | 1244039.0951 | 2682596.0557 | 1244015.9255 | 2682599.4108 | 1244015.4274 | 2682614.5493 | 1244031.7055 | 2682621.023 | 1244031.4065 | 2682624.7282 | 1244028.0223 | 2682628.0802 | 1244014.726 | 2682629.4344 | 1244007.5841 | 2682633.7651 | 1244002.492
56 | 2682564.135 | 1243955.4049 | 2682559.6237 | 1243966.1824 | 2682557.6749 | 1243970.4473 | 2682552.7583 | 1243979.9525 | 2682549.0714 | 1243985.1936
57 | 2682585.272 | 1243870.381 | 2682589.9226 | 1243847.0287
58 | 2682585.1259 | 1243871.1017 | 2682585.272 | 1243870.381
59 | 2682634.5233 | 1243849.5848 | 2682626.6522 | 1243848.7191 | 2682624.59 | 1243848.3688
60 | 2682652.9742 | 1243923.2009 | 2682655.0458 | 1243913.1113
61 | 2682671.6135 | 1243815.2543 | 2682661.8398 | 1243816.4079
62 | 2682671.6135 | 1243815.2543 | 2682673.2605 | 1243814.221 | 2682674.1683 | 1243813.6221
63 | 2682646.421 | 1243855.4659 | 2682644.996 | 1243855.7574 | 2682642.1171 | 1243856.7847 | 2682638.1552 | 1243854.7169 | 2682634.7156 | 1243852.056 | 2682634.5233 | 1243849.5848
64 | 2682634.5233 | 1243849.5848 | 2682642.0629 | 1243850.913 | 2682642.3047 | 1243848.7482
65 | 2682580.2507 | 1243895.5404 | 2682585.1259 | 1243871.1017
66 | 2682580.2507 | 1243895.5404 | 2682566.5621 | 1243893.4373 | 2682565.6503 | 1243893.4955
67 | 2682575.8754 | 1243960.0708 | 2682579.2696 | 1243951.8787 | 2682583.2157 | 1243940.4254 | 2682587.4716 | 1243923.5501 | 2682589.0854 | 1243916.2117 | 2682589.4003 | 1243914.2258 | 2682590.4947 | 1243907.2804 | 2682584.3962 | 1243906.6729 | 2682586.2372 | 1243896.5912 | 2682580.2507 | 1243895.5404
68 | 2682580.2507 | 1243895.5404 | 2682576.1838 | 1243915.1314 | 2682574.7904 | 1243921.0164
69 | 2682575.8754 | 1243960.0708 | 2682600.7944 | 1243970.9032 | 2682611.0601 | 1243971.302 | 2682627.9252 | 1243974.9421
70 | 2682574.7904 | 1243921.0164 | 2682572.4657 | 1243930.8355 | 2682570.1612 | 1243940.0101 | 2682566.574 | 1243949.5782 | 2682564.135 | 1243955.4049
71 | 2682597.2342 | 1243810.315 | 2682589.9226 | 1243847.0287
72 | 2682466.6628 | 1243804.606 | 2682476.0597 | 1243805.0036 | 2682476.0966 | 1243802.3466 | 2682484.8026 | 1243801.8784
73 | 2682466.6628 | 1243804.606 | 2682467.9377 | 1243795.5394 | 2682468.4719 | 1243789.573
74 | 2682484.8026 | 1243801.8784 | 2682484.3714 | 1243794.3003 | 2682484.0743 | 1243782.5098 | 2682484.4069 | 1243771.6399 | 2682485.0534 | 1243764.1967
75 | 2682470.9081 | 1243763.1381 | 2682469.7811 | 1243774.9501 | 2682468.4719 | 1243789.573
76 | 2682485.0534 | 1243764.1967 | 2682487.827 | 1243732.2641
77 | 2682514.8134 | 1243933.5244 | 2682510.6273 | 1243917.3682
78 | 2682520.5642 | 1243966.7173 | 2682517.8911 | 1243956.2761
79 | 2682515.0216 | 1243865.8782 | 2682526.5005 | 1243865.4709 | 2682527.3802 | 1243865.6506
80 | 2682527.3802 | 1243865.6506 | 2682535.284 | 1243867.2648
81 | 2682535.5911 | 1243867.3275 | 2682535.284 | 1243867.2648
82 | 2682447.1589 | 1243893.4883 | 2682457.7759 | 1243890.7415
83 | 2682473.7042 | 1243860.6677 | 2682473.0345 | 1243857.8554 | 2682471.6398 | 1243850.9658
84 | 2682404.4275 | 1243786.1948 | 2682424.7713 | 1243795.6509
85 | 2682424.7713 | 1243795.6509 | 2682425.5284 | 1243805.891 | 2682428.8711 | 1243822.0841
86 | 2682424.7713 | 1243795.6509 | 2682424.7862 | 1243785.3325 | 2682426.2806 | 1243780.5326
87 | 2682390.9204 | 1243804.7318 | 2682404.4275 | 1243786.1948
88 | 2682404.4275 | 1243786.1948 | 2682402.9507 | 1243785.4905
89 | 2682428.8711 | 1243822.0841 | 2682429.0549 | 1243822.9746 | 2682432.9895 | 1243838.2997
90 | 2682426.2806 | 1243780.5326 | 2682426.5821 | 1243779.5644 | 2682427.6078 | 1243761.0709
91 | 2682473.594 | 1243731.9938 | 2682471.4445 | 1243757.5162 | 2682470.9081 | 1243763.1381
92 | 2682327.8534 | 1243801.5765 | 2682323.9998 | 1243812.6916
93 | 2682327.8534 | 1243801.5765 | 2682297.0681 | 1243793.4658 | 2682309.0398 | 1243747.2095 | 2682345.124 | 1243760.7421 | 2682369.6137 | 1243769.9219
94 | 2682369.6137 | 1243769.9219 | 2682373.1398 | 1243771.2719
95 | 2682373.1398 | 1243771.2719 | 2682402.9507 | 1243785.4905
96 | 2682427.9659 | 1243754.6143 | 2682428.3264 | 1243748.1149
97 | 2682427.9659 | 1243754.6143 | 2682427.6078 | 1243761.0709
98 | 2682358.6671 | 1243848.994 | 2682351.4796 | 1243858.854
99 | 2682471.6398 | 1243850.9658 | 2682470.3258 | 1243844.4747 | 2682469.6718 | 1243840.8346
100 | 2682651.1187 | 1243932.2377 | 2682652.9742 | 1243923.2009
101 | 2682382.4295 | 1243816.3779 | 2682390.9204 | 1243804.7318
102 | 2682390.9204 | 1243804.7318 | 2682403.397 | 1243813.5781 | 2682407.5885 | 1243829.0065
103 | 2682434.5533 | 1243844.3906 | 2682432.9895 | 1243838.2997
104 | 2682382.4295 | 1243816.3779 | 2682368.1145 | 1243836.0266
105 | 2682382.4295 | 1243816.3779 | 2682378.5755 | 1243802.4074
106 | 2682434.5533 | 1243844.3906 | 2682435.4347 | 1243847.8237
107 | 2682358.6671 | 1243848.994 | 2682368.1145 | 1243836.0266
108 | 2682358.6671 | 1243848.994 | 2682377.1095 | 1243862.5598
109 | 2682377.1095 | 1243862.5598 | 2682384.053 | 1243867.664
110 | 2682394.7205 | 1243863.605 | 2682390.9969 | 1243867.7674 | 2682388.2269 | 1243869.13 | 2682386.0052 | 1243869.0991 | 2682384.053 | 1243867.664
111 | 2682391.7423 | 1243852.1998 | 2682394.4665 | 1243849.7915 | 2682397.3277 | 1243846.2175 | 2682398.3768 | 1243841.9734 | 2682398.3179 | 1243840.0858
112 | 2682394.7205 | 1243863.605 | 2682391.7423 | 1243852.1998
113 | 2682394.7205 | 1243863.605 | 2682397.6839 | 1243874.9766
114 | 2682416.8256 | 1243901.8397 | 2682422.0105 | 1243900.4122
115 | 2682430.4057 | 1243898.1008 | 2682422.0105 | 1243900.4122
116 | 2682440.4963 | 1243895.3227 | 2682430.4057 | 1243898.1008
117 | 2682440.4963 | 1243895.3227 | 2682441.7991 | 1243894.964
118 | 2682447.1589 | 1243893.4883 | 2682441.7991 | 1243894.964
119 | 2682447.1589 | 1243893.4883 | 2682444.218 | 1243882.0338
120 | 2682437.8008 | 1243857.0393 | 2682435.4347 | 1243847.8237
121 | 2682437.8008 | 1243857.0393 | 2682439.7416 | 1243864.5986
122 | 2682439.7416 | 1243864.5986 | 2682440.1035 | 1243866.0081
123 | 2682440.1035 | 1243866.0081 | 2682444.218 | 1243882.0338
124 | 2682645.5695 | 1243959.2653 | 2682647.3989 | 1243950.3554
125 | 2682649.2491 | 1243941.3436 | 2682647.3989 | 1243950.3554
126 | 2682649.2491 | 1243941.3436 | 2682651.1187 | 1243932.2377

## bus_geodata
| x | y | coords
0 | 2682579.8147 | 1243770.3599
1 | 2682565.8211 | 1243764.7587
2 | 2682587.0244 | 1243776.5707
3 | 2682535.8801 | 1243760.1221
4 | 2682603.2317 | 1243780.1989
5 | 2682600.0771 | 1243796.0392
6 | 2682577.2852 | 1243801.5703
7 | 2682577.0801 | 1243802.2899
8 | 2682645.8054 | 1243816.6625
9 | 2682639.5436 | 1243817.4648
10 | 2682659.155 | 1243816.4927
11 | 2682558.0243 | 1243664.1301
12 | 2682553.8924 | 1243722.048
13 | 2682498.4841 | 1243681.1812
14 | 2682609.3704 | 1243814.2757
15 | 2682630.2028 | 1243817.4895
16 | 2682612.959 | 1243846.3934
17 | 2682340.6531 | 1243873.7063
18 | 2682343.1035 | 1243870.3447
19 | 2682359.2399 | 1243882.8254
20 | 2682490.0784 | 1243704.4599
21 | 2682466.6288 | 1243823.8973
22 | 2682467.8374 | 1243830.6245
23 | 2682466.4353 | 1243822.0729
24 | 2682494.7181 | 1243942.1068
25 | 2682495.9331 | 1243947.4709
26 | 2682488.1784 | 1243917.2235
27 | 2682515.2724 | 1243936.9332
28 | 2682479.6243 | 1243885.0889
29 | 2682481.4314 | 1243891.5521
30 | 2682461.0429 | 1243889.8963
31 | 2682476.4101 | 1243872.0305
32 | 2682491.5429 | 1243959.0082
33 | 2682454.5203 | 1243968.9067
34 | 2682502.5335 | 1243886.1304
35 | 2682482.9841 | 1243897.4597
36 | 2682529.829 | 1243995.0445
37 | 2682525.6138 | 1243983.0984
38 | 2682532.9075 | 1243999.7574
39 | 2682619.6739 | 1243880.3337
40 | 2682620.4749 | 1243878.1766
41 | 2682630.849 | 1243883.8252
42 | 2682658.2613 | 1243897.4502
43 | 2682637.3543 | 1243881.4658
44 | 2682561.6624 | 1244090.6344
45 | 2682549.0714 | 1243985.1936
46 | 2682585.272 | 1243870.381
47 | 2682624.59 | 1243848.3688
48 | 2682655.0458 | 1243913.1113
49 | 2682661.8398 | 1243816.4079
50 | 2682671.6135 | 1243815.2543
51 | 2682646.421 | 1243855.4659
52 | 2682634.5233 | 1243849.5848
53 | 2682674.1683 | 1243813.6221
54 | 2682580.2507 | 1243895.5404
55 | 2682585.1259 | 1243871.1017
56 | 2682565.6503 | 1243893.4955
57 | 2682575.8754 | 1243960.0708
58 | 2682574.7904 | 1243921.0164
59 | 2682633.7651 | 1244002.492
60 | 2682627.9252 | 1243974.9421
61 | 2682589.9226 | 1243847.0287
62 | 2682466.6628 | 1243804.606
63 | 2682484.8026 | 1243801.8784
64 | 2682468.4719 | 1243789.573
65 | 2682485.0534 | 1243764.1967
66 | 2682514.8134 | 1243933.5244
67 | 2682517.8911 | 1243956.2761
68 | 2682510.6273 | 1243917.3682
69 | 2682515.0216 | 1243865.8782
70 | 2682520.5642 | 1243966.7173
71 | 2682597.2342 | 1243810.315
72 | 2682527.3802 | 1243865.6506
73 | 2682564.135 | 1243955.4049
74 | 2682535.5911 | 1243867.3275
75 | 2682535.284 | 1243867.2648
76 | 2682457.7759 | 1243890.7415
77 | 2682473.7042 | 1243860.6677
78 | 2682424.7713 | 1243795.6509
79 | 2682404.4275 | 1243786.1948
80 | 2682428.8711 | 1243822.0841
81 | 2682426.2806 | 1243780.5326
82 | 2682470.9081 | 1243763.1381
83 | 2682487.827 | 1243732.2641
84 | 2682327.8534 | 1243801.5765
85 | 2682323.9998 | 1243812.6916
86 | 2682369.6137 | 1243769.9219
87 | 2682373.1398 | 1243771.2719
88 | 2682473.594 | 1243731.9938
89 | 2682428.3264 | 1243748.1149
90 | 2682427.9659 | 1243754.6143
91 | 2682351.4796 | 1243858.854
92 | 2682382.0855 | 1243891.0278
93 | 2682469.6718 | 1243840.8346
94 | 2682652.9742 | 1243923.2009
95 | 2682642.3047 | 1243848.7482
96 | 2682427.6078 | 1243761.0709
97 | 2682390.9204 | 1243804.7318
98 | 2682402.9507 | 1243785.4905
99 | 2682432.9895 | 1243838.2997
100 | 2682382.4295 | 1243816.3779
101 | 2682407.5885 | 1243829.0065
102 | 2682434.5533 | 1243844.3906
103 | 2682378.5755 | 1243802.4074
104 | 2682368.1145 | 1243836.0266
105 | 2682358.6671 | 1243848.994
106 | 2682377.1095 | 1243862.5598
107 | 2682384.053 | 1243867.664
108 | 2682391.7423 | 1243852.1998
109 | 2682398.3179 | 1243840.0858
110 | 2682394.7205 | 1243863.605
111 | 2682416.8256 | 1243901.8397
112 | 2682422.0105 | 1243900.4122
113 | 2682430.4057 | 1243898.1008
114 | 2682440.4963 | 1243895.3227
115 | 2682441.7991 | 1243894.964
116 | 2682471.6398 | 1243850.9658
117 | 2682447.1589 | 1243893.4883
118 | 2682435.4347 | 1243847.8237
119 | 2682437.8008 | 1243857.0393
120 | 2682439.7416 | 1243864.5986
121 | 2682440.1035 | 1243866.0081
122 | 2682444.218 | 1243882.0338
123 | 2682397.6839 | 1243874.9766
124 | 2682645.5695 | 1243959.2653
125 | 2682647.3989 | 1243950.3554
126 | 2682649.2491 | 1243941.3436
127 | 2682651.1187 | 1243932.2377
128 | 2682502.5335 | 1243886.1304

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97591 | -0.46463 | 0.0047596 | 0.0011929
1 | 0.97571 | -0.46862 | 0.0047511 | 0.0011907
2 | 0.97609 | -0.46115 | 0 | 0
3 | 0.97541 | -0.47453 | 0.0097094 | 0.0024334
4 | 0.97638 | -0.45533 | 0 | 0
5 | 0.97667 | -0.44966 | 0.0069934 | 0.0017527
6 | 0.97672 | -0.44881 | 0.010224 | 0.0025624
7 | 0.97672 | -0.44867 | 0.0036251 | 0.00090854
8 | 0.97829 | -0.41788 | 0 | 0
9 | 0.97833 | -0.41706 | 0 | 0
10 | 0.9782 | -0.41961 | 0.0037405 | 0.00093745
11 | 0.98792 | -0.23194 | 0 | 0
12 | 0.98761 | -0.23799 | 0.0058293 | 0.001461
13 | 0.98825 | -0.22549 | 0 | 0
14 | 0.9786 | -0.41181 | 0 | 0
15 | 0.9784 | -0.41585 | 0.003384 | 0.00084811
16 | 0.979 | -0.40398 | 0 | 0
17 | 0.97744 | -0.43478 | 0 | 0
18 | 0.97747 | -0.43423 | 0.0049394 | 0.0012379
19 | 0.9773 | -0.43753 | 0.0035167 | 0.00088136
20 | 0.98839 | -0.2227 | 0.0044842 | 0.0011239
21 | 0.99124 | -0.16752 | 0 | 0
22 | 0.99153 | -0.16182 | 0.0040932 | 0.0010259
23 | 0.99116 | -0.16905 | 0.0043479 | 0.0010897
24 | 0.99237 | -0.14517 | 0 | 0
25 | 0.9923 | -0.14648 | 0.0045715 | 0.0011457
26 | 0.99362 | -0.12122 | 0.0060965 | 0.0015279
27 | 0.99141 | -0.16368 | 0 | 0
28 | 0.99461 | -0.10239 | 0 | 0
29 | 0.99496 | -0.095735 | 0 | 0
30 | 0.99392 | -0.11561 | 0.006493 | 0.0016273
31 | 0.99376 | -0.1188 | 0.0056398 | 0.0014135
32 | 0.99218 | -0.14889 | 0 | 0
33 | 0.99187 | -0.15489 | 0.0088397 | 0.0022154
34 | 0.99721 | -0.052942 | 0 | 0
35 | 0.99465 | -0.1017 | 0.0050175 | 0.0012575
36 | 0.98904 | -0.20904 | 0 | 0
37 | 0.98953 | -0.19972 | 0.0040822 | 0.0010231
38 | 0.98883 | -0.21317 | 0 | 0
39 | 0.97762 | -0.43114 | 0 | 0
40 | 0.97761 | -0.4313 | 0.0037636 | 0.00094324
41 | 0.97766 | -0.43033 | 0 | 0
42 | 0.97733 | -0.43673 | 0 | 0
43 | 0.97774 | -0.42864 | 0.0033929 | 0.00085033
44 | 0.98859 | -0.2177 | 0 | 0
45 | 0.98799 | -0.22933 | 0.0033621 | 0.00084263
46 | 0.98057 | -0.37332 | 0 | 0
47 | 0.97874 | -0.40902 | 0.0037956 | 0.00095128
48 | 0.9772 | -0.43939 | 0.0018468 | 0.00046286
49 | 0.9782 | -0.41977 | 0 | 0
50 | 0.97817 | -0.42038 | 0 | 0
51 | 0.97832 | -0.41729 | 0 | 0
52 | 0.97856 | -0.41261 | 0 | 0
53 | 0.97816 | -0.42056 | 0.0033782 | 0.00084665
54 | 0.98369 | -0.31252 | 0 | 0
55 | 0.98065 | -0.37157 | 0 | 0
56 | 0.98347 | -0.31671 | 0.015737 | 0.003944
57 | 0.98358 | -0.3147 | 0 | 0
58 | 0.98548 | -0.27775 | 0.0037923 | 0.00095045
59 | 0.98822 | -0.22507 | 0.0024305 | 0.00060913
60 | 0.9835 | -0.31623 | 0.0015575 | 0.00039036
61 | 0.97842 | -0.41534 | 0.057075 | 0.014304
62 | 0.99047 | -0.18234 | 0 | 0
63 | 0.99001 | -0.19133 | 0 | 0
64 | 0.99022 | -0.18727 | 0.0038644 | 0.00096852
65 | 0.98917 | -0.20767 | 0.0069912 | 0.0017522
66 | 0.99133 | -0.16512 | 0 | 0
67 | 0.99062 | -0.17875 | 0.0047741 | 0.0011965
68 | 0.99097 | -0.17207 | 0.023473 | 0.0058829
69 | 1 | 0 | -0.47581 | -0.12136
70 | 0.9902 | -0.18684 | 0 | 0
71 | 0.97703 | -0.44269 | 0 | 0
72 | 0.99977 | -0.0044278 | 0.009155 | 0.0022945
73 | 0.98675 | -0.25313 | 0.0068221 | 0.0017098
74 | 0.99968 | -0.0060623 | 0.00683 | 0.0017117
75 | 0.99969 | -0.006025 | 0.0045235 | 0.0011337
76 | 0.9938 | -0.11784 | 0.006588 | 0.0016511
77 | 0.99308 | -0.13191 | 0.0040857 | 0.001024
78 | 0.98358 | -0.31479 | 0 | 0
79 | 0.98204 | -0.34474 | 0 | 0
80 | 0.98578 | -0.27219 | 0.0057134 | 0.0014319
81 | 0.98338 | -0.31874 | 0.0074074 | 0.0018565
82 | 0.98987 | -0.1941 | 0.0081761 | 0.0020491
83 | 0.98866 | -0.21757 | 0.0070155 | 0.0017582
84 | 0.98097 | -0.36565 | 0 | 0
85 | 0.9809 | -0.36699 | 0.0062893 | 0.0015762
86 | 0.98181 | -0.34922 | 0 | 0
87 | 0.98183 | -0.34879 | 0 | 0
88 | 0.98969 | -0.19759 | 0.0062774 | 0.0015733
89 | 0.98321 | -0.32195 | 0.0023478 | 0.00058842
90 | 0.98323 | -0.32168 | 0.0021831 | 0.00054714
91 | 0.97763 | -0.43108 | 0.0050426 | 0.0012638
92 | 0.97722 | -0.43916 | 0.0036894 | 0.00092464
93 | 0.99202 | -0.15243 | 0.0041837 | 0.0010485
94 | 0.97713 | -0.44077 | 0.0014741 | 0.00036944
95 | 0.97853 | -0.41321 | 0.0033896 | 0.00084952
96 | 0.98325 | -0.32115 | 0.0023197 | 0.00058137
97 | 0.98068 | -0.37135 | 0 | 0
98 | 0.98203 | -0.34503 | 0.0037015 | 0.00092769
99 | 0.98724 | -0.24399 | 0.0032681 | 0.00081907
100 | 0.97988 | -0.38686 | 0 | 0
101 | 0.98054 | -0.37404 | 0.0047447 | 0.0011891
102 | 0.9878 | -0.23304 | 0.0050512 | 0.0012659
103 | 0.97984 | -0.38768 | 0.0030904 | 0.00077452
104 | 0.97861 | -0.41175 | 0.0032691 | 0.00081933
105 | 0.97782 | -0.42725 | 0.0017741 | 0.00044464
106 | 0.9771 | -0.44146 | 0 | 0
107 | 0.97683 | -0.44683 | 0.0054001 | 0.0013534
108 | 0.97631 | -0.45704 | 0 | 0
109 | 0.9761 | -0.46102 | 0.015008 | 0.0037614
110 | 0.97647 | -0.45381 | 0.0099393 | 0.002491
111 | 0.99272 | -0.13872 | 0.0053984 | 0.001353
112 | 0.99274 | -0.13821 | 0.0039213 | 0.00098277
113 | 0.99282 | -0.13677 | 0.0027498 | 0.00068916
114 | 0.99293 | -0.13454 | 0.0063194 | 0.0015838
115 | 0.99296 | -0.1341 | 0.0060072 | 0.0015055
116 | 0.99254 | -0.14233 | 0.0041725 | 0.0010457
117 | 0.99308 | -0.1317 | 0 | 0
118 | 0.98814 | -0.22655 | 0.0033136 | 0.00083046
119 | 0.98907 | -0.20861 | 0.003077 | 0.00077116
120 | 0.98986 | -0.19348 | 0.0040568 | 0.0010167
121 | 0.99001 | -0.19056 | 0.0028795 | 0.00072168
122 | 0.99178 | -0.15656 | 0.002979 | 0.00074661
123 | 0.97643 | -0.45461 | 0.0037373 | 0.00093666
124 | 0.977 | -0.4432 | 0.0014246 | 0.00035704
125 | 0.97702 | -0.44296 | 0.001429 | 0.00035814
126 | 0.97704 | -0.44248 | 0.0014661 | 0.00036744
127 | 0.97708 | -0.44175 | 0.0015018 | 0.00037639
128 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.014466 | 0.0036271 | -0.014463 | -0.0036255 | 2.7501e-06 | 1.5718e-06 | 0.022058 | 0.022058 | 0.022058 | 0.97591 | -0.46463 | 0.97571 | -0.46862 | 6.0598
1 | -0.019226 | -0.0048199 | 0.019229 | 0.0048219 | 3.1808e-06 | 1.9124e-06 | 0.029315 | 0.029315 | 0.029315 | 0.97591 | -0.46463 | 0.97609 | -0.46115 | 8.0535
2 | 0.0097122 | 0.0024348 | -0.0097094 | -0.0024334 | 2.7362e-06 | 1.3359e-06 | 0.014812 | 0.014812 | 0.014812 | 0.97571 | -0.46862 | 0.97541 | -0.47453 | 4.0692
3 | -0.019229 | -0.0048219 | 0.019234 | 0.0048251 | 5.3369e-06 | 3.2086e-06 | 0.029315 | 0.029315 | 0.029315 | 0.97609 | -0.46115 | 0.97638 | -0.45533 | 8.0535
4 | -0.019234 | -0.0048251 | 0.019239 | 0.0048282 | 5.2049e-06 | 3.1291e-06 | 0.029315 | 0.029315 | 0.029315 | 0.97638 | -0.45533 | 0.97667 | -0.44966 | 8.0535
5 | -0.026233 | -0.0065809 | 0.026242 | 0.0065863 | 8.7203e-06 | 5.3988e-06 | 0.03997 | 0.039969 | 0.03997 | 0.97667 | -0.44966 | 0.97703 | -0.44269 | 10.9806
6 | -0.010224 | -0.0025624 | 0.010224 | 0.0025624 | 6.8079e-08 | 3.4205e-08 | 0.015576 | 0.015576 | 0.015576 | 0.97672 | -0.44881 | 0.97672 | -0.44867 | 4.2791
7 | -0.013849 | -0.0034709 | 0.013853 | 0.0034732 | 3.9508e-06 | 2.2322e-06 | 0.021099 | 0.021099 | 0.021099 | 0.97672 | -0.44867 | 0.97703 | -0.44269 | 5.7964
8 | -0.0071194 | -0.0017842 | 0.0071197 | 0.0017843 | 2.7681e-07 | 9.8118e-08 | 0.010829 | 0.010829 | 0.010829 | 0.97829 | -0.41788 | 0.97833 | -0.41706 | 2.9749
9 | 0.0071194 | 0.0017842 | -0.0071188 | -0.001784 | 5.8709e-07 | 2.0812e-07 | 0.010829 | 0.010829 | 0.010829 | 0.97829 | -0.41788 | 0.9782 | -0.41961 | 2.975
10 | -0.0071197 | -0.0017843 | 0.0071201 | 0.0017845 | 4.1224e-07 | 1.4611e-07 | 0.010829 | 0.010829 | 0.010829 | 0.97833 | -0.41706 | 0.9784 | -0.41585 | 2.9749
11 | 0.0033783 | 0.00084656 | -0.0033783 | -0.00084657 | 2.6603e-08 | -1.6696e-08 | 0.005139 | 0.005139 | 0.005139 | 0.9782 | -0.41961 | 0.9782 | -0.41977 | 1.4118
12 | 0.005831 | 0.0014613 | -0.0058293 | -0.001461 | 1.6805e-06 | 3.3191e-07 | 0.0087827 | 0.008783 | 0.008783 | 0.98792 | -0.23194 | 0.98761 | -0.23799 | 2.4129
13 | -0.005831 | -0.0014613 | 0.0058328 | 0.0014617 | 1.7914e-06 | 3.5325e-07 | 0.0087827 | 0.0087825 | 0.0087827 | 0.98792 | -0.23194 | 0.98825 | -0.22549 | 2.4128
14 | -0.0058328 | -0.0014617 | 0.0058336 | 0.0014618 | 7.7507e-07 | 1.5265e-07 | 0.0087825 | 0.0087823 | 0.0087825 | 0.98825 | -0.22549 | 0.98839 | -0.2227 | 2.4128
15 | 0.010506 | 0.0026336 | -0.010504 | -0.0026326 | 2.0182e-06 | 1.0268e-06 | 0.015975 | 0.015975 | 0.015975 | 0.9786 | -0.41181 | 0.9784 | -0.41585 | 4.3888
16 | -0.010506 | -0.0026336 | 0.01051 | 0.0026356 | 3.9233e-06 | 1.9956e-06 | 0.015975 | 0.015975 | 0.015975 | 0.9786 | -0.41181 | 0.979 | -0.40398 | 4.3888
17 | -0.034022 | -0.0085364 | 0.034072 | 0.0085677 | 4.9814e-05 | 3.1255e-05 | 0.051715 | 0.051714 | 0.051715 | 0.979 | -0.40398 | 0.98057 | -0.37332 | 14.2073
18 | 0.023512 | 0.0059008 | -0.023506 | -0.0058973 | 5.6509e-06 | 3.4683e-06 | 0.035739 | 0.035739 | 0.035739 | 0.979 | -0.40398 | 0.97874 | -0.40902 | 9.8185
19 | -0.0072073 | -0.0018062 | 0.0072075 | 0.0018063 | 1.878e-07 | 6.805e-08 | 0.010972 | 0.010972 | 0.010972 | 0.97744 | -0.43478 | 0.97747 | -0.43423 | 3.0143
20 | 0.0072073 | 0.0018062 | -0.0072063 | -0.0018059 | 9.4445e-07 | 3.4227e-07 | 0.010972 | 0.010972 | 0.010972 | 0.97744 | -0.43478 | 0.9773 | -0.43753 | 3.0143
21 | -0.012147 | -0.0030442 | 0.012149 | 0.0030452 | 1.8233e-06 | 9.8863e-07 | 0.018491 | 0.018491 | 0.018491 | 0.97747 | -0.43423 | 0.97763 | -0.43108 | 5.08
22 | 0.0036897 | 0.00092452 | -0.0036894 | -0.00092464 | 2.8727e-07 | -1.2028e-07 | 0.0056177 | 0.0056178 | 0.0056178 | 0.9773 | -0.43753 | 0.97722 | -0.43916 | 1.5434
23 | -0.010318 | -0.0025857 | 0.01032 | 0.0025869 | 2.524e-06 | 1.2578e-06 | 0.015533 | 0.015533 | 0.015533 | 0.98839 | -0.2227 | 0.98866 | -0.21757 | 4.2674
24 | -0.047071 | -0.011826 | 0.047084 | 0.011834 | 1.2801e-05 | 8.1047e-06 | 0.070672 | 0.070672 | 0.070672 | 0.99124 | -0.16752 | 0.99153 | -0.16182 | 19.4153
25 | 0.047071 | 0.011826 | -0.047068 | -0.011823 | 3.4362e-06 | 2.1755e-06 | 0.070672 | 0.070672 | 0.070672 | 0.99124 | -0.16752 | 0.99116 | -0.16905 | 19.4153
26 | -0.051177 | -0.01286 | 0.0512 | 0.012874 | 2.2953e-05 | 1.4556e-05 | 0.076815 | 0.076814 | 0.076815 | 0.99153 | -0.16182 | 0.99202 | -0.15243 | 21.1029
27 | 0.04272 | 0.010734 | -0.042693 | -0.010717 | 2.7086e-05 | 1.7109e-05 | 0.064144 | 0.064144 | 0.064144 | 0.99116 | -0.16905 | 0.99047 | -0.18234 | 17.6221
28 | 0.013416 | 0.0033632 | -0.013415 | -0.0033627 | 8.3463e-07 | 4.6311e-07 | 0.020116 | 0.020116 | 0.020116 | 0.99237 | -0.14517 | 0.9923 | -0.14648 | 5.5265
29 | -0.21266 | -0.054089 | 0.2129 | 0.054245 | 0.00024569 | 0.00015591 | 0.31915 | 0.31915 | 0.31915 | 0.99237 | -0.14517 | 0.99362 | -0.12122 | 21.9199
30 | 0.19924 | 0.050725 | -0.19907 | -0.050613 | 0.00017769 | 0.00011263 | 0.29904 | 0.29904 | 0.29904 | 0.99237 | -0.14517 | 0.99141 | -0.16368 | 20.5383
31 | 0.0088432 | 0.002217 | -0.0088422 | -0.0022166 | 1.0164e-06 | 4.5143e-07 | 0.013261 | 0.013261 | 0.013261 | 0.9923 | -0.14648 | 0.99218 | -0.14889 | 3.6432
32 | -0.219 | -0.055772 | 0.21921 | 0.055904 | 0.00020646 | 0.00013108 | 0.32828 | 0.32828 | 0.32828 | 0.99362 | -0.12122 | 0.99465 | -0.1017 | 22.5469
33 | 0.023483 | 0.0058887 | -0.023481 | -0.0058877 | 1.6026e-06 | 9.8131e-07 | 0.035247 | 0.035247 | 0.035247 | 0.99141 | -0.16368 | 0.99133 | -0.16512 | 9.6831
34 | 0.17558 | 0.044724 | -0.17546 | -0.044644 | 0.00012748 | 8.0578e-05 | 0.26379 | 0.26379 | 0.26379 | 0.99141 | -0.16368 | 0.99062 | -0.17875 | 18.1176
35 | -0.22719 | -0.057628 | 0.22726 | 0.057674 | 7.2777e-05 | 4.6229e-05 | 0.34013 | 0.34013 | 0.34013 | 0.99461 | -0.10239 | 0.99496 | -0.095735 | 23.3608
36 | 0.15775 | 0.040126 | -0.15765 | -0.040063 | 0.00010041 | 6.3264e-05 | 0.23622 | 0.23622 | 0.23622 | 0.99461 | -0.10239 | 0.99392 | -0.11561 | 16.2241
37 | 0.069432 | 0.017502 | -0.069378 | -0.017467 | 5.4455e-05 | 3.4677e-05 | 0.10391 | 0.10391 | 0.10391 | 0.99461 | -0.10239 | 0.99376 | -0.1188 | 28.5472
38 | -0.45155 | -0.11488 | 0.45248 | 0.11547 | 0.00093333 | 0.0005962 | 0.67592 | 0.67592 | 0.67592 | 0.99496 | -0.095735 | 0.99721 | -0.052942 | 46.4233
39 | 0.22429 | 0.057202 | -0.22422 | -0.057161 | 6.4569e-05 | 4.1007e-05 | 0.33579 | 0.33579 | 0.33579 | 0.99496 | -0.095735 | 0.99465 | -0.1017 | 23.0624
40 | 0.15116 | 0.038435 | -0.15114 | -0.038425 | 1.6231e-05 | 1.0213e-05 | 0.2265 | 0.2265 | 0.2265 | 0.99392 | -0.11561 | 0.9938 | -0.11784 | 15.5564
41 | 0.063738 | 0.016054 | -0.063698 | -0.016028 | 3.9921e-05 | 2.5398e-05 | 0.095467 | 0.095467 | 0.095467 | 0.99376 | -0.1188 | 0.99308 | -0.13191 | 26.2272
42 | 0.0088422 | 0.0022166 | -0.0088397 | -0.0022154 | 2.5273e-06 | 1.1227e-06 | 0.013261 | 0.013261 | 0.013261 | 0.99218 | -0.14889 | 0.99187 | -0.15489 | 3.6432
43 | -0.45248 | -0.11547 | 0.45364 | 0.11621 | 0.0011605 | 0.00074132 | 0.67592 | 0.67592 | 0.67592 | 0.99721 | -0.052942 | 1 | 0 | 46.4232
44 | -0.16635 | -0.042268 | 0.16643 | 0.042315 | 7.4686e-05 | 4.7147e-05 | 0.25048 | 0.25048 | 0.25048 | 0.98904 | -0.20904 | 0.98953 | -0.19972 | 17.2035
45 | 0.16635 | 0.042268 | -0.16632 | -0.042247 | 3.3087e-05 | 2.0887e-05 | 0.25048 | 0.25048 | 0.25048 | 0.98904 | -0.20904 | 0.98883 | -0.21317 | 17.2035
46 | -0.17051 | -0.043338 | 0.17061 | 0.043405 | 0.00010583 | 6.6851e-05 | 0.25662 | 0.25662 | 0.25662 | 0.98953 | -0.19972 | 0.9902 | -0.18684 | 17.6251
47 | 0.0024318 | 0.0006065 | -0.0024313 | -0.0006075 | 5.2334e-07 | -1.0021e-06 | 0.0036584 | 0.0036589 | 0.0036589 | 0.98883 | -0.21317 | 0.98859 | -0.2177 | 1.0052
48 | 0.16389 | 0.041641 | -0.16376 | -0.04156 | 0.00012742 | 8.0403e-05 | 0.24682 | 0.24683 | 0.24683 | 0.98883 | -0.21317 | 0.98799 | -0.22933 | 16.9523
49 | 0.0037636 | 0.00094323 | -0.0037636 | -0.00094324 | 2.8303e-08 | -1.0724e-08 | 0.0057285 | 0.0057285 | 0.0057285 | 0.97762 | -0.43114 | 0.97761 | -0.4313 | 1.5738
50 | -0.0037636 | -0.00094323 | 0.0037637 | 0.00094317 | 1.464e-07 | -5.5481e-08 | 0.0057285 | 0.0057284 | 0.0057285 | 0.97762 | -0.43114 | 0.97766 | -0.43033 | 1.5738
51 | 0.0091474 | 0.0022932 | -0.0091446 | -0.0022919 | 2.7886e-06 | 1.3038e-06 | 0.013923 | 0.013923 | 0.013923 | 0.97766 | -0.43033 | 0.97733 | -0.43673 | 3.825
52 | -0.012911 | -0.0032364 | 0.012912 | 0.0032369 | 1.0406e-06 | 5.7585e-07 | 0.019651 | 0.019651 | 0.019651 | 0.97766 | -0.43033 | 0.97774 | -0.42864 | 5.3987
53 | 0.0091446 | 0.0022919 | -0.0091434 | -0.0022913 | 1.1622e-06 | 5.4349e-07 | 0.013923 | 0.013923 | 0.013923 | 0.97733 | -0.43673 | 0.9772 | -0.43939 | 3.825
54 | -0.016305 | -0.0040873 | 0.016314 | 0.0040924 | 8.8186e-06 | 5.1646e-06 | 0.024815 | 0.024815 | 0.024815 | 0.97774 | -0.42864 | 0.97832 | -0.41729 | 6.8172
55 | 0.0024313 | 0.0006075 | -0.0024305 | -0.00060913 | 8.5245e-07 | -1.6302e-06 | 0.0036589 | 0.0036597 | 0.0036597 | 0.98859 | -0.2177 | 0.98822 | -0.22507 | 1.0054
56 | 0.1604 | 0.040718 | -0.16021 | -0.040602 | 0.00018347 | 0.00011571 | 0.24176 | 0.24176 | 0.24176 | 0.98799 | -0.22933 | 0.98675 | -0.25313 | 16.6045
57 | 0.097417 | 0.024521 | -0.097222 | -0.024397 | 0.00019524 | 0.00012465 | 0.14787 | 0.14787 | 0.14787 | 0.98057 | -0.37332 | 0.97842 | -0.41534 | 40.6234
58 | -0.13149 | -0.033089 | 0.1315 | 0.033096 | 1.0979e-05 | 7.0174e-06 | 0.19958 | 0.19958 | 0.19958 | 0.98057 | -0.37332 | 0.98065 | -0.37157 | 54.8306
59 | 0.019711 | 0.0049461 | -0.019707 | -0.004944 | 3.3715e-06 | 2.032e-06 | 0.029969 | 0.029969 | 0.029969 | 0.97874 | -0.40902 | 0.97856 | -0.41261 | 8.2332
60 | 0.0072966 | 0.0018285 | -0.0072961 | -0.0018283 | 4.7683e-07 | 1.7614e-07 | 0.011111 | 0.011111 | 0.011111 | 0.9772 | -0.43939 | 0.97713 | -0.44077 | 3.0524
61 | 0.0033783 | 0.00084657 | -0.0033782 | -0.00084664 | 9.7184e-08 | -6.0985e-08 | 0.005139 | 0.005139 | 0.005139 | 0.9782 | -0.41977 | 0.97817 | -0.42038 | 1.4118
62 | 0.0033782 | 0.00084664 | -0.0033782 | -0.00084665 | 2.9959e-08 | -1.8798e-08 | 0.005139 | 0.0051391 | 0.0051391 | 0.97817 | -0.42038 | 0.97816 | -0.42056 | 1.4118
63 | -0.016314 | -0.0040924 | 0.016317 | 0.0040946 | 3.6433e-06 | 2.1335e-06 | 0.024815 | 0.024814 | 0.024815 | 0.97832 | -0.41729 | 0.97856 | -0.41261 | 6.8172
64 | 0.0033897 | 0.00084946 | -0.0033896 | -0.00084952 | 9.777e-08 | -6.0702e-08 | 0.0051545 | 0.0051545 | 0.0051545 | 0.97856 | -0.41261 | 0.97853 | -0.41321 | 1.4161
65 | 0.13187 | 0.033334 | -0.1315 | -0.033096 | 0.00037226 | 0.00023793 | 0.19958 | 0.19958 | 0.19958 | 0.98369 | -0.31252 | 0.98065 | -0.37157 | 54.8306
66 | 0.01574 | 0.0039458 | -0.015737 | -0.003944 | 3.1385e-06 | 1.8213e-06 | 0.02381 | 0.02381 | 0.02381 | 0.98369 | -0.31252 | 0.98347 | -0.31671 | 6.5412
67 | 0.0015578 | 0.00038885 | -0.0015576 | -0.00038973 | 1.6112e-07 | -8.7929e-07 | 0.0023559 | 0.0023563 | 0.0023563 | 0.98369 | -0.31252 | 0.98358 | -0.3147 | 0.64733
68 | -0.14917 | -0.037669 | 0.14942 | 0.037827 | 0.00024898 | 0.00015869 | 0.22575 | 0.22575 | 0.22575 | 0.98369 | -0.31252 | 0.98548 | -0.27775 | 31.0095
69 | 0.0015576 | 0.00038973 | -0.0015575 | -0.00039036 | 1.139e-07 | -6.2128e-07 | 0.0023563 | 0.0023565 | 0.0023565 | 0.98358 | -0.3147 | 0.9835 | -0.31623 | 0.6474
70 | -0.15321 | -0.038778 | 0.15339 | 0.038892 | 0.00018126 | 0.00011417 | 0.23148 | 0.23147 | 0.23148 | 0.98548 | -0.27775 | 0.98675 | -0.25313 | 15.898
71 | 0.040147 | 0.010093 | -0.040095 | -0.010059 | 5.2352e-05 | 3.3036e-05 | 0.061068 | 0.061068 | 0.061068 | 0.97842 | -0.41534 | 0.97703 | -0.44269 | 16.777
72 | 0.024365 | 0.0061202 | -0.024354 | -0.0061138 | 1.0444e-05 | 6.4168e-06 | 0.036609 | 0.036609 | 0.036609 | 0.99047 | -0.18234 | 0.99001 | -0.19133 | 10.0573
73 | 0.018328 | 0.0045964 | -0.018324 | -0.0045938 | 4.3065e-06 | 2.5613e-06 | 0.027536 | 0.027536 | 0.027536 | 0.99047 | -0.18234 | 0.99022 | -0.18727 | 7.5648
74 | 0.024354 | 0.0061138 | -0.024335 | -0.0061022 | 1.8963e-05 | 1.1651e-05 | 0.036609 | 0.036609 | 0.036609 | 0.99001 | -0.19133 | 0.98917 | -0.20767 | 10.0574
75 | 0.014459 | 0.0036253 | -0.014455 | -0.0036227 | 4.7002e-06 | 2.6667e-06 | 0.021729 | 0.021729 | 0.021729 | 0.99022 | -0.18727 | 0.98987 | -0.1941 | 5.9694
76 | 0.017344 | 0.00435 | -0.017336 | -0.0043452 | 8.183e-06 | 4.8259e-06 | 0.026092 | 0.026092 | 0.026092 | 0.98917 | -0.20767 | 0.98866 | -0.21757 | 7.1682
77 | 0.023481 | 0.0058877 | -0.023473 | -0.0058829 | 7.7753e-06 | 4.7611e-06 | 0.035247 | 0.035247 | 0.035247 | 0.99133 | -0.16512 | 0.99097 | -0.17207 | 9.6832
78 | 0.17068 | 0.043447 | -0.17061 | -0.043405 | 6.6542e-05 | 4.2032e-05 | 0.25662 | 0.25662 | 0.25662 | 0.99062 | -0.17875 | 0.9902 | -0.18684 | 17.6251
79 | 0.020514 | 0.005143 | -0.020509 | -0.0051403 | 4.3272e-06 | 2.607e-06 | 0.030525 | 0.030525 | 0.030525 | 1 | 0 | 0.99977 | -0.0044278 | 8.3861
80 | 0.011354 | 0.0028459 | -0.011353 | -0.0028454 | 8.6394e-07 | 4.4715e-07 | 0.016899 | 0.016899 | 0.016899 | 0.99977 | -0.0044278 | 0.99969 | -0.006025 | 4.6427
81 | -0.00683 | -0.0017117 | 0.00683 | 0.0017118 | 1.2147e-08 | 3.6648e-09 | 0.010166 | 0.010166 | 0.010166 | 0.99968 | -0.0060623 | 0.99969 | -0.006025 | 2.7929
82 | 0.14456 | 0.036774 | -0.14446 | -0.036713 | 9.6504e-05 | 6.1478e-05 | 0.21664 | 0.21664 | 0.21664 | 0.9938 | -0.11784 | 0.99308 | -0.1317 | 29.7579
83 | 0.059613 | 0.015004 | -0.059583 | -0.014985 | 2.9696e-05 | 1.8877e-05 | 0.089345 | 0.089345 | 0.089345 | 0.99308 | -0.13191 | 0.99254 | -0.14233 | 24.5454
84 | 0.074542 | 0.018831 | -0.074435 | -0.018763 | 0.00010683 | 6.8086e-05 | 0.11283 | 0.11283 | 0.11283 | 0.98358 | -0.31479 | 0.98204 | -0.34474 | 30.996
85 | -0.088804 | -0.022407 | 0.088985 | 0.022522 | 0.00018156 | 0.00011586 | 0.1344 | 0.1344 | 0.1344 | 0.98358 | -0.31479 | 0.98578 | -0.27219 | 36.9234
86 | 0.014262 | 0.0035751 | -0.014259 | -0.0035736 | 2.6789e-06 | 1.5198e-06 | 0.021576 | 0.021576 | 0.021576 | 0.98358 | -0.31479 | 0.98338 | -0.31874 | 5.9275
87 | 0.064438 | 0.016258 | -0.064356 | -0.016205 | 8.1985e-05 | 5.2181e-05 | 0.097677 | 0.097677 | 0.097677 | 0.98204 | -0.34474 | 0.98068 | -0.37135 | 26.8343
88 | 0.0099975 | 0.0025058 | -0.0099974 | -0.0025057 | 1.408e-07 | 6.9411e-08 | 0.015149 | 0.015149 | 0.015149 | 0.98204 | -0.34474 | 0.98203 | -0.34503 | 4.1617
89 | -0.094699 | -0.023954 | 0.094827 | 0.024036 | 0.00012835 | 8.1929e-05 | 0.14303 | 0.14303 | 0.14303 | 0.98578 | -0.27219 | 0.98724 | -0.24399 | 39.2927
90 | 0.0068516 | 0.0017171 | -0.0068508 | -0.0017169 | 7.8745e-07 | 2.5615e-07 | 0.010368 | 0.010368 | 0.010368 | 0.98338 | -0.31874 | 0.98325 | -0.32115 | 2.8483
91 | 0.0062784 | 0.0015735 | -0.0062774 | -0.0015733 | 1.0442e-06 | 2.6654e-07 | 0.0094381 | 0.0094382 | 0.0094382 | 0.98987 | -0.1941 | 0.98969 | -0.19759 | 2.5929
92 | 0.0062897 | 0.0015763 | -0.0062893 | -0.0015762 | 4.0156e-07 | 1.0849e-07 | 0.0095407 | 0.0095407 | 0.0095407 | 0.98097 | -0.36565 | 0.9809 | -0.36699 | 2.6211
93 | -0.0062897 | -0.0015763 | 0.0062946 | 0.0015777 | 4.9255e-06 | 1.3289e-06 | 0.0095407 | 0.00954 | 0.0095407 | 0.98097 | -0.36565 | 0.98181 | -0.34922 | 2.6211
94 | -0.0062946 | -0.0015777 | 0.0062947 | 0.0015777 | 1.2853e-07 | 3.4632e-08 | 0.00954 | 0.00954 | 0.00954 | 0.98181 | -0.34922 | 0.98183 | -0.34879 | 2.6209
95 | -0.0062947 | -0.0015777 | 0.0062958 | 0.001578 | 1.1272e-06 | 3.0363e-07 | 0.00954 | 0.0095398 | 0.00954 | 0.98183 | -0.34879 | 0.98203 | -0.34503 | 2.6209
96 | -0.0023478 | -0.00058842 | 0.0023479 | 0.00058836 | 3.0819e-08 | -6.2833e-08 | 0.0035532 | 0.0035532 | 0.0035532 | 0.98321 | -0.32195 | 0.98323 | -0.32168 | 0.97617
97 | -0.004531 | -0.0011355 | 0.0045311 | 0.0011355 | 1.1402e-07 | -9.0434e-09 | 0.0068571 | 0.0068571 | 0.0068571 | 0.98323 | -0.32168 | 0.98325 | -0.32115 | 1.8838
98 | -0.017191 | -0.004309 | 0.017194 | 0.0043109 | 3.1329e-06 | 1.852e-06 | 0.026167 | 0.026166 | 0.026167 | 0.97763 | -0.43108 | 0.97782 | -0.42725 | 7.1886
99 | -0.055384 | -0.013923 | 0.05541 | 0.01394 | 2.6721e-05 | 1.6968e-05 | 0.08309 | 0.08309 | 0.08309 | 0.99202 | -0.15243 | 0.99254 | -0.14233 | 22.8269
100 | 0.005822 | 0.0014589 | -0.0058217 | -0.0014588 | 2.7193e-07 | 5.8487e-08 | 0.0088659 | 0.008866 | 0.008866 | 0.97713 | -0.44077 | 0.97708 | -0.44175 | 2.4357
101 | 0.059611 | 0.015016 | -0.059566 | -0.014988 | 4.4205e-05 | 2.8109e-05 | 0.090477 | 0.090477 | 0.090477 | 0.98068 | -0.37135 | 0.97988 | -0.38686 | 24.8562
102 | 0.0047453 | 0.0011891 | -0.0047447 | -0.0011891 | 6.0817e-07 | -5.4058e-09 | 0.0072002 | 0.0072004 | 0.0072004 | 0.98068 | -0.37135 | 0.98054 | -0.37404 | 1.9781
103 | -0.098095 | -0.024855 | 0.098147 | 0.024888 | 5.162e-05 | 3.2956e-05 | 0.14795 | 0.14795 | 0.14795 | 0.98724 | -0.24399 | 0.9878 | -0.23304 | 40.646
104 | 0.056476 | 0.014214 | -0.056409 | -0.014171 | 6.7086e-05 | 4.2629e-05 | 0.085784 | 0.085784 | 0.085784 | 0.97988 | -0.38686 | 0.97861 | -0.41175 | 23.567
105 | 0.0030905 | 0.00077441 | -0.0030904 | -0.00077452 | 1.197e-07 | -1.0594e-07 | 0.0046931 | 0.0046931 | 0.0046931 | 0.97988 | -0.38686 | 0.97984 | -0.38768 | 1.2893
106 | -0.1032 | -0.026154 | 0.10323 | 0.026175 | 3.2164e-05 | 2.054e-05 | 0.15556 | 0.15556 | 0.15556 | 0.9878 | -0.23304 | 0.98814 | -0.22655 | 42.7364
107 | 0.05314 | 0.013352 | -0.0531 | -0.013327 | 3.9292e-05 | 2.4945e-05 | 0.080813 | 0.080813 | 0.080813 | 0.97861 | -0.41175 | 0.97782 | -0.42725 | 22.2014
108 | 0.034132 | 0.0085714 | -0.034109 | -0.0085568 | 2.3123e-05 | 1.4513e-05 | 0.051947 | 0.051947 | 0.051947 | 0.97782 | -0.42725 | 0.9771 | -0.44146 | 14.2711
109 | 0.034109 | 0.0085568 | -0.0341 | -0.0085514 | 8.7206e-06 | 5.4733e-06 | 0.051947 | 0.051947 | 0.051947 | 0.9771 | -0.44146 | 0.97683 | -0.44683 | 14.2711
110 | 0.0287 | 0.007198 | -0.02869 | -0.007192 | 9.5455e-06 | 5.9425e-06 | 0.043721 | 0.043721 | 0.043721 | 0.97683 | -0.44683 | 0.97647 | -0.45381 | 12.0112
111 | 0.015011 | 0.0037631 | -0.015008 | -0.0037614 | 2.8413e-06 | 1.6375e-06 | 0.022879 | 0.022879 | 0.022879 | 0.97631 | -0.45704 | 0.9761 | -0.46102 | 6.2855
112 | -0.015011 | -0.0037631 | 0.015013 | 0.0037644 | 2.3137e-06 | 1.3334e-06 | 0.022879 | 0.022879 | 0.022879 | 0.97631 | -0.45704 | 0.97647 | -0.45381 | 6.2855
113 | 0.0037375 | 0.0009366 | -0.0037373 | -0.00093666 | 1.4293e-07 | -5.5503e-08 | 0.0056954 | 0.0056954 | 0.0056954 | 0.97647 | -0.45381 | 0.97643 | -0.45461 | 1.5647
114 | -0.0053984 | -0.001353 | 0.0053985 | 0.001353 | 1.3205e-07 | 1.4978e-08 | 0.0080918 | 0.0080917 | 0.0080918 | 0.99272 | -0.13872 | 0.99274 | -0.13821 | 2.223
115 | -0.0093198 | -0.0023357 | 0.0093204 | 0.002336 | 6.372e-07 | 2.9522e-07 | 0.013969 | 0.013969 | 0.013969 | 0.99274 | -0.13821 | 0.99282 | -0.13677 | 3.8377
116 | -0.01207 | -0.0030252 | 0.012071 | 0.0030259 | 1.2845e-06 | 6.867e-07 | 0.018091 | 0.018091 | 0.018091 | 0.99282 | -0.13677 | 0.99293 | -0.13454 | 4.97
117 | -0.018391 | -0.0046097 | 0.018391 | 0.0046099 | 3.8492e-07 | 2.2887e-07 | 0.027561 | 0.027561 | 0.027561 | 0.99293 | -0.13454 | 0.99296 | -0.1341 | 7.5717
118 | -0.024398 | -0.0061154 | 0.024401 | 0.0061172 | 2.7869e-06 | 1.7117e-06 | 0.036563 | 0.036563 | 0.036563 | 0.99296 | -0.1341 | 0.99308 | -0.1317 | 10.0448
119 | 0.12006 | 0.030596 | -0.11992 | -0.030504 | 0.00014381 | 9.1883e-05 | 0.18007 | 0.18008 | 0.18008 | 0.99308 | -0.1317 | 0.99178 | -0.15656 | 49.4712
120 | -0.10654 | -0.027005 | 0.10664 | 0.027064 | 9.1968e-05 | 5.8738e-05 | 0.16055 | 0.16055 | 0.16055 | 0.98814 | -0.22655 | 0.98907 | -0.20861 | 44.1072
121 | -0.10971 | -0.027835 | 0.10979 | 0.027886 | 7.9852e-05 | 5.1005e-05 | 0.16518 | 0.16518 | 0.16518 | 0.98907 | -0.20861 | 0.98986 | -0.19348 | 45.3789
122 | -0.11385 | -0.028903 | 0.11387 | 0.028913 | 1.6008e-05 | 1.0227e-05 | 0.17128 | 0.17128 | 0.17128 | 0.98986 | -0.19348 | 0.99001 | -0.19056 | 47.0543
123 | -0.11674 | -0.029635 | 0.11694 | 0.029757 | 0.00019133 | 0.00012224 | 0.17561 | 0.17561 | 0.17561 | 0.99001 | -0.19056 | 0.99178 | -0.15656 | 48.2433
124 | -0.0014246 | -0.00035704 | 0.0014246 | 0.00035694 | 1.6058e-08 | -1.0363e-07 | 0.0021698 | 0.0021697 | 0.0021698 | 0.977 | -0.4432 | 0.97702 | -0.44296 | 0.59609
125 | -0.0028536 | -0.00071508 | 0.0028537 | 0.000715 | 6.5163e-08 | -7.3509e-08 | 0.0043461 | 0.004346 | 0.0043461 | 0.97702 | -0.44296 | 0.97704 | -0.44248 | 1.194
126 | -0.0043198 | -0.0010824 | 0.0043199 | 0.0010824 | 1.5088e-07 | -1.9862e-08 | 0.0065789 | 0.0065788 | 0.0065789 | 0.97704 | -0.44248 | 0.97708 | -0.44175 | 1.8074

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.47581 | 0.12136

## res_load
| p_mw | q_mvar
0 | 0.0047596 | 0.0011929
1 | 0.0047511 | 0.0011907
2 | 0.0097094 | 0.0024334
3 | 0.0069934 | 0.0017527
4 | 0.010224 | 0.0025624
5 | 0.0036251 | 0.00090854
6 | 0.0037405 | 0.00093745
7 | 0.0058293 | 0.001461
8 | 0.003384 | 0.00084811
9 | 0.0049394 | 0.0012379
10 | 0.0035167 | 0.00088136
11 | 0.0044842 | 0.0011239
12 | 0.0040932 | 0.0010259
13 | 0.0043479 | 0.0010897
14 | 0.0045715 | 0.0011457
15 | 0.0060965 | 0.0015279
16 | 0.006493 | 0.0016273
17 | 0.0056398 | 0.0014135
18 | 0.0088397 | 0.0022154
19 | 0.0050175 | 0.0012575
20 | 0.0040822 | 0.0010231
21 | 0.0037636 | 0.00094324
22 | 0.0033929 | 0.00085033
23 | 0.0033621 | 0.00084263
24 | 0.0037956 | 0.00095128
25 | 0.0018468 | 0.00046286
26 | 0.0033782 | 0.00084665
27 | 0.015737 | 0.003944
28 | 0.0037923 | 0.00095045
29 | 0.0024305 | 0.00060913
30 | 0.0015575 | 0.00039036
31 | 0.057075 | 0.014304
32 | 0.0038644 | 0.00096852
33 | 0.0069912 | 0.0017522
34 | 0.0047741 | 0.0011965
35 | 0.023473 | 0.0058829
36 | 0.009155 | 0.0022945
37 | 0.0068221 | 0.0017098
38 | 0.00683 | 0.0017117
39 | 0.0045235 | 0.0011337
40 | 0.006588 | 0.0016511
41 | 0.0040857 | 0.001024
42 | 0.0057134 | 0.0014319
43 | 0.0074074 | 0.0018565
44 | 0.0081761 | 0.0020491
45 | 0.0070155 | 0.0017582
46 | 0.0062893 | 0.0015762
47 | 0.0062774 | 0.0015733
48 | 0.0023478 | 0.00058842
49 | 0.0021831 | 0.00054714
50 | 0.0050426 | 0.0012638
51 | 0.0036894 | 0.00092464
52 | 0.0041837 | 0.0010485
53 | 0.0014741 | 0.00036944
54 | 0.0033896 | 0.00084952
55 | 0.0023197 | 0.00058137
56 | 0.0037015 | 0.00092769
57 | 0.0032681 | 0.00081907
58 | 0.0047447 | 0.0011891
59 | 0.0050512 | 0.0012659
60 | 0.0030904 | 0.00077452
61 | 0.0032691 | 0.00081933
62 | 0.0017741 | 0.00044464
63 | 0.0054001 | 0.0013534
64 | 0.015008 | 0.0037614
65 | 0.0099393 | 0.002491
66 | 0.0053984 | 0.001353
67 | 0.0039213 | 0.00098277
68 | 0.0027498 | 0.00068916
69 | 0.0063194 | 0.0015838
70 | 0.0060072 | 0.0015055
71 | 0.0041725 | 0.0010457
72 | 0.0033136 | 0.00083046
73 | 0.003077 | 0.00077116
74 | 0.0040568 | 0.0010167
75 | 0.0028795 | 0.00072168
76 | 0.002979 | 0.00074661
77 | 0.0037373 | 0.00093666
78 | 0.0014246 | 0.00035704
79 | 0.001429 | 0.00035814
80 | 0.0014661 | 0.00036744
81 | 0.0015018 | 0.00037639

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1