## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-613_1_4_node_4 | 0.4 | n |  | TRUE
1 | bus_LV_261-613_1_4_node_54 | 0.4 | n |  | TRUE
2 | bus_LV_261-613_1_4_node_11 | 0.4 | n |  | TRUE
3 | bus_LV_261-613_1_4_node_12 | 0.4 | n |  | TRUE
4 | bus_LV_261-613_1_4_node_13 | 0.4 | n |  | TRUE
5 | bus_LV_261-613_1_4_node_15 | 0.4 | n |  | TRUE
6 | bus_LV_261-613_1_4_node_48 | 0.4 | n |  | TRUE
7 | bus_LV_261-613_1_4_node_16 | 0.4 | n |  | TRUE
8 | bus_LV_261-613_1_4_node_45 | 0.4 | n |  | TRUE
9 | bus_LV_261-613_1_4_node_46 | 0.4 | n |  | TRUE
10 | bus_LV_261-613_1_4_node_19 | 0.4 | n |  | TRUE
11 | bus_LV_261-613_1_4_node_20 | 0.4 | n |  | TRUE
12 | bus_LV_261-613_1_4_node_47 | 0.4 | n |  | TRUE
13 | bus_LV_261-613_1_4_node_55 | 0.4 | n |  | TRUE
14 | bus_LV_261-613_1_4_node_32 | 0.4 | n |  | TRUE
15 | bus_LV_261-613_1_4_node_57 | 0.4 | n |  | TRUE
16 | bus_LV_261-613_1_4_node_21 | 0.4 | n |  | TRUE
17 | bus_LV_261-613_1_4_node_52 | 0.4 | n |  | TRUE
18 | bus_LV_261-613_1_4_node_51 | 0.4 | n |  | TRUE
19 | bus_LV_261-613_1_4_node_22 | 0.4 | n |  | TRUE
20 | bus_LV_261-613_1_4_node_56 | 0.4 | n |  | TRUE
21 | bus_LV_261-613_1_4_node_23 | 0.4 | n |  | TRUE
22 | bus_LV_261-613_1_4_node_53 | 0.4 | n |  | TRUE
23 | bus_LV_261-613_1_4_node_33 | 0.4 | n |  | TRUE
24 | bus_LV_261-613_1_4_node_40 | 0.4 | n |  | TRUE
25 | bus_LV_261-613_1_4_node_42 | 0.4 | n |  | TRUE
26 | bus_LV_261-613_1_4_node_41 | 0.4 | n |  | TRUE
27 | bus_LV_261-613_1_4_node_43 | 0.4 | n |  | TRUE
28 | bus_LV_261-613_1_4_node_44 | 0.4 | n |  | TRUE
29 | bus_LV_261-613_1_4_node_49 | 0.4 | n |  | TRUE
30 | bus_LV_261-613_1_4_node_50 | 0.4 | n |  | TRUE
31 | bus_MV_389_0_node_166 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-613_1_4_load_4 | 0 | 0.0096752 | 0.0024248 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-613_1_4_load_54 | 1 | 0.025611 | 0.0064187 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-613_1_4_load_11 | 2 | 0.011919 | 0.0029873 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-613_1_4_load_12 | 3 | 0.0084474 | 0.0021171 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-613_1_4_load_15 | 5 | 0.0087885 | 0.0022026 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-613_1_4_load_48 | 6 | 0.0087888 | 0.0022027 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-613_1_4_load_45 | 8 | 0.0067295 | 0.0016866 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-613_1_4_load_46 | 9 | 0.0034056 | 0.00085352 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-613_1_4_load_55 | 13 | 0.026123 | 0.0065469 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-613_1_4_load_57 | 15 | 0.025117 | 0.006295 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-613_1_4_load_52 | 17 | 0.01046 | 0.0026215 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-613_1_4_load_51 | 18 | 0.018389 | 0.0046088 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-613_1_4_load_56 | 20 | 0.0087011 | 0.0021807 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-613_1_4_load_53 | 22 | 0.029391 | 0.007366 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-613_1_4_load_33 | 23 | 0.056686 | 0.014207 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-613_1_4_load_40 | 24 | 0.0067678 | 0.0016962 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-613_1_4_load_41 | 26 | 0.0025572 | 0.00064089 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_261-613_1_4_load_43 | 27 | 0.0025024 | 0.00062715 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_261-613_1_4_load_44 | 28 | 0.0098985 | 0.0024808 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_261-613_1_4_load_49 | 29 | 0.0030985 | 0.00077655 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_261-613_1_4_load_50 | 30 | 0.023732 | 0.0059478 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 11 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-613_1_4_line_0 |  | 0 | 1 | 0.067839 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-613_1_4_line_1 |  | 1 | 13 | 0.020193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-613_1_4_line_2 |  | 2 | 3 | 0.0031697 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-613_1_4_line_3 |  | 2 | 4 | 0.0089648 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-613_1_4_line_4 |  | 4 | 5 | 0.0358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_261-613_1_4_line_5 |  | 5 | 6 | 0.019725 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_261-613_1_4_line_6 |  | 6 | 29 | 0.020812 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_261-613_1_4_line_7 |  | 7 | 8 | 0.014684 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_261-613_1_4_line_8 |  | 7 | 9 | 0.012019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_261-613_1_4_line_9 |  | 8 | 27 | 0.018246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_261-613_1_4_line_10 |  | 9 | 12 | 0.018466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_261-613_1_4_line_11 |  | 10 | 11 | 0.054579 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_261-613_1_4_line_12 |  | 10 | 12 | 0.003911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-613_1_4_line_13 |  | 10 | 13 | 0.01232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_261-613_1_4_line_14 |  | 11 | 14 | 0.077249 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
15 | LV_261-613_1_4_line_15 |  | 11 | 15 | 0.037285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_261-613_1_4_line_16 |  | 12 | 28 | 0.038287 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_261-613_1_4_line_17 |  | 14 | 23 | 0.055961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
18 | LV_261-613_1_4_line_18 |  | 16 | 17 | 0.0055567 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_261-613_1_4_line_19 |  | 16 | 18 | 0.010553 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_261-613_1_4_line_20 |  | 17 | 19 | 0.019003 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_261-613_1_4_line_21 |  | 18 | 30 | 0.023672 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_261-613_1_4_line_22 |  | 19 | 20 | 0.00581 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_261-613_1_4_line_23 |  | 19 | 21 | 0.039077 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_261-613_1_4_line_24 |  | 21 | 22 | 0.05457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
25 | LV_261-613_1_4_line_25 |  | 22 | 23 | 0.048302 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
26 | LV_261-613_1_4_line_26 |  | 24 | 25 | 0.013016 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_261-613_1_4_line_27 |  | 25 | 28 | 0.035301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_261-613_1_4_line_28 |  | 26 | 27 | 0.0072468 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_261-613_1_4_line_29 |  | 29 | 30 | 0.067086 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-613_1_4_trafo_20 | 0.63 MVA 20/0.4 kV | 31 | 11 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2678419.4419 | 1249394.7189 | 2678422.9565 | 1249399.5912 | 2678433.278 | 1249416.7513 | 2678447.24 | 1249440.0976 | 2678459.7454 | 1249432.5559
1 | 2678459.7454 | 1249432.5559 | 2678462.3948 | 1249430.9581 | 2678477.189 | 1249422.384
2 | 2678346.1007 | 1249568.4403 | 2678343.269 | 1249569.8645
3 | 2678354.1096 | 1249564.4125 | 2678346.1007 | 1249568.4403
4 | 2678354.1096 | 1249564.4125 | 2678386.2257 | 1249548.595
5 | 2678403.8395 | 1249539.7192 | 2678396.3669 | 1249543.6003 | 2678386.2257 | 1249548.595
6 | 2678403.8395 | 1249539.7192 | 2678417.8074 | 1249532.4646 | 2678422.1425 | 1249529.8308
7 | 2678517.7042 | 1249399.1115 | 2678510.2921 | 1249386.4351
8 | 2678517.7042 | 1249399.1115 | 2678507.2798 | 1249405.0932
9 | 2678510.2921 | 1249386.4351 | 2678501.082 | 1249370.6838
10 | 2678491.2638 | 1249414.2836 | 2678507.2798 | 1249405.0932
11 | 2678446.5927 | 1249445.6486 | 2678465.7894 | 1249433.4938 | 2678489.8522 | 1249419.9468 | 2678487.8479 | 1249416.2064
12 | 2678487.8479 | 1249416.2064 | 2678491.2638 | 1249414.2836
13 | 2678487.8479 | 1249416.2064 | 2678477.189 | 1249422.384
14 | 2678387.3637 | 1249495.3015 | 2678416.2735 | 1249468.6532 | 2678446.5927 | 1249445.6486
15 | 2678446.5927 | 1249445.6486 | 2678427.6162 | 1249413.5543
16 | 2678491.2638 | 1249414.2836 | 2678482.8108 | 1249399.7277 | 2678474.8561 | 1249379.8017
17 | 2678387.3637 | 1249495.3015 | 2678393.9075 | 1249493.7981 | 2678415.8748 | 1249473.6738 | 2678425.0664 | 1249466.0899 | 2678431.0027 | 1249461.4426
18 | 2678494.8482 | 1249460.6205 | 2678498.1635 | 1249456.1611
19 | 2678494.8482 | 1249460.6205 | 2678488.341 | 1249468.9279
20 | 2678509.5012 | 1249440.9112 | 2678498.1635 | 1249456.1611
21 | 2678488.341 | 1249468.9279 | 2678479.2025 | 1249480.5946 | 2678473.4743 | 1249487.343
22 | 2678509.5012 | 1249440.9112 | 2678506.6842 | 1249435.8257
23 | 2678509.5012 | 1249440.9112 | 2678519.3993 | 1249427.3212 | 2678522.7131 | 1249422.8396 | 2678525.4706 | 1249419.318 | 2678519.2065 | 1249408.8274
24 | 2678519.2065 | 1249408.8274 | 2678513.7622 | 1249411.6796 | 2678505.2984 | 1249415.6148 | 2678484.1115 | 1249427.5097 | 2678471.2119 | 1249434.7489
25 | 2678431.0027 | 1249461.4426 | 2678436.0306 | 1249457.5064 | 2678452.3899 | 1249446.3592 | 2678466.6905 | 1249437.2862 | 2678471.2119 | 1249434.7489
26 | 2678457.1861 | 1249349.3184 | 2678468.3547 | 1249342.6335
27 | 2678457.1861 | 1249349.3184 | 2678457.8323 | 1249350.6946 | 2678465.0894 | 1249362.6216 | 2678473.1271 | 1249375.4707 | 2678474.8561 | 1249379.8017
28 | 2678497.4241 | 1249364.4279 | 2678501.082 | 1249370.6838
29 | 2678422.1425 | 1249529.8308 | 2678429.5755 | 1249525.315 | 2678444.6221 | 1249515.7738 | 2678457.3867 | 1249504.6568 | 2678468.5252 | 1249493.1736 | 2678473.4743 | 1249487.343

## bus_geodata
| x | y | coords
0 | 2678419.4419 | 1249394.7189
1 | 2678459.7454 | 1249432.5559
2 | 2678346.1007 | 1249568.4403
3 | 2678343.269 | 1249569.8645
4 | 2678354.1096 | 1249564.4125
5 | 2678386.2257 | 1249548.595
6 | 2678403.8395 | 1249539.7192
7 | 2678517.7042 | 1249399.1115
8 | 2678510.2921 | 1249386.4351
9 | 2678507.2798 | 1249405.0932
10 | 2678487.848 | 1249416.2064
11 | 2678446.5927 | 1249445.6486
12 | 2678491.2638 | 1249414.2836
13 | 2678477.189 | 1249422.384
14 | 2678387.3637 | 1249495.3015
15 | 2678427.6162 | 1249413.5543
16 | 2678494.8482 | 1249460.6205
17 | 2678498.1635 | 1249456.1611
18 | 2678488.341 | 1249468.9279
19 | 2678509.5012 | 1249440.9112
20 | 2678506.6842 | 1249435.8257
21 | 2678519.2065 | 1249408.8274
22 | 2678471.2119 | 1249434.7489
23 | 2678431.0027 | 1249461.4426
24 | 2678468.3547 | 1249342.6335
25 | 2678457.1861 | 1249349.3184
26 | 2678497.4241 | 1249364.4279
27 | 2678501.082 | 1249370.6838
28 | 2678474.8561 | 1249379.8017
29 | 2678422.1425 | 1249529.8308
30 | 2678473.4743 | 1249487.343
31 | 2678489.8522 | 1249419.9468

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99342 | -0.12662 | 0.0096752 | 0.0024248
1 | 0.99402 | -0.11503 | 0.025611 | 0.0064187
2 | 0.97006 | -0.57861 | 0.011919 | 0.0029873
3 | 0.97003 | -0.5791 | 0.0084474 | 0.0021171
4 | 0.97023 | -0.57523 | 0 | 0
5 | 0.97091 | -0.56174 | 0.0087885 | 0.0022026
6 | 0.97145 | -0.55111 | 0.0087888 | 0.0022027
7 | 0.99486 | -0.098775 | 0 | 0
8 | 0.9947 | -0.10182 | 0.0067295 | 0.0016866
9 | 0.99499 | -0.09628 | 0.0034056 | 0.00085352
10 | 0.99536 | -0.089148 | 0 | 0
11 | 1 | 0 | -0.31245 | -0.079441
12 | 0.99524 | -0.091341 | 0 | 0
13 | 0.99467 | -0.10247 | 0.026123 | 0.0065469
14 | 0.99326 | -0.12771 | 0 | 0
15 | 0.99915 | -0.016337 | 0.025117 | 0.006295
16 | 0.977 | -0.44176 | 0 | 0
17 | 0.97743 | -0.43333 | 0.01046 | 0.0026215
18 | 0.97619 | -0.4578 | 0.018389 | 0.0046088
19 | 0.97909 | -0.40092 | 0 | 0
20 | 0.97905 | -0.40184 | 0.0087011 | 0.0021807
21 | 0.98282 | -0.32849 | 0 | 0
22 | 0.98542 | -0.27824 | 0.029391 | 0.007366
23 | 0.98837 | -0.22131 | 0.056686 | 0.014207
24 | 0.99436 | -0.10834 | 0.0067678 | 0.0016962
25 | 0.99444 | -0.10679 | 0 | 0
26 | 0.9946 | -0.10378 | 0.0025572 | 0.00064089
27 | 0.99462 | -0.10345 | 0.0025024 | 0.00062715
28 | 0.99466 | -0.10258 | 0.0098985 | 0.0024808
29 | 0.97218 | -0.53653 | 0.0030985 | 0.00077655
30 | 0.97476 | -0.48589 | 0.023732 | 0.0059478
31 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0096752 | -0.0024248 | 0.0096805 | 0.0024274 | 5.3428e-06 | 2.5405e-06 | 0.014492 | 0.014492 | 0.014492 | 0.99342 | -0.12662 | 0.99402 | -0.11503 | 3.9814
1 | -0.035291 | -0.0088461 | 0.035313 | 0.0088593 | 2.1135e-05 | 1.3265e-05 | 0.052831 | 0.052831 | 0.052831 | 0.99402 | -0.11503 | 0.99467 | -0.10247 | 14.5139
2 | 0.0084476 | 0.0021172 | -0.0084474 | -0.0021171 | 1.9959e-07 | 8.8605e-08 | 0.012958 | 0.012958 | 0.012958 | 0.97006 | -0.57861 | 0.97003 | -0.5791 | 3.5599
3 | -0.020367 | -0.0051045 | 0.02037 | 0.0051065 | 3.2813e-06 | 1.9893e-06 | 0.031242 | 0.031242 | 0.031242 | 0.97006 | -0.57861 | 0.97023 | -0.57523 | 8.5829
4 | -0.02037 | -0.0051065 | 0.020383 | 0.0051144 | 1.3103e-05 | 7.9437e-06 | 0.031242 | 0.031242 | 0.031242 | 0.97023 | -0.57523 | 0.97091 | -0.56174 | 8.5829
5 | -0.029172 | -0.007317 | 0.029187 | 0.0073262 | 1.4787e-05 | 9.2194e-06 | 0.044711 | 0.044711 | 0.044711 | 0.97091 | -0.56174 | 0.97145 | -0.55111 | 12.2832
6 | -0.037975 | -0.0095289 | 0.038002 | 0.0095456 | 2.6411e-05 | 1.6645e-05 | 0.058173 | 0.058173 | 0.058173 | 0.97145 | -0.55111 | 0.97218 | -0.53653 | 15.9816
7 | 0.011791 | 0.0029555 | -0.011789 | -0.0029545 | 1.7128e-06 | 9.0553e-07 | 0.017636 | 0.017636 | 0.017636 | 0.99486 | -0.098775 | 0.9947 | -0.10182 | 4.8451
8 | -0.011791 | -0.0029555 | 0.011793 | 0.0029562 | 1.4018e-06 | 7.411e-07 | 0.017636 | 0.017636 | 0.017636 | 0.99486 | -0.098775 | 0.99499 | -0.09628 | 4.8451
9 | 0.00506 | 0.001268 | -0.0050596 | -0.001268 | 3.9204e-07 | 1.4078e-08 | 0.0075694 | 0.0075695 | 0.0075695 | 0.9947 | -0.10182 | 0.99462 | -0.10345 | 2.0795
10 | -0.015198 | -0.0038097 | 0.015202 | 0.0038118 | 3.5774e-06 | 2.0496e-06 | 0.022729 | 0.022729 | 0.022729 | 0.99499 | -0.09628 | 0.99524 | -0.091341 | 6.2443
11 | -0.093356 | -0.023428 | 0.093755 | 0.023682 | 0.00039872 | 0.00025447 | 0.13957 | 0.13957 | 0.13957 | 0.99536 | -0.089148 | 1 | 0 | 38.3446
12 | 0.031882 | 0.0079966 | -0.031879 | -0.0079945 | 3.3321e-06 | 2.0817e-06 | 0.047665 | 0.047665 | 0.047665 | 0.99536 | -0.089148 | 0.99524 | -0.091341 | 13.0947
13 | 0.061474 | 0.015431 | -0.061435 | -0.015406 | 3.9026e-05 | 2.4817e-05 | 0.09191 | 0.09191 | 0.09191 | 0.99536 | -0.089148 | 0.99467 | -0.10247 | 25.2499
14 | 0.19191 | 0.049452 | -0.19072 | -0.048695 | 0.0011851 | 0.00075645 | 0.28604 | 0.28604 | 0.28604 | 1 | 0 | 0.99326 | -0.12771 | 39.2915
15 | 0.025137 | 0.0063071 | -0.025117 | -0.006295 | 1.9564e-05 | 1.2032e-05 | 0.037407 | 0.037407 | 0.037407 | 1 | 0 | 0.99915 | -0.016337 | 10.2766
16 | 0.016677 | 0.0041828 | -0.016668 | -0.0041775 | 8.9274e-06 | 5.2163e-06 | 0.024935 | 0.024936 | 0.024936 | 0.99524 | -0.091341 | 0.99466 | -0.10258 | 6.8505
17 | 0.19072 | 0.048695 | -0.18986 | -0.048147 | 0.00085852 | 0.00054801 | 0.28604 | 0.28604 | 0.28604 | 0.99326 | -0.12771 | 0.98837 | -0.22131 | 39.2915
18 | -0.083472 | -0.021038 | 0.083506 | 0.021059 | 3.3701e-05 | 2.1499e-05 | 0.12717 | 0.12717 | 0.12717 | 0.977 | -0.44176 | 0.97743 | -0.43333 | 34.9379
19 | 0.083472 | 0.021038 | -0.083408 | -0.020997 | 6.4001e-05 | 4.0828e-05 | 0.12717 | 0.12717 | 0.12717 | 0.977 | -0.44176 | 0.97619 | -0.4578 | 34.9379
20 | -0.093966 | -0.023681 | 0.094111 | 0.023774 | 0.00014592 | 9.3149e-05 | 0.1431 | 0.1431 | 0.1431 | 0.97743 | -0.43333 | 0.97909 | -0.40092 | 39.3125
21 | 0.065019 | 0.016388 | -0.064932 | -0.016333 | 8.7253e-05 | 5.5547e-05 | 0.099143 | 0.099143 | 0.099143 | 0.97619 | -0.4578 | 0.97476 | -0.48589 | 27.2371
22 | 0.0087015 | 0.0021809 | -0.0087011 | -0.0021807 | 3.8104e-07 | 1.708e-07 | 0.013224 | 0.013225 | 0.013225 | 0.97909 | -0.40092 | 0.97905 | -0.40184 | 3.6331
23 | -0.10281 | -0.025955 | 0.10317 | 0.026184 | 0.00035809 | 0.00022869 | 0.15632 | 0.15632 | 0.15632 | 0.97909 | -0.40092 | 0.98282 | -0.32849 | 42.9455
24 | -0.10317 | -0.026184 | 0.10342 | 0.026342 | 0.00025003 | 0.00015863 | 0.15632 | 0.15632 | 0.15632 | 0.98282 | -0.32849 | 0.98542 | -0.27824 | 21.4727
25 | -0.13281 | -0.033708 | 0.13318 | 0.03394 | 0.00036481 | 0.00023225 | 0.2007 | 0.2007 | 0.2007 | 0.98542 | -0.27824 | 0.98837 | -0.22131 | 27.5689
26 | -0.0067678 | -0.0016962 | 0.0067683 | 0.0016963 | 5.0066e-07 | 1.5156e-07 | 0.010128 | 0.010128 | 0.010128 | 0.99436 | -0.10834 | 0.99444 | -0.10679 | 2.7823
27 | -0.0067683 | -0.0016963 | 0.0067697 | 0.0016967 | 1.3578e-06 | 4.1089e-07 | 0.010128 | 0.010127 | 0.010128 | 0.99444 | -0.10679 | 0.99466 | -0.10258 | 2.7823
28 | -0.0025572 | -0.00064089 | 0.0025572 | 0.00064082 | 3.9775e-08 | -6.8594e-08 | 0.0038258 | 0.0038257 | 0.0038258 | 0.9946 | -0.10378 | 0.99462 | -0.10345 | 1.051
29 | -0.0411 | -0.010322 | 0.0412 | 0.010385 | 9.9582e-05 | 6.2898e-05 | 0.062915 | 0.062915 | 0.062915 | 0.97218 | -0.53653 | 0.97476 | -0.48589 | 17.2845

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.31245 | 0.079441

## res_load
| p_mw | q_mvar
0 | 0.0096752 | 0.0024248
1 | 0.025611 | 0.0064187
2 | 0.011919 | 0.0029873
3 | 0.0084474 | 0.0021171
4 | 0.0087885 | 0.0022026
5 | 0.0087888 | 0.0022027
6 | 0.0067295 | 0.0016866
7 | 0.0034056 | 0.00085352
8 | 0.026123 | 0.0065469
9 | 0.025117 | 0.006295
10 | 0.01046 | 0.0026215
11 | 0.018389 | 0.0046088
12 | 0.0087011 | 0.0021807
13 | 0.029391 | 0.007366
14 | 0.056686 | 0.014207
15 | 0.0067678 | 0.0016962
16 | 0.0025572 | 0.00064089
17 | 0.0025024 | 0.00062715
18 | 0.0098985 | 0.0024808
19 | 0.0030985 | 0.00077655
20 | 0.023732 | 0.0059478

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1