## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-623_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-623_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-623_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_261-623_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_261-623_0_3_node_8 | 0.4 | n |  | TRUE
5 | bus_LV_261-623_0_3_node_106 | 0.4 | n |  | TRUE
6 | bus_LV_261-623_0_3_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_261-623_0_3_node_109 | 0.4 | n |  | TRUE
8 | bus_LV_261-623_0_3_node_7 | 0.4 | n |  | TRUE
9 | bus_LV_261-623_0_3_node_108 | 0.4 | n |  | TRUE
10 | bus_LV_261-623_0_3_node_107 | 0.4 | n |  | TRUE
11 | bus_LV_261-623_0_3_node_89 | 0.4 | n |  | TRUE
12 | bus_LV_261-623_0_3_node_103 | 0.4 | n |  | TRUE
13 | bus_LV_261-623_0_3_node_60 | 0.4 | n |  | TRUE
14 | bus_LV_261-623_0_3_node_87 | 0.4 | n |  | TRUE
15 | bus_LV_261-623_0_3_node_94 | 0.4 | n |  | TRUE
16 | bus_LV_261-623_0_3_node_90 | 0.4 | n |  | TRUE
17 | bus_LV_261-623_0_3_node_9 | 0.4 | n |  | TRUE
18 | bus_LV_261-623_0_3_node_10 | 0.4 | n |  | TRUE
19 | bus_LV_261-623_0_3_node_11 | 0.4 | n |  | TRUE
20 | bus_LV_261-623_0_3_node_12 | 0.4 | n |  | TRUE
21 | bus_LV_261-623_0_3_node_13 | 0.4 | n |  | TRUE
22 | bus_LV_261-623_0_3_node_16 | 0.4 | n |  | TRUE
23 | bus_LV_261-623_0_3_node_136 | 0.4 | n |  | TRUE
24 | bus_LV_261-623_0_3_node_23 | 0.4 | n |  | TRUE
25 | bus_LV_261-623_0_3_node_21 | 0.4 | n |  | TRUE
26 | bus_LV_261-623_0_3_node_132 | 0.4 | n |  | TRUE
27 | bus_LV_261-623_0_3_node_15 | 0.4 | n |  | TRUE
28 | bus_LV_261-623_0_3_node_135 | 0.4 | n |  | TRUE
29 | bus_LV_261-623_0_3_node_14 | 0.4 | n |  | TRUE
30 | bus_LV_261-623_0_3_node_134 | 0.4 | n |  | TRUE
31 | bus_LV_261-623_0_3_node_130 | 0.4 | n |  | TRUE
32 | bus_LV_261-623_0_3_node_17 | 0.4 | n |  | TRUE
33 | bus_LV_261-623_0_3_node_18 | 0.4 | n |  | TRUE
34 | bus_LV_261-623_0_3_node_19 | 0.4 | n |  | TRUE
35 | bus_LV_261-623_0_3_node_20 | 0.4 | n |  | TRUE
36 | bus_LV_261-623_0_3_node_36 | 0.4 | n |  | TRUE
37 | bus_LV_261-623_0_3_node_37 | 0.4 | n |  | TRUE
38 | bus_LV_261-623_0_3_node_38 | 0.4 | n |  | TRUE
39 | bus_LV_261-623_0_3_node_42 | 0.4 | n |  | TRUE
40 | bus_LV_261-623_0_3_node_39 | 0.4 | n |  | TRUE
41 | bus_LV_261-623_0_3_node_24 | 0.4 | n |  | TRUE
42 | bus_LV_261-623_0_3_node_35 | 0.4 | n |  | TRUE
43 | bus_LV_261-623_0_3_node_32 | 0.4 | n |  | TRUE
44 | bus_LV_261-623_0_3_node_28 | 0.4 | n |  | TRUE
45 | bus_LV_261-623_0_3_node_105 | 0.4 | n |  | TRUE
46 | bus_LV_261-623_0_3_node_104 | 0.4 | n |  | TRUE
47 | bus_LV_261-623_0_3_node_30 | 0.4 | n |  | TRUE
48 | bus_LV_261-623_0_3_node_29 | 0.4 | n |  | TRUE
49 | bus_LV_261-623_0_3_node_102 | 0.4 | n |  | TRUE
50 | bus_LV_261-623_0_3_node_100 | 0.4 | n |  | TRUE
51 | bus_LV_261-623_0_3_node_101 | 0.4 | n |  | TRUE
52 | bus_LV_261-623_0_3_node_31 | 0.4 | n |  | TRUE
53 | bus_LV_261-623_0_3_node_33 | 0.4 | n |  | TRUE
54 | bus_LV_261-623_0_3_node_34 | 0.4 | n |  | TRUE
55 | bus_LV_261-623_0_3_node_43 | 0.4 | n |  | TRUE
56 | bus_LV_261-623_0_3_node_44 | 0.4 | n |  | TRUE
57 | bus_LV_261-623_0_3_node_46 | 0.4 | n |  | TRUE
58 | bus_LV_261-623_0_3_node_40 | 0.4 | n |  | TRUE
59 | bus_LV_261-623_0_3_node_41 | 0.4 | n |  | TRUE
60 | bus_LV_261-623_0_3_node_47 | 0.4 | n |  | TRUE
61 | bus_LV_261-623_0_3_node_45 | 0.4 | n |  | TRUE
62 | bus_LV_261-623_0_3_node_99 | 0.4 | n |  | TRUE
63 | bus_LV_261-623_0_3_node_55 | 0.4 | n |  | TRUE
64 | bus_LV_261-623_0_3_node_48 | 0.4 | n |  | TRUE
65 | bus_LV_261-623_0_3_node_49 | 0.4 | n |  | TRUE
66 | bus_LV_261-623_0_3_node_50 | 0.4 | n |  | TRUE
67 | bus_LV_261-623_0_3_node_51 | 0.4 | n |  | TRUE
68 | bus_LV_261-623_0_3_node_62 | 0.4 | n |  | TRUE
69 | bus_LV_261-623_0_3_node_75 | 0.4 | n |  | TRUE
70 | bus_LV_261-623_0_3_node_63 | 0.4 | n |  | TRUE
71 | bus_LV_261-623_0_3_node_78 | 0.4 | n |  | TRUE
72 | bus_LV_261-623_0_3_node_73 | 0.4 | n |  | TRUE
73 | bus_LV_261-623_0_3_node_52 | 0.4 | n |  | TRUE
74 | bus_LV_261-623_0_3_node_53 | 0.4 | n |  | TRUE
75 | bus_LV_261-623_0_3_node_54 | 0.4 | n |  | TRUE
76 | bus_LV_261-623_0_3_node_56 | 0.4 | n |  | TRUE
77 | bus_LV_261-623_0_3_node_76 | 0.4 | n |  | TRUE
78 | bus_LV_261-623_0_3_node_61 | 0.4 | n |  | TRUE
79 | bus_LV_261-623_0_3_node_57 | 0.4 | n |  | TRUE
80 | bus_LV_261-623_0_3_node_58 | 0.4 | n |  | TRUE
81 | bus_LV_261-623_0_3_node_59 | 0.4 | n |  | TRUE
82 | bus_LV_261-623_0_3_node_65 | 0.4 | n |  | TRUE
83 | bus_LV_261-623_0_3_node_64 | 0.4 | n |  | TRUE
84 | bus_LV_261-623_0_3_node_71 | 0.4 | n |  | TRUE
85 | bus_LV_261-623_0_3_node_83 | 0.4 | n |  | TRUE
86 | bus_LV_261-623_0_3_node_66 | 0.4 | n |  | TRUE
87 | bus_LV_261-623_0_3_node_67 | 0.4 | n |  | TRUE
88 | bus_LV_261-623_0_3_node_81 | 0.4 | n |  | TRUE
89 | bus_LV_261-623_0_3_node_82 | 0.4 | n |  | TRUE
90 | bus_LV_261-623_0_3_node_110 | 0.4 | n |  | TRUE
91 | bus_LV_261-623_0_3_node_111 | 0.4 | n |  | TRUE
92 | bus_LV_261-623_0_3_node_116 | 0.4 | n |  | TRUE
93 | bus_LV_261-623_0_3_node_68 | 0.4 | n |  | TRUE
94 | bus_LV_261-623_0_3_node_69 | 0.4 | n |  | TRUE
95 | bus_LV_261-623_0_3_node_70 | 0.4 | n |  | TRUE
96 | bus_LV_261-623_0_3_node_124 | 0.4 | n |  | TRUE
97 | bus_LV_261-623_0_3_node_138 | 0.4 | n |  | TRUE
98 | bus_LV_261-623_0_3_node_129 | 0.4 | n |  | TRUE
99 | bus_LV_261-623_0_3_node_122 | 0.4 | n |  | TRUE
100 | bus_LV_261-623_0_3_node_72 | 0.4 | n |  | TRUE
101 | bus_LV_261-623_0_3_node_74 | 0.4 | n |  | TRUE
102 | bus_LV_261-623_0_3_node_77 | 0.4 | n |  | TRUE
103 | bus_LV_261-623_0_3_node_79 | 0.4 | n |  | TRUE
104 | bus_LV_261-623_0_3_node_80 | 0.4 | n |  | TRUE
105 | bus_LV_261-623_0_3_node_127 | 0.4 | n |  | TRUE
106 | bus_LV_261-623_0_3_node_98 | 0.4 | n |  | TRUE
107 | bus_LV_261-623_0_3_node_112 | 0.4 | n |  | TRUE
108 | bus_LV_261-623_0_3_node_118 | 0.4 | n |  | TRUE
109 | bus_LV_261-623_0_3_node_114 | 0.4 | n |  | TRUE
110 | bus_LV_261-623_0_3_node_84 | 0.4 | n |  | TRUE
111 | bus_LV_261-623_0_3_node_85 | 0.4 | n |  | TRUE
112 | bus_LV_261-623_0_3_node_86 | 0.4 | n |  | TRUE
113 | bus_LV_261-623_0_3_node_88 | 0.4 | n |  | TRUE
114 | bus_LV_261-623_0_3_node_140 | 0.4 | n |  | TRUE
115 | bus_LV_261-623_0_3_node_141 | 0.4 | n |  | TRUE
116 | bus_LV_261-623_0_3_node_91 | 0.4 | n |  | TRUE
117 | bus_LV_261-623_0_3_node_92 | 0.4 | n |  | TRUE
118 | bus_LV_261-623_0_3_node_93 | 0.4 | n |  | TRUE
119 | bus_LV_261-623_0_3_node_96 | 0.4 | n |  | TRUE
120 | bus_LV_261-623_0_3_node_95 | 0.4 | n |  | TRUE
121 | bus_LV_261-623_0_3_node_97 | 0.4 | n |  | TRUE
122 | bus_LV_261-623_0_3_node_126 | 0.4 | n |  | TRUE
123 | bus_LV_261-623_0_3_node_113 | 0.4 | n |  | TRUE
124 | bus_LV_261-623_0_3_node_115 | 0.4 | n |  | TRUE
125 | bus_LV_261-623_0_3_node_117 | 0.4 | n |  | TRUE
126 | bus_LV_261-623_0_3_node_119 | 0.4 | n |  | TRUE
127 | bus_LV_261-623_0_3_node_120 | 0.4 | n |  | TRUE
128 | bus_LV_261-623_0_3_node_125 | 0.4 | n |  | TRUE
129 | bus_LV_261-623_0_3_node_121 | 0.4 | n |  | TRUE
130 | bus_LV_261-623_0_3_node_123 | 0.4 | n |  | TRUE
131 | bus_LV_261-623_0_3_node_128 | 0.4 | n |  | TRUE
132 | bus_LV_261-623_0_3_node_131 | 0.4 | n |  | TRUE
133 | bus_LV_261-623_0_3_node_133 | 0.4 | n |  | TRUE
134 | bus_LV_261-623_0_3_node_139 | 0.4 | n |  | TRUE
135 | bus_LV_261-623_0_3_node_137 | 0.4 | n |  | TRUE
136 | bus_MV_529_1_node_80 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-623_0_3_load_0 | 0 | 0.0061317 | 0.0015367 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-623_0_3_load_106 | 5 | 0.0020458 | 0.00051273 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-623_0_3_load_109 | 7 | 0.0016635 | 0.00041691 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-623_0_3_load_108 | 9 | 0.0015867 | 0.00039768 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-623_0_3_load_107 | 10 | 0.0017582 | 0.00044065 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-623_0_3_load_89 | 11 | 0.0017038 | 0.00042703 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-623_0_3_load_103 | 12 | 0.0032501 | 0.00081454 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-623_0_3_load_60 | 13 | 0.0039156 | 0.00098135 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-623_0_3_load_87 | 14 | 0.0016864 | 0.00042264 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-623_0_3_load_90 | 16 | 0.0019554 | 0.00049007 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-623_0_3_load_9 | 17 | 0.0010493 | 0.00026297 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-623_0_3_load_10 | 18 | 0.000498 | 0.00012481 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-623_0_3_load_136 | 23 | 0.00096771 | 0.00024253 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-623_0_3_load_23 | 24 | 0.0010326 | 0.0002588 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-623_0_3_load_21 | 25 | 0.0009877 | 0.00024754 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-623_0_3_load_15 | 27 | 0.0059832 | 0.0014995 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-623_0_3_load_135 | 28 | 0.00093606 | 0.0002346 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_261-623_0_3_load_14 | 29 | 0.00083842 | 0.00021013 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_261-623_0_3_load_130 | 31 | 0.0012291 | 0.00030804 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_261-623_0_3_load_17 | 32 | 0.0078339 | 0.0019634 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_261-623_0_3_load_18 | 33 | 0.0013052 | 0.00032712 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_261-623_0_3_load_19 | 34 | 0.001031 | 0.00025839 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_261-623_0_3_load_36 | 36 | 0.0080674 | 0.0020219 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_261-623_0_3_load_38 | 38 | 0.0069284 | 0.0017364 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_261-623_0_3_load_42 | 39 | 0.0074096 | 0.001857 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_261-623_0_3_load_39 | 40 | 0.0086845 | 0.0021765 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_261-623_0_3_load_35 | 42 | 0.0057997 | 0.0014535 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_261-623_0_3_load_32 | 43 | 0.0049295 | 0.0012355 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_261-623_0_3_load_105 | 45 | 0.0051336 | 0.0012866 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_261-623_0_3_load_104 | 46 | 0.0025917 | 0.00064955 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_261-623_0_3_load_29 | 48 | 0.0033844 | 0.0008482 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_261-623_0_3_load_102 | 49 | 0.0030398 | 0.00076185 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_261-623_0_3_load_100 | 50 | 0.00318 | 0.00079698 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_261-623_0_3_load_101 | 51 | 0.0067913 | 0.0017021 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_261-623_0_3_load_31 | 52 | 0.0029685 | 0.00074398 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_261-623_0_3_load_33 | 53 | 0.018516 | 0.0046406 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_261-623_0_3_load_34 | 54 | 0.014283 | 0.0035796 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_261-623_0_3_load_43 | 55 | 0.0051987 | 0.0013029 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_261-623_0_3_load_44 | 56 | 0.014262 | 0.0035743 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_261-623_0_3_load_46 | 57 | 0.0081089 | 0.0020323 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_261-623_0_3_load_40 | 58 | 0.0074026 | 0.0018553 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_261-623_0_3_load_41 | 59 | 0.0080112 | 0.0020078 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_261-623_0_3_load_47 | 60 | 0.0082223 | 0.0020607 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_261-623_0_3_load_45 | 61 | 0.0056632 | 0.0014193 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_261-623_0_3_load_55 | 63 | 0.0017525 | 0.00043922 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_261-623_0_3_load_48 | 64 | 0.0064301 | 0.0016115 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_261-623_0_3_load_50 | 66 | 0.00096806 | 0.00024262 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_261-623_0_3_load_51 | 67 | 0.0012271 | 0.00030755 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_261-623_0_3_load_63 | 70 | 0.0066366 | 0.0016633 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_261-623_0_3_load_78 | 71 | 0.0011086 | 0.00027783 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_261-623_0_3_load_52 | 73 | 0.0027511 | 0.00068949 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_261-623_0_3_load_53 | 74 | 0.0028113 | 0.00070457 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_261-623_0_3_load_54 | 75 | 0.001515 | 0.0003797 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_261-623_0_3_load_56 | 76 | 0.0016787 | 0.00042073 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_261-623_0_3_load_76 | 77 | 0.001026 | 0.00025714 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_261-623_0_3_load_57 | 79 | 0.0047493 | 0.0011903 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_261-623_0_3_load_58 | 80 | 0.0017436 | 0.000437 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_261-623_0_3_load_59 | 81 | 0.0017808 | 0.00044631 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_261-623_0_3_load_65 | 82 | 0.00097995 | 0.0002456 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_261-623_0_3_load_64 | 83 | 0.0014039 | 0.00035184 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_261-623_0_3_load_71 | 84 | 0.0014011 | 0.00035114 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_261-623_0_3_load_83 | 85 | 0.0014827 | 0.00037159 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_261-623_0_3_load_66 | 86 | 0.00098422 | 0.00024667 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_261-623_0_3_load_82 | 89 | 0.0014846 | 0.00037209 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_261-623_0_3_load_111 | 91 | 0.001951 | 0.00048896 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_261-623_0_3_load_68 | 93 | 0.0016348 | 0.00040971 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_261-623_0_3_load_69 | 94 | 0.0012565 | 0.00031491 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_261-623_0_3_load_138 | 97 | 0.0013818 | 0.00034631 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_261-623_0_3_load_129 | 98 | 0.0012116 | 0.00030366 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_261-623_0_3_load_122 | 99 | 0.0013033 | 0.00032663 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_261-623_0_3_load_72 | 100 | 0.0010341 | 0.00025917 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_261-623_0_3_load_74 | 101 | 0.0079544 | 0.0019936 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_261-623_0_3_load_77 | 102 | 0.001145 | 0.00028698 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_261-623_0_3_load_79 | 103 | 0.0014748 | 0.00036962 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_261-623_0_3_load_80 | 104 | 0.0015172 | 0.00038025 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_261-623_0_3_load_127 | 105 | 0.001068 | 0.00026766 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_261-623_0_3_load_112 | 107 | 0.0020015 | 0.00050163 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_261-623_0_3_load_118 | 108 | 0.001181 | 0.00029599 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_261-623_0_3_load_114 | 109 | 0.0014607 | 0.0003661 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_261-623_0_3_load_84 | 110 | 0.0018482 | 0.00046319 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_261-623_0_3_load_85 | 111 | 0.00195 | 0.00048872 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_261-623_0_3_load_86 | 112 | 0.0018335 | 0.00045952 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_261-623_0_3_load_140 | 114 | 0.0020074 | 0.00050311 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_261-623_0_3_load_141 | 115 | 0.0035251 | 0.00088347 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_261-623_0_3_load_91 | 116 | 0.0017823 | 0.00044668 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_261-623_0_3_load_92 | 117 | 0.0012914 | 0.00032366 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_261-623_0_3_load_93 | 118 | 0.0033639 | 0.00084307 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_261-623_0_3_load_96 | 119 | 0.0019451 | 0.00048748 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_261-623_0_3_load_95 | 120 | 0.0018861 | 0.00047269 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_261-623_0_3_load_97 | 121 | 0.003727 | 0.00093407 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_261-623_0_3_load_126 | 122 | 0.0014043 | 0.00035195 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_261-623_0_3_load_113 | 123 | 0.0038158 | 0.00095634 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_261-623_0_3_load_115 | 124 | 0.0016786 | 0.00042071 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_261-623_0_3_load_119 | 126 | 0.0020223 | 0.00050683 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_261-623_0_3_load_120 | 127 | 0.0010196 | 0.00025554 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_261-623_0_3_load_125 | 128 | 0.0013179 | 0.0003303 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_261-623_0_3_load_121 | 129 | 0.0014226 | 0.00035653 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_261-623_0_3_load_123 | 130 | 0.00098491 | 0.00024684 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_261-623_0_3_load_128 | 131 | 0.0026073 | 0.00065344 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_261-623_0_3_load_131 | 132 | 0.00095391 | 0.00023907 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_261-623_0_3_load_133 | 133 | 0.001938 | 0.0004857 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_261-623_0_3_load_139 | 134 | 0.0059799 | 0.0014987 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_261-623_0_3_load_137 | 135 | 0.0020607 | 0.00051647 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 67 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-623_0_3_line_0 |  | 0 | 1 | 0.025042 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-623_0_3_line_1 |  | 0 | 2 | 0.041725 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-623_0_3_line_2 |  | 1 | 3 | 0.12077 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-623_0_3_line_3 |  | 2 | 4 | 0.34116 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-623_0_3_line_4 |  | 3 | 5 | 0.031675 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_261-623_0_3_line_5 |  | 4 | 11 | 0.013522 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_261-623_0_3_line_6 |  | 4 | 8 | 0.012939 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_261-623_0_3_line_7 |  | 6 | 7 | 0.016197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_261-623_0_3_line_8 |  | 6 | 8 | 0.036322 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_261-623_0_3_line_9 |  | 6 | 9 | 0.016032 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_261-623_0_3_line_10 |  | 7 | 14 | 0.00021845 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_261-623_0_3_line_11 |  | 8 | 10 | 0.019228 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_261-623_0_3_line_12 |  | 9 | 15 | 0.023539 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-623_0_3_line_13 |  | 11 | 16 | 0.00157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_261-623_0_3_line_14 |  | 12 | 13 | 0.013214 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_261-623_0_3_line_15 |  | 13 | 80 | 0.018137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_261-623_0_3_line_16 |  | 14 | 111 | 0.012799 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_261-623_0_3_line_17 |  | 15 | 106 | 0.004843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_261-623_0_3_line_18 |  | 15 | 117 | 0.015085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_261-623_0_3_line_19 |  | 17 | 18 | 0.0097275 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_261-623_0_3_line_20 |  | 17 | 19 | 0.014957 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_261-623_0_3_line_21 |  | 19 | 20 | 0.13859 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_261-623_0_3_line_22 |  | 19 | 21 | 0.019614 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_261-623_0_3_line_23 |  | 20 | 22 | 0.017459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_261-623_0_3_line_24 |  | 20 | 23 | 0.014017 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_261-623_0_3_line_25 |  | 21 | 24 | 0.11441 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_261-623_0_3_line_26 |  | 21 | 25 | 0.030149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_261-623_0_3_line_27 |  | 22 | 26 | 0.021568 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_261-623_0_3_line_28 |  | 22 | 27 | 0.013134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_261-623_0_3_line_29 |  | 23 | 28 | 6.8731e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_261-623_0_3_line_30 |  | 26 | 30 | 0.010103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_261-623_0_3_line_31 |  | 26 | 31 | 0.013782 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_261-623_0_3_line_32 |  | 27 | 29 | 0.0015218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_261-623_0_3_line_33 |  | 28 | 135 | 0.013294 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_261-623_0_3_line_34 |  | 30 | 97 | 0.014575 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_261-623_0_3_line_35 |  | 30 | 95 | 0.023523 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_261-623_0_3_line_36 |  | 31 | 132 | 0.00017583 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_261-623_0_3_line_37 |  | 32 | 33 | 0.000125 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_261-623_0_3_line_38 |  | 32 | 34 | 0.0073804 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_261-623_0_3_line_39 |  | 33 | 35 | 0.048034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_261-623_0_3_line_40 |  | 35 | 36 | 0.014442 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_261-623_0_3_line_41 |  | 35 | 37 | 0.010025 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_261-623_0_3_line_42 |  | 36 | 38 | 0.0023283 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_261-623_0_3_line_43 |  | 37 | 39 | 0.014399 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_261-623_0_3_line_44 |  | 37 | 40 | 0.017446 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_261-623_0_3_line_45 |  | 39 | 57 | 0.017227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_261-623_0_3_line_46 |  | 40 | 58 | 5.5315e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_261-623_0_3_line_47 |  | 41 | 42 | 0.022079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_261-623_0_3_line_48 |  | 41 | 43 | 0.013252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_261-623_0_3_line_49 |  | 43 | 47 | 0.010076 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_261-623_0_3_line_50 |  | 44 | 45 | 0.031173 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_261-623_0_3_line_51 |  | 44 | 46 | 0.015916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_261-623_0_3_line_52 |  | 45 | 51 | 0.016068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_261-623_0_3_line_53 |  | 47 | 52 | 0.010233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_261-623_0_3_line_54 |  | 47 | 48 | 0.026183 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_261-623_0_3_line_55 |  | 49 | 50 | 0.00096544 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_261-623_0_3_line_56 |  | 50 | 62 | 0.046472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_261-623_0_3_line_57 |  | 51 | 62 | 0.017463 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_261-623_0_3_line_58 |  | 52 | 53 | 0.023385 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_261-623_0_3_line_59 |  | 53 | 54 | 0.017087 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_261-623_0_3_line_60 |  | 54 | 55 | 0.038663 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_261-623_0_3_line_61 |  | 55 | 56 | 0.01919 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_261-623_0_3_line_62 |  | 56 | 61 | 0.013963 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_261-623_0_3_line_63 |  | 57 | 60 | 0.0034256 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_261-623_0_3_line_64 |  | 58 | 59 | 0.010247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_261-623_0_3_line_65 |  | 60 | 64 | 0.020789 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_261-623_0_3_line_66 |  | 61 | 62 | 0.021884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_261-623_0_3_line_67 |  | 62 | 63 | 0.018132 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_261-623_0_3_line_68 |  | 63 | 74 | 0.023826 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_261-623_0_3_line_69 |  | 64 | 65 | 0.008784 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_261-623_0_3_line_70 |  | 65 | 66 | 0.015698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_261-623_0_3_line_71 |  | 65 | 67 | 0.010588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_261-623_0_3_line_72 |  | 66 | 68 | 0.011789 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_261-623_0_3_line_73 |  | 67 | 69 | 0.025729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
74 | LV_261-623_0_3_line_74 |  | 68 | 70 | 0.012152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_261-623_0_3_line_75 |  | 69 | 71 | 0.015763 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_261-623_0_3_line_76 |  | 69 | 72 | 0.00236 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
77 | LV_261-623_0_3_line_77 |  | 70 | 85 | 0.0020075 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_261-623_0_3_line_78 |  | 71 | 102 | 0.00044248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_261-623_0_3_line_79 |  | 72 | 84 | 0.013293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_261-623_0_3_line_80 |  | 72 | 78 | 0.038519 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
81 | LV_261-623_0_3_line_81 |  | 73 | 74 | 2.2674e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_261-623_0_3_line_82 |  | 73 | 75 | 0.017782 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_261-623_0_3_line_83 |  | 75 | 76 | 0.0094062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_261-623_0_3_line_84 |  | 76 | 77 | 0.0012546 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_261-623_0_3_line_85 |  | 77 | 78 | 0.015157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_261-623_0_3_line_86 |  | 78 | 82 | 0.016865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_261-623_0_3_line_87 |  | 78 | 81 | 0.018388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_261-623_0_3_line_88 |  | 79 | 80 | 0.0058176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_261-623_0_3_line_89 |  | 79 | 81 | 0.020453 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_261-623_0_3_line_90 |  | 82 | 83 | 0.0023738 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_261-623_0_3_line_91 |  | 83 | 86 | 0.018893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_261-623_0_3_line_92 |  | 84 | 100 | 0.0011598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_261-623_0_3_line_93 |  | 86 | 87 | 0.035221 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_261-623_0_3_line_94 |  | 87 | 88 | 0.016755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_261-623_0_3_line_95 |  | 87 | 89 | 0.012861 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_261-623_0_3_line_96 |  | 88 | 90 | 0.007091 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_261-623_0_3_line_97 |  | 88 | 91 | 0.013255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_261-623_0_3_line_98 |  | 89 | 92 | 0.017123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_261-623_0_3_line_99 |  | 90 | 105 | 0.014009 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_261-623_0_3_line_100 |  | 90 | 106 | 0.033471 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_261-623_0_3_line_101 |  | 91 | 107 | 0.00048474 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_261-623_0_3_line_102 |  | 92 | 108 | 0.0040742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_261-623_0_3_line_103 |  | 92 | 109 | 0.013012 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_261-623_0_3_line_104 |  | 93 | 94 | 0.017331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_261-623_0_3_line_105 |  | 94 | 95 | 0.013148 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_261-623_0_3_line_106 |  | 95 | 96 | 0.00595 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_261-623_0_3_line_107 |  | 96 | 98 | 0.018246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_261-623_0_3_line_108 |  | 96 | 99 | 0.014312 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_261-623_0_3_line_109 |  | 97 | 134 | 0.00054891 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_261-623_0_3_line_110 |  | 98 | 108 | 0.018182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_261-623_0_3_line_111 |  | 99 | 129 | 0.00030691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_261-623_0_3_line_112 |  | 100 | 101 | 0.003791 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_261-623_0_3_line_113 |  | 102 | 103 | 0.011942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_261-623_0_3_line_114 |  | 103 | 104 | 0.012761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_261-623_0_3_line_115 |  | 105 | 122 | 0.00022126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_261-623_0_3_line_116 |  | 106 | 119 | 0.011931 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_261-623_0_3_line_117 |  | 107 | 123 | 0.013152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_261-623_0_3_line_118 |  | 109 | 124 | 0.00018048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_261-623_0_3_line_119 |  | 110 | 111 | 0.00014188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_261-623_0_3_line_120 |  | 110 | 112 | 0.013992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_261-623_0_3_line_121 |  | 112 | 113 | 0.0071551 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_261-623_0_3_line_122 |  | 113 | 114 | 0.0061727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_261-623_0_3_line_123 |  | 114 | 115 | 0.0040799 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_261-623_0_3_line_124 |  | 116 | 117 | 0.00094145 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_261-623_0_3_line_125 |  | 116 | 118 | 0.015772 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_261-623_0_3_line_126 |  | 119 | 120 | 0.0010896 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_261-623_0_3_line_127 |  | 120 | 121 | 0.01339 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_261-623_0_3_line_128 |  | 122 | 131 | 0.012533 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_261-623_0_3_line_129 |  | 124 | 125 | 0.012334 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_261-623_0_3_line_130 |  | 125 | 126 | 0.016091 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_261-623_0_3_line_131 |  | 125 | 127 | 0.025086 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_261-623_0_3_line_132 |  | 127 | 128 | 0.0041062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_261-623_0_3_line_133 |  | 129 | 130 | 0.011916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_261-623_0_3_line_134 |  | 132 | 133 | 0.012691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-623_0_3_trafo_51 | 0.63 MVA 20/0.4 kV | 136 | 67 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19
0 | 2678435.2113 | 1247725.1447 | 2678427.0378 | 1247738.9244 | 2678422.3686 | 1247746.6429
1 | 2678401.3227 | 1247782.6606 | 2678407.9415 | 1247770.4948 | 2678410.8758 | 1247765.6412 | 2678422.3686 | 1247746.6429
2 | 2678435.2113 | 1247725.1447 | 2678434.0111 | 1247715.3884 | 2678443.2979 | 1247712.7982 | 2678471.0866 | 1247678.4965 | 2678491.8132 | 1247647.6373 | 2678493.0673 | 1247637.3575 | 2678488.39 | 1247628.9451
3 | 2678401.3227 | 1247782.6606 | 2678427.3774 | 1247794.8806 | 2678454.9834 | 1247801.1614 | 2678470.1149 | 1247802.0845 | 2678481.7446 | 1247801.0821 | 2678493.6995 | 1247800.0507 | 2678508.2192 | 1247806.1028 | 2678515.7991 | 1247802.356 | 2678533.5572 | 1247792.584 | 2678552.7286 | 1247782.1748 | 2678575.7328 | 1247765.2562 | 2678585.8804 | 1247759.8311 | 2678603.0066 | 1247757.2896 | 2678642.3408 | 1247720.4398 | 2678654.006 | 1247708.2412 | 2678668.5206 | 1247693.056 | 2678673.7526 | 1247692.0914 | 2678679.167 | 1247693.3197 | 2678690.1804 | 1247700.0707 | 2678695.2431 | 1247703.3292
4 | 2678488.39 | 1247628.9451 | 2678499.5192 | 1247621.2757 | 2678517.5259 | 1247618.9259
5 | 2678695.2431 | 1247703.3292 | 2678702.5025 | 1247691.9209
6 | 2678706.2938 | 1247710.1141 | 2678695.2431 | 1247703.3292
7 | 2678726.0551 | 1247719.5944 | 2678740.0694 | 1247727.715
8 | 2678726.0551 | 1247719.5944 | 2678731.5493 | 1247710.8276 | 2678728.255 | 1247710.3502 | 2678723.339 | 1247711.4079 | 2678719.6869 | 1247712.2712 | 2678715.3608 | 1247712.7029 | 2678710.5888 | 1247712.0169 | 2678706.2938 | 1247710.1141
9 | 2678726.0551 | 1247719.5944 | 2678723.0344 | 1247724.6691 | 2678718.2157 | 1247733.5749
10 | 2678740.2584 | 1247727.8245 | 2678740.0694 | 1247727.715
11 | 2678706.2938 | 1247710.1141 | 2678697.4531 | 1247714.3665 | 2678691.5694 | 1247721.72
12 | 2678707.0139 | 1247754.2779 | 2678718.2157 | 1247733.5749
13 | 2678703.3454 | 1247690.5963 | 2678702.5025 | 1247691.9209
14 | 2678796.7849 | 1247803.2959 | 2678786.7399 | 1247811.8815
15 | 2678786.7399 | 1247811.8815 | 2678786.2823 | 1247812.2726 | 2678773.7349 | 1247818.6662 | 2678770.8022 | 1247820.4879
16 | 2678751.3327 | 1247734.2415 | 2678740.2584 | 1247727.8245
17 | 2678707.0139 | 1247754.2779 | 2678704.7065 | 1247758.5393
18 | 2678707.0139 | 1247754.2779 | 2678720.3115 | 1247761.4013
19 | 2678478.9855 | 1248037.4157 | 2678472.6546 | 1248044.8012
20 | 2678488.7196 | 1248026.0601 | 2678478.9855 | 1248037.4157
21 | 2678488.7196 | 1248026.0601 | 2678498.3318 | 1248014.8348 | 2678529.8416 | 1247980.6382 | 2678556.3865 | 1247952.3692 | 2678567.577 | 1247940.0418 | 2678582.4602 | 1247923.7716
22 | 2678488.7196 | 1248026.0601 | 2678504.0779 | 1248038.3168
23 | 2678582.4602 | 1247923.7716 | 2678594.2103 | 1247910.829
24 | 2678582.4602 | 1247923.7716 | 2678571.7616 | 1247914.7155
25 | 2678504.0779 | 1248038.3168 | 2678509.1532 | 1248032.6243 | 2678527.101 | 1248011.9024 | 2678556.5143 | 1247978.6233 | 2678567.8294 | 1247965.4414 | 2678577.2951 | 1247950.467
26 | 2678504.0779 | 1248038.3168 | 2678527.6383 | 1248057.1281
27 | 2678607.6444 | 1247893.9281 | 2678607.076 | 1247894.6434 | 2678594.2103 | 1247910.829
28 | 2678594.2103 | 1247910.829 | 2678604.499 | 1247918.9933
29 | 2678571.7616 | 1247914.7155 | 2678571.7091 | 1247914.6711
30 | 2678607.6444 | 1247893.9281 | 2678614.2341 | 1247886.2544
31 | 2678607.6444 | 1247893.9281 | 2678596.9911 | 1247885.1839
32 | 2678605.691 | 1247919.9392 | 2678604.499 | 1247918.9933
33 | 2678561.562 | 1247906.0819 | 2678571.7091 | 1247914.6711
34 | 2678614.2341 | 1247886.2544 | 2678625.5714 | 1247895.4136
35 | 2678629.5768 | 1247868.3892 | 2678625.8331 | 1247872.7539 | 2678618.3152 | 1247881.505 | 2678614.2341 | 1247886.2544
36 | 2678596.9911 | 1247885.1839 | 2678596.8552 | 1247885.0724
37 | 2678603.7173 | 1247982.8069 | 2678603.8141 | 1247982.886
38 | 2678598.0003 | 1247978.1393 | 2678603.7173 | 1247982.8069
39 | 2678640.1342 | 1247966.4005 | 2678623.3423 | 1247984.213 | 2678612.5778 | 1247990.0412 | 2678603.8141 | 1247982.886
40 | 2678640.1342 | 1247966.4005 | 2678643.534 | 1247973.7175 | 2678646.4748 | 1247977.4926 | 2678647.8164 | 1247978.3433
41 | 2678647.0211 | 1247959.0976 | 2678640.1342 | 1247966.4005
42 | 2678647.8164 | 1247978.3433 | 2678649.7827 | 1247979.5902
43 | 2678647.0211 | 1247959.0976 | 2678656.3419 | 1247948.1219
44 | 2678647.0211 | 1247959.0976 | 2678633.7758 | 1247947.7433
45 | 2678656.3419 | 1247948.1219 | 2678667.493 | 1247934.991
46 | 2678633.7758 | 1247947.7433 | 2678633.7338 | 1247947.7073
47 | 2678714.8735 | 1248055.8794 | 2678719.0632 | 1248063.4182 | 2678726.5591 | 1248074.5913
48 | 2678714.8735 | 1248055.8794 | 2678720.1747 | 1248043.7337
49 | 2678724.2056 | 1248034.4988 | 2678720.1747 | 1248043.7337
50 | 2678839.0093 | 1247962.1602 | 2678831.4616 | 1247952.6974 | 2678819.5714 | 1247937.79
51 | 2678839.0093 | 1247962.1602 | 2678833.8865 | 1247969.1305 | 2678830.1374 | 1247975.3539
52 | 2678819.5714 | 1247937.79 | 2678809.5519 | 1247925.2281
53 | 2678724.2056 | 1248034.4988 | 2678728.2208 | 1248025.0868
54 | 2678724.2056 | 1248034.4988 | 2678728.6133 | 1248037.5706 | 2678742.7464 | 1248052.8461
55 | 2678830.4523 | 1247876.4534 | 2678829.8668 | 1247877.2211
56 | 2678798.6629 | 1247911.576 | 2678822.4112 | 1247886.996 | 2678829.8668 | 1247877.2211
57 | 2678798.6629 | 1247911.576 | 2678809.5519 | 1247925.2281
58 | 2678728.2208 | 1248025.0868 | 2678737.397 | 1248003.5774
59 | 2678745.532 | 1247988.5517 | 2678737.4033 | 1248003.5626 | 2678737.397 | 1248003.5774
60 | 2678745.532 | 1247988.5517 | 2678750.6511 | 1247979.0985 | 2678765.8626 | 1247955.6945
61 | 2678776.9258 | 1247940.0172 | 2678767.4675 | 1247953.2252 | 2678765.8626 | 1247955.6945
62 | 2678776.9258 | 1247940.0172 | 2678785.0555 | 1247928.6645
63 | 2678669.7104 | 1247932.3799 | 2678667.493 | 1247934.991
64 | 2678625.9543 | 1247941.0385 | 2678633.7338 | 1247947.7073
65 | 2678669.7104 | 1247932.3799 | 2678683.1669 | 1247916.5343
66 | 2678798.6629 | 1247911.576 | 2678792.4784 | 1247918.2987 | 2678785.0555 | 1247928.6645
67 | 2678798.6629 | 1247911.576 | 2678786.7265 | 1247897.9277
68 | 2678786.7265 | 1247897.9277 | 2678771.0414 | 1247879.9931
69 | 2678688.8528 | 1247909.8389 | 2678683.1669 | 1247916.5343
70 | 2678688.8528 | 1247909.8389 | 2678676.7966 | 1247899.7854
71 | 2678688.8528 | 1247909.8389 | 2678695.67 | 1247901.7374
72 | 2678667.7422 | 1247892.2349 | 2678676.7966 | 1247899.7854
73 | 2678712.2353 | 1247882.0512 | 2678695.67 | 1247901.7374
74 | 2678667.7422 | 1247892.2349 | 2678659.8925 | 1247901.5112
75 | 2678712.2353 | 1247882.0512 | 2678700.2833 | 1247871.7738
76 | 2678712.2353 | 1247882.0512 | 2678713.7623 | 1247880.248
77 | 2678658.5957 | 1247903.0437 | 2678659.8925 | 1247901.5112
78 | 2678700.2833 | 1247871.7738 | 2678699.9478 | 1247871.4853
79 | 2678713.7623 | 1247880.248 | 2678724.0909 | 1247888.6167
80 | 2678738.6476 | 1247850.7902 | 2678713.7623 | 1247880.248
81 | 2678771.0264 | 1247879.976 | 2678771.0414 | 1247879.9931
82 | 2678771.0264 | 1247879.976 | 2678770.2579 | 1247879.0973 | 2678757.8805 | 1247868.0132
83 | 2678750.8733 | 1247861.7383 | 2678757.8805 | 1247868.0132
84 | 2678749.9387 | 1247860.9013 | 2678750.8733 | 1247861.7383
85 | 2678738.6476 | 1247850.7902 | 2678749.9387 | 1247860.9013
86 | 2678738.6476 | 1247850.7902 | 2678724.7327 | 1247841.2616
87 | 2678738.6476 | 1247850.7902 | 2678749.861 | 1247836.2174
88 | 2678765.8605 | 1247823.5577 | 2678770.8022 | 1247820.4879
89 | 2678749.861 | 1247836.2174 | 2678761.047 | 1247826.5478 | 2678765.8605 | 1247823.5577
90 | 2678722.7741 | 1247839.9204 | 2678724.7327 | 1247841.2616
91 | 2678722.7741 | 1247839.9204 | 2678707.186 | 1247829.246
92 | 2678724.0909 | 1247888.6167 | 2678724.992 | 1247889.3468
93 | 2678678.1251 | 1247809.3457 | 2678707.186 | 1247829.246
94 | 2678686.0929 | 1247794.5963 | 2678678.1251 | 1247809.3457
95 | 2678678.1251 | 1247809.3457 | 2678669.994 | 1247819.3107
96 | 2678689.5364 | 1247788.393 | 2678686.0929 | 1247794.5963
97 | 2678686.0929 | 1247794.5963 | 2678674.4804 | 1247788.2051
98 | 2678659.1685 | 1247832.5778 | 2678669.994 | 1247819.3107
99 | 2678689.5364 | 1247788.393 | 2678702.0365 | 1247794.7169
100 | 2678704.7065 | 1247758.5393 | 2678689.5364 | 1247788.393
101 | 2678674.0557 | 1247787.9713 | 2678674.4804 | 1247788.2051
102 | 2678659.1685 | 1247832.5778 | 2678656.5924 | 1247835.7343
103 | 2678659.1685 | 1247832.5778 | 2678649.3719 | 1247824.0137
104 | 2678652.1137 | 1247876.1196 | 2678647.1553 | 1247882.3992 | 2678639.8589 | 1247876.5839
105 | 2678629.5768 | 1247868.3892 | 2678639.8589 | 1247876.5839
106 | 2678633.4586 | 1247863.8707 | 2678629.5768 | 1247868.3892
107 | 2678633.4586 | 1247863.8707 | 2678637.0028 | 1247859.737 | 2678645.0964 | 1247849.8201
108 | 2678633.4586 | 1247863.8707 | 2678622.6948 | 1247854.4383
109 | 2678625.9983 | 1247895.7585 | 2678625.5714 | 1247895.4136
110 | 2678656.5924 | 1247835.7343 | 2678645.0964 | 1247849.8201
111 | 2678622.4639 | 1247854.236 | 2678622.6948 | 1247854.4383
112 | 2678727.9375 | 1247891.7334 | 2678724.992 | 1247889.3468
113 | 2678699.9478 | 1247871.4853 | 2678690.893 | 1247863.6991
114 | 2678682.48 | 1247873.2945 | 2678690.893 | 1247863.6991 | 2678690.893 | 1247863.6991
115 | 2678702.234 | 1247794.8167 | 2678702.0365 | 1247794.7169
116 | 2678704.7065 | 1247758.5393 | 2678694.1447 | 1247752.9892
117 | 2678662.5336 | 1247781.6299 | 2678674.0557 | 1247787.9713
118 | 2678649.236 | 1247823.8949 | 2678649.3719 | 1247824.0137
119 | 2678751.4554 | 1247734.3127 | 2678751.3327 | 1247734.2415
120 | 2678751.4554 | 1247734.3127 | 2678763.5621 | 1247741.3279
121 | 2678769.7529 | 1247744.9152 | 2678763.5621 | 1247741.3279
122 | 2678769.7529 | 1247744.9152 | 2678768.0367 | 1247749.5847 | 2678768.122 | 1247750.7795
123 | 2678768.4124 | 1247754.8491 | 2678768.122 | 1247750.7795
124 | 2678721.1413 | 1247761.8458 | 2678720.3115 | 1247761.4013
125 | 2678734.9163 | 1247769.5149 | 2678731.5977 | 1247767.4472 | 2678721.1413 | 1247761.8458
126 | 2678693.1802 | 1247752.4823 | 2678694.1447 | 1247752.9892
127 | 2678681.3269 | 1247746.2535 | 2678693.1802 | 1247752.4823
128 | 2678713.4171 | 1247800.4743 | 2678702.234 | 1247794.8167
129 | 2678639.9502 | 1247815.7774 | 2678649.236 | 1247823.8949
130 | 2678639.9502 | 1247815.7774 | 2678632.6803 | 1247807.5417 | 2678634.0004 | 1247806.5251 | 2678631.0718 | 1247804.6738
131 | 2678639.9502 | 1247815.7774 | 2678633.5345 | 1247816.5929 | 2678625.983 | 1247820.4734 | 2678620.4473 | 1247822.1346 | 2678617.054 | 1247821.1444 | 2678616.4805 | 1247820.5664
132 | 2678616.2168 | 1247817.6419 | 2678614.9075 | 1247818.9811 | 2678616.4805 | 1247820.5664
133 | 2678613.5017 | 1247846.3823 | 2678622.4639 | 1247854.236
134 | 2678587.0454 | 1247877.0206 | 2678596.8552 | 1247885.0724

## bus_geodata
| x | y | coords
0 | 2678422.3686 | 1247746.6429
1 | 2678435.2113 | 1247725.1447
2 | 2678401.3227 | 1247782.6606
3 | 2678488.39 | 1247628.9451
4 | 2678695.2431 | 1247703.3292
5 | 2678517.5259 | 1247618.9259
6 | 2678726.0551 | 1247719.5944
7 | 2678740.0694 | 1247727.715
8 | 2678706.2938 | 1247710.1141
9 | 2678718.2157 | 1247733.5749
10 | 2678691.5694 | 1247721.72
11 | 2678702.5025 | 1247691.9209
12 | 2678796.7849 | 1247803.2959
13 | 2678786.7399 | 1247811.8815
14 | 2678740.2584 | 1247727.8245
15 | 2678707.0139 | 1247754.2779
16 | 2678703.3454 | 1247690.5963
17 | 2678478.9855 | 1248037.4157
18 | 2678472.6546 | 1248044.8012
19 | 2678488.7196 | 1248026.0601
20 | 2678582.4602 | 1247923.7716
21 | 2678504.0779 | 1248038.3168
22 | 2678594.2103 | 1247910.829
23 | 2678571.7616 | 1247914.7155
24 | 2678577.2951 | 1247950.467
25 | 2678527.6383 | 1248057.1281
26 | 2678607.6444 | 1247893.9281
27 | 2678604.499 | 1247918.9933
28 | 2678571.7091 | 1247914.6711
29 | 2678605.691 | 1247919.9392
30 | 2678614.2341 | 1247886.2544
31 | 2678596.9911 | 1247885.1839
32 | 2678603.7173 | 1247982.8069
33 | 2678603.8141 | 1247982.886
34 | 2678598.0003 | 1247978.1393
35 | 2678640.1342 | 1247966.4005
36 | 2678647.8164 | 1247978.3433
37 | 2678647.0211 | 1247959.0976
38 | 2678649.7827 | 1247979.5902
39 | 2678656.3419 | 1247948.1219
40 | 2678633.7758 | 1247947.7433
41 | 2678714.8735 | 1248055.8794
42 | 2678726.5591 | 1248074.5913
43 | 2678720.1747 | 1248043.7337
44 | 2678839.0093 | 1247962.1602
45 | 2678819.5714 | 1247937.79
46 | 2678830.1374 | 1247975.3539
47 | 2678724.2056 | 1248034.4988
48 | 2678742.7464 | 1248052.8461
49 | 2678830.4523 | 1247876.4534
50 | 2678829.8668 | 1247877.2211
51 | 2678809.5519 | 1247925.2281
52 | 2678728.2208 | 1248025.0868
53 | 2678737.397 | 1248003.5774
54 | 2678745.532 | 1247988.5517
55 | 2678765.8626 | 1247955.6945
56 | 2678776.9258 | 1247940.0172
57 | 2678667.493 | 1247934.991
58 | 2678633.7338 | 1247947.7073
59 | 2678625.9543 | 1247941.0385
60 | 2678669.7104 | 1247932.3799
61 | 2678785.0555 | 1247928.6645
62 | 2678798.6629 | 1247911.576
63 | 2678786.7265 | 1247897.9277
64 | 2678683.1669 | 1247916.5343
65 | 2678688.8528 | 1247909.8389
66 | 2678676.7966 | 1247899.7854
67 | 2678695.67 | 1247901.7374
68 | 2678667.7422 | 1247892.2349
69 | 2678712.2353 | 1247882.0512
70 | 2678659.8925 | 1247901.5112
71 | 2678700.2833 | 1247871.7738
72 | 2678713.7623 | 1247880.248
73 | 2678771.0264 | 1247879.976
74 | 2678771.0414 | 1247879.9931
75 | 2678757.8805 | 1247868.0132
76 | 2678750.8733 | 1247861.7383
77 | 2678749.9387 | 1247860.9013
78 | 2678738.6476 | 1247850.7902
79 | 2678765.8605 | 1247823.5577
80 | 2678770.8022 | 1247820.4879
81 | 2678749.861 | 1247836.2174
82 | 2678724.7327 | 1247841.2616
83 | 2678722.7741 | 1247839.9204
84 | 2678724.0909 | 1247888.6167
85 | 2678658.5957 | 1247903.0437
86 | 2678707.186 | 1247829.246
87 | 2678678.1251 | 1247809.3457
88 | 2678686.0929 | 1247794.5963
89 | 2678669.994 | 1247819.3107
90 | 2678689.5364 | 1247788.393
91 | 2678674.4804 | 1247788.2051
92 | 2678659.1685 | 1247832.5778
93 | 2678652.1137 | 1247876.1196
94 | 2678639.8589 | 1247876.5839
95 | 2678629.5768 | 1247868.3892
96 | 2678633.4586 | 1247863.8707
97 | 2678625.5714 | 1247895.4136
98 | 2678645.0964 | 1247849.8201
99 | 2678622.6948 | 1247854.4383
100 | 2678724.992 | 1247889.3468
101 | 2678727.9375 | 1247891.7334
102 | 2678699.9478 | 1247871.4853
103 | 2678690.893 | 1247863.6991
104 | 2678682.48 | 1247873.2945
105 | 2678702.0365 | 1247794.7169
106 | 2678704.7065 | 1247758.5393
107 | 2678674.0557 | 1247787.9713
108 | 2678656.5924 | 1247835.7343
109 | 2678649.3719 | 1247824.0137
110 | 2678751.4554 | 1247734.3127
111 | 2678751.3327 | 1247734.2415
112 | 2678763.5621 | 1247741.3279
113 | 2678769.7529 | 1247744.9152
114 | 2678768.122 | 1247750.7795
115 | 2678768.4124 | 1247754.8491
116 | 2678721.1413 | 1247761.8458
117 | 2678720.3115 | 1247761.4013
118 | 2678734.9163 | 1247769.5149
119 | 2678694.1447 | 1247752.9892
120 | 2678693.1802 | 1247752.4823
121 | 2678681.3269 | 1247746.2535
122 | 2678702.234 | 1247794.8167
123 | 2678662.5336 | 1247781.6299
124 | 2678649.236 | 1247823.8949
125 | 2678639.9502 | 1247815.7774
126 | 2678631.0718 | 1247804.6738
127 | 2678616.4805 | 1247820.5664
128 | 2678616.2168 | 1247817.6419
129 | 2678622.4639 | 1247854.236
130 | 2678613.5017 | 1247846.3823
131 | 2678713.4171 | 1247800.4743
132 | 2678596.8552 | 1247885.0724
133 | 2678587.0454 | 1247877.0206
134 | 2678625.9983 | 1247895.7585
135 | 2678561.562 | 1247906.0819
136 | 2678688.8528 | 1247909.8389

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97871 | -0.41084 | 0.0061317 | 0.0015367
1 | 0.97866 | -0.41177 | 0 | 0
2 | 0.97902 | -0.40462 | 0 | 0
3 | 0.97843 | -0.41627 | 0 | 0
4 | 0.98161 | -0.35395 | 0 | 0
5 | 0.97837 | -0.41746 | 0.0020458 | 0.00051273
6 | 0.9822 | -0.34224 | 0 | 0
7 | 0.98199 | -0.34648 | 0.0016635 | 0.00041691
8 | 0.98175 | -0.35117 | 0 | 0
9 | 0.98262 | -0.33409 | 0.0015867 | 0.00039768
10 | 0.98172 | -0.35179 | 0.0017582 | 0.00044065
11 | 0.98156 | -0.35484 | 0.0017038 | 0.00042703
12 | 0.99212 | -0.15012 | 0.0032501 | 0.00081454
13 | 0.99216 | -0.14936 | 0.0039156 | 0.00098135
14 | 0.98198 | -0.34653 | 0.0016864 | 0.00042264
15 | 0.98327 | -0.32147 | 0 | 0
16 | 0.98156 | -0.3549 | 0.0019554 | 0.00049007
17 | 0.98177 | -0.35089 | 0.0010493 | 0.00026297
18 | 0.98176 | -0.35098 | 0.000498 | 0.00012481
19 | 0.98179 | -0.35047 | 0 | 0
20 | 0.98225 | -0.34151 | 0 | 0
21 | 0.98175 | -0.35119 | 0 | 0
22 | 0.98237 | -0.33913 | 0 | 0
23 | 0.98219 | -0.34252 | 0.00096771 | 0.00024253
24 | 0.98164 | -0.35333 | 0.0010326 | 0.0002588
25 | 0.98172 | -0.35173 | 0.0009877 | 0.00024754
26 | 0.98265 | -0.33354 | 0 | 0
27 | 0.98228 | -0.34075 | 0.0059832 | 0.0014995
28 | 0.98219 | -0.34252 | 0.00093606 | 0.0002346
29 | 0.98228 | -0.34078 | 0.00083842 | 0.00021013
30 | 0.98282 | -0.33017 | 0 | 0
31 | 0.9826 | -0.33456 | 0.0012291 | 0.00030804
32 | 0.99471 | -0.10167 | 0.0078339 | 0.0019634
33 | 0.99472 | -0.10165 | 0.0013052 | 0.00032712
34 | 0.99471 | -0.10181 | 0.001031 | 0.00025839
35 | 0.99516 | -0.093053 | 0 | 0
36 | 0.99496 | -0.096865 | 0.0080674 | 0.0020219
37 | 0.99539 | -0.088613 | 0 | 0
38 | 0.99495 | -0.097149 | 0.0069284 | 0.0017364
39 | 0.99604 | -0.076142 | 0.0074096 | 0.001857
40 | 0.99501 | -0.096012 | 0.0086845 | 0.0021765
41 | 0.97844 | -0.41554 | 0 | 0
42 | 0.97832 | -0.41787 | 0.0057997 | 0.0014535
43 | 0.97851 | -0.41414 | 0.0049295 | 0.0012355
44 | 0.98444 | -0.29838 | 0 | 0
45 | 0.98451 | -0.29693 | 0.0051336 | 0.0012866
46 | 0.9844 | -0.29913 | 0.0025917 | 0.00064955
47 | 0.97861 | -0.41217 | 0 | 0
48 | 0.97853 | -0.41379 | 0.0033844 | 0.0008482
49 | 0.98459 | -0.29539 | 0.0030398 | 0.00076185
50 | 0.98459 | -0.29534 | 0.00318 | 0.00079698
51 | 0.98463 | -0.2947 | 0.0067913 | 0.0017021
52 | 0.97875 | -0.40954 | 0.0029685 | 0.00074398
53 | 0.97912 | -0.40228 | 0.018516 | 0.0046406
54 | 0.97968 | -0.39122 | 0.014283 | 0.0035796
55 | 0.98147 | -0.35626 | 0.0051987 | 0.0013029
56 | 0.98244 | -0.33715 | 0.014262 | 0.0035743
57 | 0.99693 | -0.059003 | 0.0081089 | 0.0020323
58 | 0.99501 | -0.096027 | 0.0074026 | 0.0018553
59 | 0.99493 | -0.097472 | 0.0080112 | 0.0020078
60 | 0.99713 | -0.055112 | 0.0082223 | 0.0020607
61 | 0.98334 | -0.31968 | 0.0056632 | 0.0014193
62 | 0.98486 | -0.29014 | 0 | 0
63 | 0.98646 | -0.25899 | 0.0017525 | 0.00043922
64 | 0.99851 | -0.028542 | 0.0064301 | 0.0016115
65 | 0.99915 | -0.016352 | 0 | 0
66 | 0.99902 | -0.018843 | 0.00096806 | 0.00024262
67 | 1 | 0 | -0.33617 | -0.085331
68 | 0.99893 | -0.020515 | 0 | 0
69 | 0.99713 | -0.05445 | 0 | 0
70 | 0.99884 | -0.022238 | 0.0066366 | 0.0016633
71 | 0.99705 | -0.0559 | 0.0011086 | 0.00027783
72 | 0.99687 | -0.059352 | 0 | 0
73 | 0.98861 | -0.21743 | 0.0027511 | 0.00068949
74 | 0.98861 | -0.21747 | 0.0028113 | 0.00070457
75 | 0.99031 | -0.1848 | 0.001515 | 0.0003797
76 | 0.99122 | -0.16734 | 0.0016787 | 0.00042073
77 | 0.99134 | -0.16497 | 0.001026 | 0.00025714
78 | 0.99284 | -0.13618 | 0 | 0
79 | 0.99233 | -0.14614 | 0.0047493 | 0.0011903
80 | 0.99228 | -0.14706 | 0.0017436 | 0.000437
81 | 0.99258 | -0.1412 | 0.0017808 | 0.00044631
82 | 0.99123 | -0.16717 | 0.00097995 | 0.0002456
83 | 0.991 | -0.1715 | 0.0014039 | 0.00035184
84 | 0.99674 | -0.061775 | 0.0014011 | 0.00035114
85 | 0.99884 | -0.02229 | 0.0014827 | 0.00037159
86 | 0.98923 | -0.20556 | 0.00098422 | 0.00024667
87 | 0.98597 | -0.26875 | 0 | 0
88 | 0.9851 | -0.28576 | 0 | 0
89 | 0.98545 | -0.27887 | 0.0014846 | 0.00037209
90 | 0.98478 | -0.29198 | 0 | 0
91 | 0.985 | -0.28761 | 0.001951 | 0.00048896
92 | 0.98478 | -0.29189 | 0 | 0
93 | 0.98332 | -0.3204 | 0.0016348 | 0.00040971
94 | 0.98335 | -0.31989 | 0.0012565 | 0.00031491
95 | 0.98339 | -0.3192 | 0 | 0
96 | 0.98354 | -0.31612 | 0 | 0
97 | 0.98273 | -0.3321 | 0.0013818 | 0.00034631
98 | 0.98409 | -0.30546 | 0.0012116 | 0.00030366
99 | 0.98349 | -0.31708 | 0.0013033 | 0.00032663
100 | 0.99673 | -0.061958 | 0.0010341 | 0.00025917
101 | 0.99671 | -0.062487 | 0.0079544 | 0.0019936
102 | 0.99705 | -0.055932 | 0.001145 | 0.00028698
103 | 0.99702 | -0.056559 | 0.0014748 | 0.00036962
104 | 0.997 | -0.056898 | 0.0015172 | 0.00038025
105 | 0.98471 | -0.29326 | 0.001068 | 0.00026766
106 | 0.98343 | -0.31831 | 0 | 0
107 | 0.985 | -0.28766 | 0.0020015 | 0.00050163
108 | 0.98465 | -0.29444 | 0.001181 | 0.00029599
109 | 0.98469 | -0.29365 | 0.0014607 | 0.0003661
110 | 0.98185 | -0.34914 | 0.0018482 | 0.00046319
111 | 0.98185 | -0.34912 | 0.00195 | 0.00048872
112 | 0.98176 | -0.35101 | 0.0018335 | 0.00045952
113 | 0.98172 | -0.35172 | 0 | 0
114 | 0.98169 | -0.35234 | 0.0020074 | 0.00050311
115 | 0.98167 | -0.3526 | 0.0035251 | 0.00088347
116 | 0.98317 | -0.32331 | 0.0017823 | 0.00044668
117 | 0.98318 | -0.32322 | 0.0012914 | 0.00032366
118 | 0.98312 | -0.32427 | 0.0033639 | 0.00084307
119 | 0.98335 | -0.31994 | 0.0019451 | 0.00048748
120 | 0.98334 | -0.32005 | 0.0018861 | 0.00047269
121 | 0.98329 | -0.32095 | 0.003727 | 0.00093407
122 | 0.98471 | -0.29327 | 0.0014043 | 0.00035195
123 | 0.98495 | -0.28856 | 0.0038158 | 0.00095634
124 | 0.98469 | -0.29367 | 0.0016786 | 0.00042071
125 | 0.98464 | -0.29463 | 0 | 0
126 | 0.98461 | -0.29522 | 0.0020223 | 0.00050683
127 | 0.98459 | -0.29569 | 0.0010196 | 0.00025554
128 | 0.98459 | -0.29579 | 0.0013179 | 0.0003303
129 | 0.98349 | -0.31709 | 0.0014226 | 0.00035653
130 | 0.98348 | -0.3173 | 0.00098491 | 0.00024684
131 | 0.98468 | -0.29386 | 0.0026073 | 0.00065344
132 | 0.9826 | -0.33457 | 0.00095391 | 0.00023907
133 | 0.98258 | -0.33502 | 0.001938 | 0.0004857
134 | 0.98272 | -0.33216 | 0.0059799 | 0.0014987
135 | 0.98217 | -0.34302 | 0.0020607 | 0.00051647
136 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0020465 | 0.00051091 | -0.0020464 | -0.00051117 | 9.0874e-08 | -2.5652e-07 | 0.0031107 | 0.0031108 | 0.0031108 | 0.97871 | -0.41084 | 0.97866 | -0.41177 | 0.85462
1 | -0.0081782 | -0.0020477 | 0.0081806 | 0.0020487 | 2.4188e-06 | 1.0235e-06 | 0.012433 | 0.012433 | 0.012433 | 0.97871 | -0.41084 | 0.97902 | -0.40462 | 3.4157
2 | 0.0020464 | 0.00051117 | -0.0020459 | -0.0005124 | 4.3835e-07 | -1.2366e-06 | 0.0031108 | 0.0031114 | 0.0031114 | 0.97866 | -0.41177 | 0.97843 | -0.41627 | 0.85477
3 | -0.0081806 | -0.0020487 | 0.0082004 | 0.002057 | 1.9774e-05 | 8.3541e-06 | 0.012433 | 0.012432 | 0.012433 | 0.97902 | -0.40462 | 0.98161 | -0.35395 | 3.4157
4 | 0.0020459 | 0.0005124 | -0.0020458 | -0.00051273 | 1.1499e-07 | -3.242e-07 | 0.0031114 | 0.0031115 | 0.0031115 | 0.97843 | -0.41627 | 0.97837 | -0.41746 | 0.85481
5 | 0.0036594 | 0.000917 | -0.0036592 | -0.00091707 | 1.5604e-07 | -7.1062e-08 | 0.0055472 | 0.0055473 | 0.0055473 | 0.98161 | -0.35395 | 0.98156 | -0.35484 | 1.524
6 | -0.01186 | -0.002974 | 0.011861 | 0.0029749 | 1.5684e-06 | 8.4018e-07 | 0.017979 | 0.017979 | 0.017979 | 0.98161 | -0.35395 | 0.98175 | -0.35117 | 4.9392
7 | 0.014519 | 0.0036402 | -0.014516 | -0.0036386 | 2.939e-06 | 1.676e-06 | 0.021997 | 0.021997 | 0.021997 | 0.9822 | -0.34224 | 0.98199 | -0.34648 | 6.0432
8 | 0.013625 | 0.0034186 | -0.01362 | -0.0034153 | 5.8046e-06 | 3.2555e-06 | 0.020643 | 0.020644 | 0.020644 | 0.9822 | -0.34224 | 0.98175 | -0.35117 | 5.6713
9 | -0.028145 | -0.0070588 | 0.028156 | 0.0070656 | 1.0931e-05 | 6.7927e-06 | 0.042641 | 0.04264 | 0.042641 | 0.9822 | -0.34224 | 0.98262 | -0.33409 | 11.7144
10 | 0.012853 | 0.0032217 | -0.012853 | -0.0032217 | 3.1075e-08 | 1.7124e-08 | 0.019476 | 0.019476 | 0.019476 | 0.98199 | -0.34648 | 0.98198 | -0.34653 | 5.3507
11 | 0.0017583 | 0.00044044 | -0.0017582 | -0.00044065 | 5.1207e-08 | -2.1035e-07 | 0.0026649 | 0.002665 | 0.002665 | 0.98175 | -0.35117 | 0.98172 | -0.35179 | 0.73213
12 | -0.029742 | -0.0074633 | 0.02976 | 0.0074745 | 1.791e-05 | 1.1164e-05 | 0.045043 | 0.045043 | 0.045043 | 0.98262 | -0.33409 | 0.98327 | -0.32147 | 12.3745
13 | 0.0019554 | 0.00049005 | -0.0019554 | -0.00049007 | 5.1735e-09 | -1.6534e-08 | 0.0029643 | 0.0029643 | 0.0029643 | 0.98156 | -0.35484 | 0.98156 | -0.3549 | 0.81437
14 | -0.0032501 | -0.00081454 | 0.0032502 | 0.00081445 | 1.1774e-07 | -9.5291e-08 | 0.0048746 | 0.0048745 | 0.0048746 | 0.99212 | -0.15012 | 0.99216 | -0.14936 | 1.3392
15 | -0.0071658 | -0.0017958 | 0.0071666 | 0.0017961 | 7.8554e-07 | 2.6849e-07 | 0.010747 | 0.010747 | 0.010747 | 0.99216 | -0.14936 | 0.99228 | -0.14706 | 2.9525
16 | 0.011167 | 0.002799 | -0.011165 | -0.0027983 | 1.3743e-06 | 7.1763e-07 | 0.016921 | 0.016921 | 0.016921 | 0.98198 | -0.34653 | 0.98185 | -0.34912 | 4.6487
17 | -0.036199 | -0.0090879 | 0.036204 | 0.0090913 | 5.4512e-06 | 3.4273e-06 | 0.054786 | 0.054786 | 0.054786 | 0.98327 | -0.32147 | 0.98343 | -0.31831 | 15.0512
18 | 0.0064383 | 0.0016135 | -0.0064378 | -0.0016133 | 5.3703e-07 | 1.5238e-07 | 0.0097433 | 0.0097433 | 0.0097433 | 0.98327 | -0.32147 | 0.98318 | -0.32322 | 2.6767
19 | 0.000498 | 0.00012469 | -0.000498 | -0.00012481 | 2.0781e-09 | -1.2168e-07 | 0.00075475 | 0.0007548 | 0.0007548 | 0.98177 | -0.35089 | 0.98176 | -0.35098 | 0.20736
20 | -0.0015473 | -0.00038766 | 0.0015473 | 0.00038749 | 3.0844e-08 | -1.6939e-07 | 0.0023451 | 0.002345 | 0.0023451 | 0.98177 | -0.35089 | 0.98179 | -0.35047 | 0.64425
21 | -0.0035678 | -0.00089189 | 0.0035694 | 0.00089111 | 1.519e-06 | -7.8118e-07 | 0.0054067 | 0.005406 | 0.0054067 | 0.98179 | -0.35047 | 0.98225 | -0.34151 | 1.4853
22 | 0.0020205 | 0.0005044 | -0.0020205 | -0.0005046 | 6.8948e-08 | -2.039e-07 | 0.0030617 | 0.0030617 | 0.0030617 | 0.98179 | -0.35047 | 0.98175 | -0.35119 | 0.84114
23 | -0.0075341 | -0.0018845 | 0.0075349 | 0.0018848 | 8.5268e-07 | 3.247e-07 | 0.011412 | 0.011412 | 0.011412 | 0.98225 | -0.34151 | 0.98237 | -0.33913 | 3.1352
24 | 0.0039647 | 0.0009934 | -0.0039645 | -0.00099346 | 1.8962e-07 | -5.6056e-08 | 0.0060061 | 0.0060062 | 0.0060062 | 0.98225 | -0.34151 | 0.98219 | -0.34252 | 1.6501
25 | 0.0010327 | 0.00025742 | -0.0010326 | -0.0002588 | 1.0509e-07 | -1.3793e-06 | 0.0015648 | 0.0015653 | 0.0015653 | 0.98175 | -0.35119 | 0.98164 | -0.35333 | 0.43003
26 | 0.00098773 | 0.00024718 | -0.0009877 | -0.00024754 | 2.5337e-08 | -3.65e-07 | 0.0014969 | 0.0014971 | 0.0014971 | 0.98175 | -0.35119 | 0.98172 | -0.35173 | 0.41128
27 | -0.014357 | -0.0035947 | 0.014361 | 0.0035968 | 3.8246e-06 | 2.1746e-06 | 0.021746 | 0.021746 | 0.021746 | 0.98237 | -0.33913 | 0.98265 | -0.33354 | 5.9741
28 | 0.0068222 | 0.0017098 | -0.0068217 | -0.0017096 | 5.2597e-07 | 1.7034e-07 | 0.010334 | 0.010334 | 0.010334 | 0.98237 | -0.33913 | 0.98228 | -0.34075 | 2.839
29 | 0.0029968 | 0.00075093 | -0.0029968 | -0.00075093 | 5.3143e-10 | -5.3008e-10 | 0.0045401 | 0.0045401 | 0.0045401 | 0.98219 | -0.34252 | 0.98219 | -0.34252 | 1.2473
30 | -0.018482 | -0.0046295 | 0.018485 | 0.0046312 | 2.9674e-06 | 1.7711e-06 | 0.027986 | 0.027986 | 0.027986 | 0.98265 | -0.33354 | 0.98282 | -0.33017 | 7.6885
31 | 0.0041212 | 0.0010326 | -0.004121 | -0.0010327 | 2.0128e-07 | -4.5765e-08 | 0.0062406 | 0.0062406 | 0.0062406 | 0.98265 | -0.33354 | 0.9826 | -0.33456 | 1.7145
32 | 0.00083842 | 0.00021011 | -0.00083842 | -0.00021013 | 9.2055e-10 | -1.8674e-08 | 0.0012701 | 0.0012701 | 0.0012701 | 0.98228 | -0.34075 | 0.98228 | -0.34078 | 0.34892
33 | 0.0020608 | 0.00051633 | -0.0020607 | -0.00051647 | 4.8593e-08 | -1.3715e-07 | 0.003122 | 0.0031221 | 0.0031221 | 0.98219 | -0.34252 | 0.98217 | -0.34302 | 0.85771
34 | 0.0073624 | 0.0018453 | -0.0073617 | -0.001845 | 6.7911e-07 | 2.4995e-07 | 0.011147 | 0.011147 | 0.011147 | 0.98282 | -0.33017 | 0.98273 | -0.3321 | 3.0623
35 | -0.025848 | -0.0064765 | 0.025861 | 0.0064848 | 1.3509e-05 | 8.3473e-06 | 0.039133 | 0.039133 | 0.039133 | 0.98282 | -0.33017 | 0.98339 | -0.3192 | 10.7509
36 | 0.0028919 | 0.00072463 | -0.0028919 | -0.00072463 | 1.2641e-09 | -1.4177e-09 | 0.0043793 | 0.0043794 | 0.0043794 | 0.9826 | -0.33456 | 0.9826 | -0.33457 | 1.2031
37 | -0.0088649 | -0.0022217 | 0.0088649 | 0.0022217 | 8.2429e-09 | 3.6517e-09 | 0.013261 | 0.013261 | 0.013261 | 0.99471 | -0.10167 | 0.99472 | -0.10165 | 3.6432
38 | 0.001031 | 0.0002583 | -0.001031 | -0.00025839 | 6.5833e-09 | -9.159e-08 | 0.0015423 | 0.0015423 | 0.0015423 | 0.99471 | -0.10167 | 0.99471 | -0.10181 | 0.42371
39 | -0.01017 | -0.0025488 | 0.010174 | 0.0025508 | 4.1691e-06 | 2.0444e-06 | 0.015214 | 0.015213 | 0.015214 | 0.99472 | -0.10165 | 0.99516 | -0.093053 | 4.1796
40 | 0.014999 | 0.0037599 | -0.014996 | -0.0037583 | 2.724e-06 | 1.5558e-06 | 0.022427 | 0.022427 | 0.022427 | 0.99516 | -0.093053 | 0.99496 | -0.096865 | 6.1613
41 | -0.025173 | -0.0063107 | 0.025178 | 0.006314 | 5.3263e-06 | 3.2786e-06 | 0.03764 | 0.03764 | 0.03764 | 0.99516 | -0.093053 | 0.99539 | -0.088613 | 10.3408
42 | 0.0069285 | 0.0017364 | -0.0069284 | -0.0017364 | 9.3744e-08 | 2.9758e-08 | 0.010362 | 0.010362 | 0.010362 | 0.99496 | -0.096865 | 0.99495 | -0.097149 | 2.8467
43 | -0.049286 | -0.012359 | 0.049315 | 0.012378 | 2.9314e-05 | 1.8573e-05 | 0.07368 | 0.07368 | 0.07368 | 0.99539 | -0.088613 | 0.99604 | -0.076142 | 20.2417
44 | 0.024107 | 0.006045 | -0.024099 | -0.0060398 | 8.4972e-06 | 5.2115e-06 | 0.036039 | 0.036039 | 0.036039 | 0.99539 | -0.088613 | 0.99501 | -0.096012 | 9.9009
45 | -0.056724 | -0.014235 | 0.056771 | 0.014264 | 4.6399e-05 | 2.9471e-05 | 0.084749 | 0.084749 | 0.084749 | 0.99604 | -0.076142 | 0.99693 | -0.059003 | 23.2827
46 | 0.015414 | 0.0038633 | -0.015414 | -0.0038633 | 1.1021e-08 | 6.3378e-09 | 0.023052 | 0.023052 | 0.023052 | 0.99501 | -0.096012 | 0.99501 | -0.096027 | 6.3329
47 | 0.0058003 | 0.0014537 | -0.0057997 | -0.0014535 | 6.4428e-07 | 1.3506e-07 | 0.0088212 | 0.0088213 | 0.0088213 | 0.97844 | -0.41554 | 0.97832 | -0.41787 | 2.4234
48 | -0.0058003 | -0.0014537 | 0.0058007 | 0.0014538 | 3.8669e-07 | 8.1028e-08 | 0.0088212 | 0.0088211 | 0.0088212 | 0.97844 | -0.41554 | 0.97851 | -0.41414 | 2.4234
49 | -0.01073 | -0.0026892 | 0.010731 | 0.0026897 | 1.0061e-06 | 5.173e-07 | 0.016317 | 0.016317 | 0.016317 | 0.97851 | -0.41414 | 0.97861 | -0.41217 | 4.4828
50 | -0.0025918 | -0.00064941 | 0.002592 | 0.00064913 | 1.794e-07 | -2.8154e-07 | 0.0039176 | 0.0039175 | 0.0039176 | 0.98444 | -0.29838 | 0.98451 | -0.29693 | 1.0763
51 | 0.0025918 | 0.00064941 | -0.0025917 | -0.00064955 | 9.1603e-08 | -1.4372e-07 | 0.0039176 | 0.0039177 | 0.0039177 | 0.98444 | -0.29838 | 0.9844 | -0.29913 | 1.0763
52 | -0.0077256 | -0.0019357 | 0.0077264 | 0.0019361 | 8.2154e-07 | 3.2144e-07 | 0.011677 | 0.011676 | 0.011677 | 0.98451 | -0.29693 | 0.98463 | -0.2947 | 3.2078
53 | -0.014116 | -0.0035378 | 0.014118 | 0.0035388 | 1.7678e-06 | 1.0028e-06 | 0.021464 | 0.021464 | 0.021464 | 0.97861 | -0.41217 | 0.97875 | -0.40954 | 5.8966
54 | 0.0033846 | 0.00084804 | -0.0033844 | -0.0008482 | 2.6005e-07 | -1.6251e-07 | 0.0051464 | 0.0051465 | 0.0051465 | 0.97861 | -0.41217 | 0.97853 | -0.41379 | 1.4139
55 | -0.0030398 | -0.00076185 | 0.0030398 | 0.00076184 | 7.641e-09 | -7.3883e-09 | 0.0045941 | 0.0045941 | 0.0045941 | 0.98459 | -0.29539 | 0.98459 | -0.29534 | 1.2621
56 | -0.0062198 | -0.0015588 | 0.0062213 | 0.0015592 | 1.5398e-06 | 3.9428e-07 | 0.0094 | 0.0093998 | 0.0094 | 0.98459 | -0.29534 | 0.98486 | -0.29014 | 2.5824
57 | -0.014518 | -0.0036381 | 0.014521 | 0.0036399 | 3.1522e-06 | 1.7952e-06 | 0.02194 | 0.02194 | 0.02194 | 0.98463 | -0.2947 | 0.98486 | -0.29014 | 6.0274
58 | -0.017086 | -0.0042827 | 0.017092 | 0.0042862 | 5.9175e-06 | 3.4932e-06 | 0.025977 | 0.025977 | 0.025977 | 0.97875 | -0.40954 | 0.97912 | -0.40228 | 7.1365
59 | -0.035608 | -0.0089269 | 0.035627 | 0.0089387 | 1.8765e-05 | 1.1795e-05 | 0.054117 | 0.054117 | 0.054117 | 0.97912 | -0.40228 | 0.97968 | -0.39122 | 14.8673
60 | -0.04991 | -0.012518 | 0.049993 | 0.012571 | 8.3328e-05 | 5.2842e-05 | 0.075811 | 0.07581 | 0.075811 | 0.97968 | -0.39122 | 0.98147 | -0.35626 | 20.8271
61 | -0.055192 | -0.013874 | 0.055242 | 0.013906 | 5.0406e-05 | 3.2017e-05 | 0.083692 | 0.083692 | 0.083692 | 0.98147 | -0.35626 | 0.98244 | -0.33715 | 22.9924
62 | -0.069504 | -0.01748 | 0.069562 | 0.017517 | 5.8053e-05 | 3.6977e-05 | 0.10529 | 0.10529 | 0.10529 | 0.98244 | -0.33715 | 0.98334 | -0.31968 | 28.9267
63 | -0.06488 | -0.016296 | 0.064892 | 0.016304 | 1.205e-05 | 7.6673e-06 | 0.096852 | 0.096852 | 0.096852 | 0.99693 | -0.059003 | 0.99713 | -0.055112 | 26.6078
64 | 0.0080117 | 0.002008 | -0.0080112 | -0.0020078 | 5.5161e-07 | 2.1995e-07 | 0.011981 | 0.011981 | 0.011981 | 0.99501 | -0.096027 | 0.99493 | -0.097472 | 3.2916
65 | -0.073114 | -0.018365 | 0.073207 | 0.018424 | 9.2829e-05 | 5.9139e-05 | 0.10912 | 0.10912 | 0.10912 | 0.99713 | -0.055112 | 0.99851 | -0.028542 | 29.9787
66 | -0.075225 | -0.018937 | 0.075332 | 0.019004 | 0.0001064 | 6.7815e-05 | 0.11386 | 0.11386 | 0.11386 | 0.98334 | -0.31968 | 0.98486 | -0.29014 | 31.281
67 | -0.096074 | -0.024204 | 0.096217 | 0.024295 | 0.00014335 | 9.1516e-05 | 0.1452 | 0.1452 | 0.1452 | 0.98486 | -0.29014 | 0.98646 | -0.25899 | 39.8907
68 | -0.09797 | -0.024734 | 0.098165 | 0.024859 | 0.0001953 | 0.00012469 | 0.14785 | 0.14785 | 0.14785 | 0.98646 | -0.25899 | 0.98861 | -0.21747 | 40.6169
69 | -0.079637 | -0.020035 | 0.079683 | 0.020065 | 4.6415e-05 | 2.9591e-05 | 0.1187 | 0.1187 | 0.1187 | 0.99851 | -0.028542 | 0.99915 | -0.016352 | 32.6112
70 | 0.0090897 | 0.0022785 | -0.0090886 | -0.002278 | 1.0788e-06 | 4.8486e-07 | 0.013537 | 0.013537 | 0.013537 | 0.99915 | -0.016352 | 0.99902 | -0.018843 | 3.7191
71 | -0.088773 | -0.022343 | 0.088843 | 0.022388 | 6.9437e-05 | 4.4301e-05 | 0.13224 | 0.13224 | 0.13224 | 0.99915 | -0.016352 | 1 | 0 | 36.3302
72 | 0.0081206 | 0.0020354 | -0.0081199 | -0.0020351 | 6.468e-07 | 2.596e-07 | 0.012095 | 0.012096 | 0.012096 | 0.99902 | -0.018843 | 0.99893 | -0.020515 | 3.3229
73 | 0.24567 | 0.062943 | -0.24503 | -0.06253 | 0.0006464 | 0.00041302 | 0.36605 | 0.36605 | 0.36605 | 1 | 0 | 0.99713 | -0.05445 | 50.282
74 | 0.0081199 | 0.0020351 | -0.0081192 | -0.0020348 | 6.6669e-07 | 2.6761e-07 | 0.012096 | 0.012096 | 0.012096 | 0.99893 | -0.020515 | 0.99884 | -0.022238 | 3.323
75 | 0.0052461 | 0.0013145 | -0.0052457 | -0.0013144 | 3.6229e-07 | 2.6265e-08 | 0.0078287 | 0.0078287 | 0.0078287 | 0.99713 | -0.05445 | 0.99705 | -0.0559 | 2.1507
76 | 0.23978 | 0.061216 | -0.23972 | -0.06118 | 5.6784e-05 | 3.628e-05 | 0.35822 | 0.35822 | 0.35822 | 0.99713 | -0.05445 | 0.99687 | -0.059352 | 49.2066
77 | 0.0014827 | 0.00037156 | -0.0014827 | -0.00037159 | 3.6728e-09 | -2.3925e-08 | 0.0022088 | 0.0022088 | 0.0022088 | 0.99884 | -0.022238 | 0.99884 | -0.02229 | 0.60681
78 | 0.0041372 | 0.0010366 | -0.0041372 | -0.0010366 | 6.3257e-09 | -1.7225e-09 | 0.0061743 | 0.0061743 | 0.0061743 | 0.99705 | -0.0559 | 0.99705 | -0.055932 | 1.6962
79 | 0.010391 | 0.0026046 | -0.01039 | -0.002604 | 1.1993e-06 | 5.9428e-07 | 0.015511 | 0.015511 | 0.015511 | 0.99687 | -0.059352 | 0.99674 | -0.061775 | 4.2612
80 | 0.22933 | 0.058575 | -0.22848 | -0.058033 | 0.00084828 | 0.0005419 | 0.34271 | 0.34271 | 0.34271 | 0.99687 | -0.059352 | 0.99284 | -0.13618 | 47.0761
81 | 0.10098 | 0.025564 | -0.10098 | -0.025564 | 1.9664e-07 | 1.2556e-07 | 0.15208 | 0.15208 | 0.15208 | 0.98861 | -0.21743 | 0.98861 | -0.21747 | 41.7794
82 | -0.10373 | -0.026253 | 0.10389 | 0.026357 | 0.00016274 | 0.00010392 | 0.15622 | 0.15622 | 0.15622 | 0.98861 | -0.21743 | 0.99031 | -0.1848 | 42.917
83 | -0.10541 | -0.026737 | 0.10549 | 0.026793 | 8.8607e-05 | 5.6588e-05 | 0.15849 | 0.15849 | 0.15849 | 0.99031 | -0.1848 | 0.99122 | -0.16734 | 43.5423
84 | -0.10717 | -0.027214 | 0.10718 | 0.027222 | 1.2197e-05 | 7.7899e-06 | 0.16101 | 0.16101 | 0.16101 | 0.99122 | -0.16734 | 0.99134 | -0.16497 | 44.2347
85 | -0.10821 | -0.027479 | 0.10836 | 0.027575 | 0.00015019 | 9.5923e-05 | 0.16255 | 0.16255 | 0.16255 | 0.99134 | -0.16497 | 0.99284 | -0.13618 | 44.6577
86 | 0.10468 | 0.026584 | -0.10452 | -0.026485 | 0.0001559 | 9.9559e-05 | 0.15701 | 0.15701 | 0.15701 | 0.99284 | -0.13618 | 0.99123 | -0.16717 | 43.1338
87 | 0.015448 | 0.0038738 | -0.015444 | -0.0038716 | 3.6963e-06 | 2.1279e-06 | 0.023153 | 0.023153 | 0.023153 | 0.99284 | -0.13618 | 0.99258 | -0.1412 | 6.3607
88 | 0.0089106 | 0.0022332 | -0.0089102 | -0.0022331 | 3.8949e-07 | 1.7412e-07 | 0.013362 | 0.013362 | 0.013362 | 0.99233 | -0.14614 | 0.99228 | -0.14706 | 3.6708
89 | -0.01366 | -0.0034235 | 0.013663 | 0.0034253 | 3.218e-06 | 1.7952e-06 | 0.020483 | 0.020483 | 0.020483 | 0.99233 | -0.14614 | 0.99258 | -0.1412 | 5.6273
90 | 0.10354 | 0.026239 | -0.10352 | -0.026226 | 2.1535e-05 | 1.3752e-05 | 0.15554 | 0.15554 | 0.15554 | 0.99123 | -0.16717 | 0.991 | -0.1715 | 42.7297
91 | 0.10211 | 0.025874 | -0.10195 | -0.025767 | 0.00016678 | 0.00010649 | 0.15343 | 0.15343 | 0.15343 | 0.991 | -0.1715 | 0.98923 | -0.20556 | 42.1506
92 | 0.0089888 | 0.0022529 | -0.0089887 | -0.0022528 | 7.8322e-08 | 3.5009e-08 | 0.013419 | 0.013419 | 0.013419 | 0.99674 | -0.061775 | 0.99673 | -0.061958 | 3.6866
93 | 0.10096 | 0.025521 | -0.10066 | -0.025326 | 0.00030495 | 0.00019472 | 0.15195 | 0.15195 | 0.15195 | 0.98923 | -0.20556 | 0.98597 | -0.26875 | 41.7439
94 | 0.056728 | 0.014279 | -0.056682 | -0.01425 | 4.6076e-05 | 2.9275e-05 | 0.085635 | 0.085635 | 0.085635 | 0.98597 | -0.26875 | 0.9851 | -0.28576 | 23.5261
95 | 0.043931 | 0.011047 | -0.04391 | -0.011033 | 2.1209e-05 | 1.341e-05 | 0.066313 | 0.066313 | 0.066313 | 0.98597 | -0.26875 | 0.98545 | -0.27887 | 18.2179
96 | 0.048912 | 0.012303 | -0.048898 | -0.012294 | 1.4522e-05 | 9.2037e-06 | 0.073899 | 0.073899 | 0.073899 | 0.9851 | -0.28576 | 0.98478 | -0.29198 | 20.302
97 | 0.0077692 | 0.0019471 | -0.0077685 | -0.0019469 | 6.8458e-07 | 2.6939e-07 | 0.011736 | 0.011736 | 0.011736 | 0.9851 | -0.28576 | 0.985 | -0.28761 | 3.2241
98 | 0.042425 | 0.010661 | -0.042399 | -0.010645 | 2.636e-05 | 1.6652e-05 | 0.064071 | 0.064071 | 0.064071 | 0.98545 | -0.27887 | 0.98478 | -0.29189 | 17.602
99 | 0.0050799 | 0.001273 | -0.0050796 | -0.0012729 | 3.0951e-07 | 1.9868e-08 | 0.0076758 | 0.0076759 | 0.0076759 | 0.98478 | -0.29198 | 0.98471 | -0.29326 | 2.1088
100 | 0.043818 | 0.011021 | -0.043763 | -0.010986 | 5.5046e-05 | 3.4804e-05 | 0.066224 | 0.066224 | 0.066224 | 0.98478 | -0.29198 | 0.98343 | -0.31831 | 18.1933
101 | 0.0058175 | 0.0014579 | -0.0058175 | -0.0014579 | 1.4039e-08 | 2.8154e-09 | 0.0087883 | 0.0087883 | 0.0087883 | 0.985 | -0.28761 | 0.985 | -0.28766 | 2.4144
102 | 0.034899 | 0.0087653 | -0.034894 | -0.0087626 | 4.2495e-06 | 2.6678e-06 | 0.052739 | 0.052739 | 0.052739 | 0.98478 | -0.29189 | 0.98465 | -0.29444 | 14.4887
103 | 0.0075002 | 0.0018792 | -0.0074996 | -0.001879 | 6.2669e-07 | 2.3554e-07 | 0.011333 | 0.011333 | 0.011333 | 0.98478 | -0.29189 | 0.98469 | -0.29365 | 3.1134
104 | -0.0016348 | -0.00040971 | 0.0016348 | 0.00040951 | 3.9772e-08 | -1.9441e-07 | 0.0024738 | 0.0024737 | 0.0024738 | 0.98332 | -0.3204 | 0.98335 | -0.31989 | 0.67961
105 | -0.0028913 | -0.00072442 | 0.0028914 | 0.00072432 | 9.4376e-08 | -1.064e-07 | 0.0043751 | 0.004375 | 0.0043751 | 0.98335 | -0.31989 | 0.98339 | -0.3192 | 1.2019
106 | -0.028752 | -0.0072092 | 0.028757 | 0.0072118 | 4.2236e-06 | 2.6276e-06 | 0.043508 | 0.043508 | 0.043508 | 0.98339 | -0.3192 | 0.98354 | -0.31612 | 11.9528
107 | -0.032468 | -0.0081416 | 0.032484 | 0.0081519 | 1.651e-05 | 1.0335e-05 | 0.049122 | 0.049122 | 0.049122 | 0.98354 | -0.31612 | 0.98409 | -0.30546 | 13.4951
108 | 0.0037109 | 0.00092978 | -0.0037107 | -0.00092985 | 1.6916e-07 | -7.3358e-08 | 0.0056142 | 0.0056143 | 0.0056143 | 0.98354 | -0.31612 | 0.98349 | -0.31708 | 1.5424
109 | 0.0059799 | 0.0014987 | -0.0059799 | -0.0014987 | 1.6876e-08 | 3.8458e-09 | 0.0090546 | 0.0090546 | 0.0090546 | 0.98273 | -0.3321 | 0.98272 | -0.33216 | 2.4875
110 | -0.033696 | -0.0084556 | 0.033713 | 0.0084667 | 1.7702e-05 | 1.1098e-05 | 0.050954 | 0.050954 | 0.050954 | 0.98409 | -0.30546 | 0.98465 | -0.29444 | 13.9984
111 | 0.0024075 | 0.00060322 | -0.0024075 | -0.00060323 | 1.5269e-09 | -2.9172e-09 | 0.0036425 | 0.0036425 | 0.0036425 | 0.98349 | -0.31708 | 0.98349 | -0.31709 | 1.0007
112 | 0.0079546 | 0.0019937 | -0.0079544 | -0.0019936 | 2.0048e-07 | 7.8901e-08 | 0.011875 | 0.011875 | 0.011875 | 0.99673 | -0.061958 | 0.99671 | -0.062487 | 3.2625
113 | 0.0029921 | 0.00074962 | -0.002992 | -0.00074972 | 8.9298e-08 | -9.8594e-08 | 0.0044654 | 0.0044655 | 0.0044655 | 0.99705 | -0.055932 | 0.99702 | -0.056559 | 1.2268
114 | 0.0015172 | 0.0003801 | -0.0015172 | -0.00038025 | 2.4537e-08 | -1.5071e-07 | 0.0022644 | 0.0022644 | 0.0022644 | 0.99702 | -0.056559 | 0.997 | -0.056898 | 0.62209
115 | 0.0040116 | 0.0010053 | -0.0040116 | -0.0010053 | 3.049e-09 | -8.6389e-10 | 0.006062 | 0.006062 | 0.006062 | 0.98471 | -0.29326 | 0.98471 | -0.29327 | 1.6654
116 | 0.0075589 | 0.0018944 | -0.0075583 | -0.0018942 | 5.8528e-07 | 2.2321e-07 | 0.011437 | 0.011437 | 0.011437 | 0.98343 | -0.31831 | 0.98335 | -0.31994 | 3.1421
117 | 0.003816 | 0.00095628 | -0.0038158 | -0.00095634 | 1.639e-07 | -6.2503e-08 | 0.0057647 | 0.0057648 | 0.0057648 | 0.985 | -0.28766 | 0.98495 | -0.28856 | 1.5837
118 | 0.0060388 | 0.0015129 | -0.0060388 | -0.0015129 | 5.6346e-09 | 1.3114e-09 | 0.0091253 | 0.0091253 | 0.0091253 | 0.98469 | -0.29365 | 0.98469 | -0.29367 | 2.507
119 | -0.0092152 | -0.0023096 | 0.0092153 | 0.0023096 | 1.0377e-08 | 4.8473e-09 | 0.013966 | 0.013966 | 0.013966 | 0.98185 | -0.34914 | 0.98185 | -0.34912 | 3.8368
120 | 0.0073671 | 0.0018464 | -0.0073664 | -0.0018461 | 6.5409e-07 | 2.4167e-07 | 0.011165 | 0.011165 | 0.011165 | 0.98185 | -0.34914 | 0.98176 | -0.35101 | 3.0673
121 | 0.0055329 | 0.0013866 | -0.0055327 | -0.0013866 | 1.887e-07 | 3.0294e-08 | 0.0083861 | 0.0083861 | 0.0083861 | 0.98176 | -0.35101 | 0.98172 | -0.35172 | 2.3039
122 | 0.0055327 | 0.0013866 | -0.0055326 | -0.0013866 | 1.6279e-07 | 2.6141e-08 | 0.0083861 | 0.0083861 | 0.0083861 | 0.98172 | -0.35172 | 0.98169 | -0.35234 | 2.3039
123 | 0.0035251 | 0.00088345 | -0.0035251 | -0.00088347 | 4.3682e-08 | -2.3626e-08 | 0.0053433 | 0.0053433 | 0.0053433 | 0.98169 | -0.35234 | 0.98167 | -0.3526 | 1.4679
124 | -0.0051463 | -0.0012896 | 0.0051463 | 0.0012896 | 2.1418e-08 | 1.7681e-09 | 0.0077888 | 0.0077888 | 0.0077888 | 0.98317 | -0.32331 | 0.98318 | -0.32322 | 2.1398
125 | 0.003364 | 0.00084296 | -0.0033639 | -0.00084307 | 1.5332e-07 | -1.0188e-07 | 0.0050914 | 0.0050914 | 0.0050914 | 0.98317 | -0.32331 | 0.98312 | -0.32427 | 1.3987
126 | 0.0056132 | 0.0014067 | -0.0056132 | -0.0014067 | 2.948e-08 | 5.0444e-09 | 0.008494 | 0.008494 | 0.008494 | 0.98335 | -0.31994 | 0.98334 | -0.32005 | 2.3335
127 | 0.0037271 | 0.000934 | -0.003727 | -0.00093407 | 1.5973e-07 | -6.7633e-08 | 0.00564 | 0.00564 | 0.00564 | 0.98334 | -0.32005 | 0.98329 | -0.32095 | 1.5495
128 | 0.0026073 | 0.00065333 | -0.0026073 | -0.00065344 | 7.2956e-08 | -1.1273e-07 | 0.0039399 | 0.00394 | 0.00394 | 0.98471 | -0.29327 | 0.98468 | -0.29386 | 1.0824
129 | 0.0043602 | 0.0010922 | -0.00436 | -0.0010922 | 2.0078e-07 | -2.8386e-08 | 0.0065886 | 0.0065887 | 0.0065887 | 0.98469 | -0.29367 | 0.98464 | -0.29463 | 1.8101
130 | 0.0020223 | 0.00050667 | -0.0020223 | -0.00050683 | 5.636e-08 | -1.6859e-07 | 0.0030562 | 0.0030562 | 0.0030562 | 0.98464 | -0.29463 | 0.98461 | -0.29522 | 0.83962
131 | 0.0023376 | 0.00058554 | -0.0023375 | -0.00058578 | 1.174e-07 | -2.4393e-07 | 0.0035326 | 0.0035327 | 0.0035327 | 0.98464 | -0.29463 | 0.98459 | -0.29569 | 0.97051
132 | 0.0013179 | 0.00033025 | -0.0013179 | -0.0003303 | 6.1086e-09 | -4.8314e-08 | 0.0019917 | 0.0019918 | 0.0019918 | 0.98459 | -0.29569 | 0.98459 | -0.29579 | 0.54719
133 | 0.00098492 | 0.0002467 | -0.00098491 | -0.00024684 | 9.9228e-09 | -1.4487e-07 | 0.0014901 | 0.0014902 | 0.0014902 | 0.98349 | -0.31709 | 0.98348 | -0.3173 | 0.40939
134 | 0.001938 | 0.00048556 | -0.001938 | -0.0004857 | 4.0991e-08 | -1.3452e-07 | 0.0029348 | 0.0029348 | 0.0029348 | 0.9826 | -0.33457 | 0.98258 | -0.33502 | 0.80627

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.33739 | 0.085639

## res_load
| p_mw | q_mvar
0 | 0.0061317 | 0.0015367
1 | 0.0020458 | 0.00051273
2 | 0.0016635 | 0.00041691
3 | 0.0015867 | 0.00039768
4 | 0.0017582 | 0.00044065
5 | 0.0017038 | 0.00042703
6 | 0.0032501 | 0.00081454
7 | 0.0039156 | 0.00098135
8 | 0.0016864 | 0.00042264
9 | 0.0019554 | 0.00049007
10 | 0.0010493 | 0.00026297
11 | 0.000498 | 0.00012481
12 | 0.00096771 | 0.00024253
13 | 0.0010326 | 0.0002588
14 | 0.0009877 | 0.00024754
15 | 0.0059832 | 0.0014995
16 | 0.00093606 | 0.0002346
17 | 0.00083842 | 0.00021013
18 | 0.0012291 | 0.00030804
19 | 0.0078339 | 0.0019634
20 | 0.0013052 | 0.00032712
21 | 0.001031 | 0.00025839
22 | 0.0080674 | 0.0020219
23 | 0.0069284 | 0.0017364
24 | 0.0074096 | 0.001857
25 | 0.0086845 | 0.0021765
26 | 0.0057997 | 0.0014535
27 | 0.0049295 | 0.0012355
28 | 0.0051336 | 0.0012866
29 | 0.0025917 | 0.00064955
30 | 0.0033844 | 0.0008482
31 | 0.0030398 | 0.00076185
32 | 0.00318 | 0.00079698
33 | 0.0067913 | 0.0017021
34 | 0.0029685 | 0.00074398
35 | 0.018516 | 0.0046406
36 | 0.014283 | 0.0035796
37 | 0.0051987 | 0.0013029
38 | 0.014262 | 0.0035743
39 | 0.0081089 | 0.0020323
40 | 0.0074026 | 0.0018553
41 | 0.0080112 | 0.0020078
42 | 0.0082223 | 0.0020607
43 | 0.0056632 | 0.0014193
44 | 0.0017525 | 0.00043922
45 | 0.0064301 | 0.0016115
46 | 0.00096806 | 0.00024262
47 | 0.0012271 | 0.00030755
48 | 0.0066366 | 0.0016633
49 | 0.0011086 | 0.00027783
50 | 0.0027511 | 0.00068949
51 | 0.0028113 | 0.00070457
52 | 0.001515 | 0.0003797
53 | 0.0016787 | 0.00042073
54 | 0.001026 | 0.00025714
55 | 0.0047493 | 0.0011903
56 | 0.0017436 | 0.000437
57 | 0.0017808 | 0.00044631
58 | 0.00097995 | 0.0002456
59 | 0.0014039 | 0.00035184
60 | 0.0014011 | 0.00035114
61 | 0.0014827 | 0.00037159
62 | 0.00098422 | 0.00024667
63 | 0.0014846 | 0.00037209
64 | 0.001951 | 0.00048896
65 | 0.0016348 | 0.00040971
66 | 0.0012565 | 0.00031491
67 | 0.0013818 | 0.00034631
68 | 0.0012116 | 0.00030366
69 | 0.0013033 | 0.00032663
70 | 0.0010341 | 0.00025917
71 | 0.0079544 | 0.0019936
72 | 0.001145 | 0.00028698
73 | 0.0014748 | 0.00036962
74 | 0.0015172 | 0.00038025
75 | 0.001068 | 0.00026766
76 | 0.0020015 | 0.00050163
77 | 0.001181 | 0.00029599
78 | 0.0014607 | 0.0003661
79 | 0.0018482 | 0.00046319
80 | 0.00195 | 0.00048872
81 | 0.0018335 | 0.00045952
82 | 0.0020074 | 0.00050311
83 | 0.0035251 | 0.00088347
84 | 0.0017823 | 0.00044668
85 | 0.0012914 | 0.00032366
86 | 0.0033639 | 0.00084307
87 | 0.0019451 | 0.00048748
88 | 0.0018861 | 0.00047269
89 | 0.003727 | 0.00093407
90 | 0.0014043 | 0.00035195
91 | 0.0038158 | 0.00095634
92 | 0.0016786 | 0.00042071
93 | 0.0020223 | 0.00050683
94 | 0.0010196 | 0.00025554
95 | 0.0013179 | 0.0003303
96 | 0.0014226 | 0.00035653
97 | 0.00098491 | 0.00024684
98 | 0.0026073 | 0.00065344
99 | 0.00095391 | 0.00023907
100 | 0.001938 | 0.0004857
101 | 0.0059799 | 0.0014987
102 | 0.0020607 | 0.00051647

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1