## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-633_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-633_0_4_node_2 | 0.4 | n |  | TRUE
2 | bus_LV_261-633_0_4_node_7 | 0.4 | n |  | TRUE
3 | bus_LV_261-633_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_261-633_0_4_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_261-633_0_4_node_11 | 0.4 | n |  | TRUE
6 | bus_LV_261-633_0_4_node_26 | 0.4 | n |  | TRUE
7 | bus_LV_261-633_0_4_node_33 | 0.4 | n |  | TRUE
8 | bus_LV_261-633_0_4_node_30 | 0.4 | n |  | TRUE
9 | bus_LV_261-633_0_4_node_29 | 0.4 | n |  | TRUE
10 | bus_LV_261-633_0_4_node_28 | 0.4 | n |  | TRUE
11 | bus_LV_261-633_0_4_node_9 | 0.4 | n |  | TRUE
12 | bus_LV_261-633_0_4_node_10 | 0.4 | n |  | TRUE
13 | bus_LV_261-633_0_4_node_18 | 0.4 | n |  | TRUE
14 | bus_LV_261-633_0_4_node_27 | 0.4 | n |  | TRUE
15 | bus_LV_261-633_0_4_node_25 | 0.4 | n |  | TRUE
16 | bus_LV_261-633_0_4_node_23 | 0.4 | n |  | TRUE
17 | bus_LV_261-633_0_4_node_12 | 0.4 | n |  | TRUE
18 | bus_LV_261-633_0_4_node_24 | 0.4 | n |  | TRUE
19 | bus_LV_261-633_0_4_node_13 | 0.4 | n |  | TRUE
20 | bus_LV_261-633_0_4_node_22 | 0.4 | n |  | TRUE
21 | bus_LV_261-633_0_4_node_19 | 0.4 | n |  | TRUE
22 | bus_LV_261-633_0_4_node_34 | 0.4 | n |  | TRUE
23 | bus_LV_261-633_0_4_node_32 | 0.4 | n |  | TRUE
24 | bus_LV_261-633_0_4_node_35 | 0.4 | n |  | TRUE
25 | bus_LV_261-633_0_4_node_31 | 0.4 | n |  | TRUE
26 | bus_LV_261-633_0_4_node_37 | 0.4 | n |  | TRUE
27 | bus_LV_261-633_0_4_node_17 | 0.4 | n |  | TRUE
28 | bus_LV_261-633_0_4_node_21 | 0.4 | n |  | TRUE
29 | bus_LV_261-633_0_4_node_36 | 0.4 | n |  | TRUE
30 | bus_LV_261-633_0_4_node_20 | 0.4 | n |  | TRUE
31 | bus_LV_261-633_0_4_node_16 | 0.4 | n |  | TRUE
32 | bus_MV_549_0_node_30 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-633_0_4_load_0 | 0 | 0.032432 | 0.0081282 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-633_0_4_load_26 | 6 | 0.0044201 | 0.0011078 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-633_0_4_load_33 | 7 | 0.0062444 | 0.001565 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-633_0_4_load_30 | 8 | 0.0066101 | 0.0016567 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-633_0_4_load_29 | 9 | 0.045099 | 0.011303 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-633_0_4_load_28 | 10 | 0.03938 | 0.0098696 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-633_0_4_load_18 | 13 | 0.08997 | 0.022549 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-633_0_4_load_27 | 14 | 0.023197 | 0.0058138 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-633_0_4_load_25 | 15 | 0.0039851 | 0.00099877 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-633_0_4_load_23 | 16 | 0.0090599 | 0.0022706 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-633_0_4_load_24 | 18 | 0.0092144 | 0.0023093 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-633_0_4_load_22 | 20 | 0.014468 | 0.003626 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-633_0_4_load_19 | 21 | 0.013368 | 0.0033503 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-633_0_4_load_34 | 22 | 0.062295 | 0.015613 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-633_0_4_load_32 | 23 | 0.011435 | 0.0028658 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-633_0_4_load_35 | 24 | 0.0083653 | 0.0020965 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-633_0_4_load_31 | 25 | 0.034563 | 0.0086623 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_261-633_0_4_load_37 | 26 | 0.031108 | 0.0077965 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_261-633_0_4_load_17 | 27 | 0.053537 | 0.013418 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_261-633_0_4_load_21 | 28 | 0.019677 | 0.0049314 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_261-633_0_4_load_36 | 29 | 0.018447 | 0.0046231 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_261-633_0_4_load_20 | 30 | 0.010036 | 0.0025153 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_261-633_0_4_load_16 | 31 | 0.026482 | 0.0066371 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 13 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-633_0_4_line_0 |  | 0 | 1 | 0.083031 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-633_0_4_line_1 |  | 1 | 2 | 0.069311 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-633_0_4_line_2 |  | 2 | 9 | 0.033768 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-633_0_4_line_3 |  | 2 | 10 | 0.0091703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-633_0_4_line_4 |  | 3 | 4 | 0.010725 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_261-633_0_4_line_5 |  | 3 | 5 | 0.005502 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_261-633_0_4_line_6 |  | 3 | 6 | 0.0054913 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
7 | LV_261-633_0_4_line_7 |  | 4 | 7 | 0.02793 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_261-633_0_4_line_8 |  | 4 | 8 | 0.013665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_261-633_0_4_line_9 |  | 5 | 16 | 0.01933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_261-633_0_4_line_10 |  | 6 | 15 | 0.011958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
11 | LV_261-633_0_4_line_11 |  | 7 | 24 | 0.015113 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_261-633_0_4_line_12 |  | 8 | 25 | 0.015493 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-633_0_4_line_13 |  | 9 | 26 | 0.017315 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_261-633_0_4_line_14 |  | 10 | 11 | 0.051618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
15 | LV_261-633_0_4_line_15 |  | 11 | 12 | 0.008524 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
16 | LV_261-633_0_4_line_16 |  | 11 | 13 | 0.013203 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
17 | LV_261-633_0_4_line_17 |  | 12 | 14 | 0.0042245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_261-633_0_4_line_18 |  | 12 | 15 | 0.031404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
19 | LV_261-633_0_4_line_19 |  | 13 | 27 | 0.031411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_261-633_0_4_line_20 |  | 14 | 28 | 0.011161 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_261-633_0_4_line_21 |  | 16 | 17 | 0.017366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_261-633_0_4_line_22 |  | 17 | 18 | 0.014614 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_261-633_0_4_line_23 |  | 18 | 29 | 0.013277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_261-633_0_4_line_24 |  | 19 | 20 | 0.028664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_261-633_0_4_line_25 |  | 19 | 21 | 0.010627 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_261-633_0_4_line_26 |  | 21 | 30 | 0.0083606 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_261-633_0_4_line_27 |  | 22 | 23 | 0.010247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_261-633_0_4_line_28 |  | 23 | 25 | 0.013171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_261-633_0_4_line_29 |  | 27 | 31 | 0.027615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_261-633_0_4_line_30 |  | 28 | 30 | 0.01582 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-633_0_4_trafo_18 | 0.63 MVA 20/0.4 kV | 32 | 13 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2679025.0892 | 1249298.3233 | 2678999.304 | 1249237.0348 | 2678999.1739 | 1249235.4653 | 2678993.3803 | 1249221.6681
1 | 2679015.5262 | 1249242.5217 | 2679017.2671 | 1249247.3039 | 2679009.9846 | 1249249.2416 | 2679030.1831 | 1249296.2897 | 2679025.0892 | 1249298.3233
2 | 2679015.5262 | 1249242.5217 | 2679013.831 | 1249242.2322 | 2679012.3852 | 1249241.3678 | 2679011.216 | 1249240.1402 | 2679010.4565 | 1249238.7736 | 2678999.9592 | 1249213.7837
3 | 2679015.5262 | 1249242.5217 | 2679017.3541 | 1249242.4793 | 2679024.4769 | 1249240.6991
4 | 2679125.5125 | 1249215.0795 | 2679125.6331 | 1249220.1848 | 2679125.762 | 1249225.8018
5 | 2679128.449 | 1249210.6265 | 2679128.168 | 1249211.8792 | 2679126.9476 | 1249213.92 | 2679125.5125 | 1249215.0795
6 | 2679125.5125 | 1249215.0795 | 2679123.5303 | 1249215.9314 | 2679121.1137 | 1249216.5107 | 2679120.2906 | 1249216.7174
7 | 2679125.762 | 1249225.8018 | 2679126.9356 | 1249226.6959 | 2679127.6454 | 1249227.8284 | 2679127.6413 | 1249236.0455 | 2679126.5501 | 1249238.5994 | 2679126.825 | 1249248.5437 | 2679126.96 | 1249252.7173
8 | 2679125.762 | 1249225.8018 | 2679123.9886 | 1249225.1554 | 2679121.0009 | 1249224.9598 | 2679117.0277 | 1249225.6184 | 2679112.4167 | 1249226.784
9 | 2679128.449 | 1249210.6265 | 2679128.7059 | 1249209.4847 | 2679129.7677 | 1249191.3565
10 | 2679120.2906 | 1249216.7174 | 2679108.6929 | 1249219.6302
11 | 2679127.9778 | 1249267.7896 | 2679127.1617 | 1249258.9558 | 2679126.96 | 1249252.7173
12 | 2679112.4167 | 1249226.784 | 2679097.3962 | 1249230.5808
13 | 2678999.9592 | 1249213.7837 | 2678993.2534 | 1249197.8198
14 | 2679071.4438 | 1249224.3094 | 2679071.2698 | 1249226.0305 | 2679070.5719 | 1249227.4 | 2679069.4369 | 1249228.708 | 2679068.0973 | 1249229.5019 | 2679066.7674 | 1249230.129 | 2679024.4769 | 1249240.6991
15 | 2679079.6018 | 1249221.8386 | 2679075.591 | 1249223.0526 | 2679071.4438 | 1249224.3094
16 | 2679071.4438 | 1249224.3094 | 2679071.2302 | 1249222.772 | 2679067.6024 | 1249211.6998
17 | 2679079.6018 | 1249221.8386 | 2679078.4867 | 1249218.8215 | 2679078.1734 | 1249217.8635
18 | 2679079.6018 | 1249221.8386 | 2679080.791 | 1249223.8225 | 2679081.6329 | 1249224.6788 | 2679082.8115 | 1249225.1949 | 2679083.6547 | 1249225.3841 | 2679084.8778 | 1249225.4004 | 2679086.4736 | 1249225.2105 | 2679108.6929 | 1249219.6302
19 | 2679057.8223 | 1249181.8505 | 2679067.6024 | 1249211.6998
20 | 2679078.1734 | 1249217.8635 | 2679074.7034 | 1249207.2552
21 | 2679130.7804 | 1249174.0197 | 2679130.5546 | 1249177.9196 | 2679129.7677 | 1249191.3565
22 | 2679130.7804 | 1249174.0197 | 2679122.1222 | 1249174.36 | 2679116.3259 | 1249175.7001
23 | 2679103.3901 | 1249178.691 | 2679116.3259 | 1249175.7001
24 | 2679063.8821 | 1249174.1718 | 2679091.0228 | 1249164.9532
25 | 2679063.8821 | 1249174.1718 | 2679067.1859 | 1249184.2725
26 | 2679069.7851 | 1249192.2188 | 2679067.1859 | 1249184.2725
27 | 2679074.6924 | 1249236.3199 | 2679084.6269 | 1249233.8086
28 | 2679097.3962 | 1249230.5808 | 2679084.6269 | 1249233.8086
29 | 2679049.224 | 1249155.608 | 2679057.8223 | 1249181.8505
30 | 2679069.7851 | 1249192.2188 | 2679074.7034 | 1249207.2552

## bus_geodata
| x | y | coords
0 | 2678993.3803 | 1249221.6681
1 | 2679025.0892 | 1249298.3233
2 | 2679015.5262 | 1249242.5217
3 | 2679125.5125 | 1249215.0795
4 | 2679125.762 | 1249225.8018
5 | 2679128.449 | 1249210.6265
6 | 2679120.2906 | 1249216.7174
7 | 2679126.96 | 1249252.7173
8 | 2679112.4167 | 1249226.784
9 | 2678999.9592 | 1249213.7837
10 | 2679024.4769 | 1249240.6991
11 | 2679071.4438 | 1249224.3094
12 | 2679079.6018 | 1249221.8386
13 | 2679067.6024 | 1249211.6998
14 | 2679078.1734 | 1249217.8635
15 | 2679108.6929 | 1249219.6302
16 | 2679129.7677 | 1249191.3565
17 | 2679130.7804 | 1249174.0197
18 | 2679116.3259 | 1249175.7001
19 | 2679063.8821 | 1249174.1718
20 | 2679091.0228 | 1249164.9532
21 | 2679067.1859 | 1249184.2725
22 | 2679074.6924 | 1249236.3199
23 | 2679084.6269 | 1249233.8086
24 | 2679127.9778 | 1249267.7896
25 | 2679097.3962 | 1249230.5808
26 | 2678993.2534 | 1249197.8198
27 | 2679057.8223 | 1249181.8505
28 | 2679074.7034 | 1249207.2552
29 | 2679103.3901 | 1249178.691
30 | 2679069.7851 | 1249192.2188
31 | 2679049.224 | 1249155.608
32 | 2679071.4438 | 1249224.3094

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98944 | -0.20316 | 0.032432 | 0.0081282
1 | 0.99191 | -0.15534 | 0 | 0
2 | 0.99397 | -0.1156 | 0 | 0
3 | 0.995 | -0.09575 | 0 | 0
4 | 0.99373 | -0.12024 | 0 | 0
5 | 0.99482 | -0.099308 | 0 | 0
6 | 0.99542 | -0.087718 | 0.0044201 | 0.0011078
7 | 0.99336 | -0.12744 | 0.0062444 | 0.001565
8 | 0.99229 | -0.14799 | 0.0066101 | 0.0016567
9 | 0.99162 | -0.1611 | 0.045099 | 0.011303
10 | 0.99488 | -0.098036 | 0.03938 | 0.0098696
11 | 0.99838 | -0.030997 | 0 | 0
12 | 0.99771 | -0.043695 | 0 | 0
13 | 1 | 0 | -0.48803 | -0.12304
14 | 0.9974 | -0.049669 | 0.023197 | 0.0058138
15 | 0.99604 | -0.07576 | 0.0039851 | 0.00099877
16 | 0.99417 | -0.11182 | 0.0090599 | 0.0022706
17 | 0.99373 | -0.12029 | 0 | 0
18 | 0.99336 | -0.12743 | 0.0092144 | 0.0023093
19 | 0.99592 | -0.078235 | 0 | 0
20 | 0.99554 | -0.085526 | 0.014468 | 0.003626
21 | 0.99606 | -0.075534 | 0.013368 | 0.0033503
22 | 0.98928 | -0.20636 | 0.062295 | 0.015613
23 | 0.98986 | -0.19499 | 0.011435 | 0.0028658
24 | 0.99324 | -0.12967 | 0.0083653 | 0.0020965
25 | 0.99075 | -0.17773 | 0.034563 | 0.0086623
26 | 0.99113 | -0.17066 | 0.031108 | 0.0077965
27 | 0.99772 | -0.04391 | 0.053537 | 0.013418
28 | 0.99682 | -0.06093 | 0.019677 | 0.0049314
29 | 0.99314 | -0.13176 | 0.018447 | 0.0046231
30 | 0.99627 | -0.071446 | 0.010036 | 0.0025153
31 | 0.99705 | -0.056723 | 0.026482 | 0.0066371
32 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.032432 | -0.0081282 | 0.032506 | 0.0081746 | 7.4071e-05 | 4.6337e-05 | 0.048774 | 0.048774 | 0.048774 | 0.98944 | -0.20316 | 0.99191 | -0.15534 | 13.3995
1 | -0.032506 | -0.0081746 | 0.032568 | 0.0082133 | 6.1831e-05 | 3.8675e-05 | 0.048774 | 0.048774 | 0.048774 | 0.99191 | -0.15534 | 0.99397 | -0.1156 | 13.3994
2 | 0.076387 | 0.019214 | -0.076221 | -0.019108 | 0.00016567 | 0.00010559 | 0.11438 | 0.11438 | 0.11438 | 0.99397 | -0.1156 | 0.99162 | -0.1611 | 31.4228
3 | -0.10895 | -0.027427 | 0.10905 | 0.027485 | 9.1538e-05 | 5.8466e-05 | 0.16315 | 0.16315 | 0.16315 | 0.99397 | -0.1156 | 0.99488 | -0.098036 | 44.8221
4 | 0.13007 | 0.032816 | -0.12992 | -0.032718 | 0.00015231 | 9.7336e-05 | 0.1946 | 0.1946 | 0.1946 | 0.995 | -0.09575 | 0.99373 | -0.12024 | 53.4611
5 | 0.036773 | 0.0092358 | -0.036767 | -0.0092319 | 6.2416e-06 | 3.9232e-06 | 0.055001 | 0.055001 | 0.055001 | 0.995 | -0.09575 | 0.99482 | -0.099308 | 15.1102
6 | -0.16685 | -0.042051 | 0.16691 | 0.042092 | 6.4145e-05 | 4.091e-05 | 0.2496 | 0.2496 | 0.2496 | 0.995 | -0.09575 | 0.99542 | -0.087718 | 34.2857
7 | 0.014616 | 0.0036647 | -0.014611 | -0.0036619 | 5.017e-06 | 2.8492e-06 | 0.021886 | 0.021886 | 0.021886 | 0.99373 | -0.12024 | 0.99336 | -0.12744 | 6.0127
8 | 0.1153 | 0.029054 | -0.11515 | -0.028956 | 0.00015286 | 9.7653e-05 | 0.17271 | 0.17271 | 0.17271 | 0.99373 | -0.12024 | 0.99229 | -0.14799 | 47.4485
9 | 0.036767 | 0.0092319 | -0.036745 | -0.0092181 | 2.1928e-05 | 1.3783e-05 | 0.055001 | 0.055001 | 0.055001 | 0.99482 | -0.099308 | 0.99417 | -0.11182 | 15.1102
10 | -0.17133 | -0.0432 | 0.17143 | 0.043263 | 9.8117e-05 | 6.2329e-05 | 0.25621 | 0.25621 | 0.25621 | 0.99542 | -0.087718 | 0.99604 | -0.07576 | 23.4622
11 | 0.0083661 | 0.0020969 | -0.0083653 | -0.0020965 | 8.9012e-07 | 3.7405e-07 | 0.012532 | 0.012532 | 0.012532 | 0.99336 | -0.12744 | 0.99324 | -0.12967 | 3.4429
12 | 0.10854 | 0.027299 | -0.10839 | -0.027201 | 0.00015398 | 9.835e-05 | 0.1628 | 0.1628 | 0.1628 | 0.99229 | -0.14799 | 0.99075 | -0.17773 | 44.7254
13 | 0.031123 | 0.0078054 | -0.031108 | -0.0077965 | 1.4163e-05 | 8.8414e-06 | 0.046704 | 0.046704 | 0.046704 | 0.99162 | -0.1611 | 0.99113 | -0.17066 | 12.8309
14 | -0.14843 | -0.037355 | 0.1489 | 0.037659 | 0.00047721 | 0.00030407 | 0.22205 | 0.22205 | 0.22205 | 0.99488 | -0.098036 | 0.99838 | -0.030997 | 30.5017
15 | 0.25667 | 0.064823 | -0.25651 | -0.064723 | 0.00015607 | 9.9552e-05 | 0.38272 | 0.38272 | 0.38272 | 0.99838 | -0.030997 | 0.99771 | -0.043695 | 35.048
16 | -0.40557 | -0.10248 | 0.40618 | 0.10287 | 0.00060365 | 0.00038582 | 0.60478 | 0.60478 | 0.60478 | 0.99838 | -0.030997 | 1 | 0 | 55.3825
17 | 0.080831 | 0.02029 | -0.080808 | -0.020276 | 2.3028e-05 | 1.4683e-05 | 0.12056 | 0.12056 | 0.12056 | 0.99771 | -0.043695 | 0.9974 | -0.049669 | 33.1222
18 | 0.17568 | 0.044433 | -0.17541 | -0.044261 | 0.00026979 | 0.00017144 | 0.26216 | 0.26216 | 0.26216 | 0.99771 | -0.043695 | 0.99604 | -0.07576 | 24.0074
19 | 0.080204 | 0.020172 | -0.080036 | -0.020065 | 0.00016784 | 0.00010701 | 0.11937 | 0.11937 | 0.11937 | 1 | 0 | 0.99772 | -0.04391 | 32.7939
20 | 0.057611 | 0.014462 | -0.05758 | -0.014442 | 3.0925e-05 | 1.9646e-05 | 0.085957 | 0.085957 | 0.085957 | 0.9974 | -0.049669 | 0.99682 | -0.06093 | 23.6145
21 | 0.027685 | 0.0069475 | -0.027674 | -0.0069406 | 1.1184e-05 | 6.9327e-06 | 0.041441 | 0.041441 | 0.041441 | 0.99417 | -0.11182 | 0.99373 | -0.12029 | 11.3849
22 | 0.027674 | 0.0069406 | -0.027665 | -0.0069347 | 9.4116e-06 | 5.8342e-06 | 0.041441 | 0.041441 | 0.041441 | 0.99373 | -0.12029 | 0.99336 | -0.12743 | 11.3849
23 | 0.01845 | 0.0046254 | -0.018447 | -0.0046231 | 3.8033e-06 | 2.2623e-06 | 0.027638 | 0.027638 | 0.027638 | 0.99336 | -0.12743 | 0.99314 | -0.13176 | 7.593
24 | 0.014473 | 0.0036288 | -0.014468 | -0.003626 | 5.0265e-06 | 2.8441e-06 | 0.021625 | 0.021625 | 0.021625 | 0.99592 | -0.078235 | 0.99554 | -0.085526 | 5.9409
25 | -0.014473 | -0.0036288 | 0.014475 | 0.0036299 | 1.8636e-06 | 1.0544e-06 | 0.021625 | 0.021625 | 0.021625 | 0.99592 | -0.078235 | 0.99606 | -0.075534 | 5.9409
26 | -0.027843 | -0.0069802 | 0.027848 | 0.0069836 | 5.4243e-06 | 3.3627e-06 | 0.041595 | 0.041595 | 0.041595 | 0.99606 | -0.075534 | 0.99627 | -0.071446 | 11.4272
27 | -0.062295 | -0.015613 | 0.062329 | 0.015634 | 3.3738e-05 | 2.1461e-05 | 0.093701 | 0.093701 | 0.093701 | 0.98928 | -0.20636 | 0.98986 | -0.19499 | 25.742
28 | -0.073764 | -0.0185 | 0.073824 | 0.018539 | 6.0734e-05 | 3.87e-05 | 0.11089 | 0.11089 | 0.11089 | 0.98986 | -0.19499 | 0.99075 | -0.17773 | 30.4643
29 | 0.026499 | 0.0066471 | -0.026482 | -0.0066371 | 1.6176e-05 | 9.9924e-06 | 0.039523 | 0.039523 | 0.039523 | 0.99772 | -0.04391 | 0.99705 | -0.056723 | 10.8579
30 | 0.037903 | 0.0095108 | -0.037884 | -0.0094988 | 1.8995e-05 | 1.1951e-05 | 0.056584 | 0.056585 | 0.056585 | 0.99682 | -0.06093 | 0.99627 | -0.071446 | 15.5452

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.578 | 0.14559

## res_load
| p_mw | q_mvar
0 | 0.032432 | 0.0081282
1 | 0.0044201 | 0.0011078
2 | 0.0062444 | 0.001565
3 | 0.0066101 | 0.0016567
4 | 0.045099 | 0.011303
5 | 0.03938 | 0.0098696
6 | 0.08997 | 0.022549
7 | 0.023197 | 0.0058138
8 | 0.0039851 | 0.00099877
9 | 0.0090599 | 0.0022706
10 | 0.0092144 | 0.0023093
11 | 0.014468 | 0.003626
12 | 0.013368 | 0.0033503
13 | 0.062295 | 0.015613
14 | 0.011435 | 0.0028658
15 | 0.0083653 | 0.0020965
16 | 0.034563 | 0.0086623
17 | 0.031108 | 0.0077965
18 | 0.053537 | 0.013418
19 | 0.019677 | 0.0049314
20 | 0.018447 | 0.0046231
21 | 0.010036 | 0.0025153
22 | 0.026482 | 0.0066371

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1