## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-634_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-634_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-634_0_3_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_261-634_0_3_node_19 | 0.4 | n |  | TRUE
4 | bus_LV_261-634_0_3_node_24 | 0.4 | n |  | TRUE
5 | bus_LV_261-634_0_3_node_4 | 0.4 | n |  | TRUE
6 | bus_LV_261-634_0_3_node_22 | 0.4 | n |  | TRUE
7 | bus_LV_261-634_0_3_node_18 | 0.4 | n |  | TRUE
8 | bus_LV_261-634_0_3_node_5 | 0.4 | n |  | TRUE
9 | bus_LV_261-634_0_3_node_21 | 0.4 | n |  | TRUE
10 | bus_LV_261-634_0_3_node_23 | 0.4 | n |  | TRUE
11 | bus_LV_261-634_0_3_node_6 | 0.4 | n |  | TRUE
12 | bus_LV_261-634_0_3_node_7 | 0.4 | n |  | TRUE
13 | bus_LV_261-634_0_3_node_10 | 0.4 | n |  | TRUE
14 | bus_LV_261-634_0_3_node_17 | 0.4 | n |  | TRUE
15 | bus_LV_261-634_0_3_node_29 | 0.4 | n |  | TRUE
16 | bus_LV_261-634_0_3_node_12 | 0.4 | n |  | TRUE
17 | bus_LV_261-634_0_3_node_15 | 0.4 | n |  | TRUE
18 | bus_LV_261-634_0_3_node_27 | 0.4 | n |  | TRUE
19 | bus_LV_261-634_0_3_node_13 | 0.4 | n |  | TRUE
20 | bus_LV_261-634_0_3_node_20 | 0.4 | n |  | TRUE
21 | bus_LV_261-634_0_3_node_28 | 0.4 | n |  | TRUE
22 | bus_LV_261-634_0_3_node_26 | 0.4 | n |  | TRUE
23 | bus_LV_261-634_0_3_node_16 | 0.4 | n |  | TRUE
24 | bus_LV_261-634_0_3_node_25 | 0.4 | n |  | TRUE
25 | bus_LV_261-634_0_3_node_32 | 0.4 | n |  | TRUE
26 | bus_LV_261-634_0_3_node_30 | 0.4 | n |  | TRUE
27 | bus_LV_261-634_0_3_node_33 | 0.4 | n |  | TRUE
28 | bus_LV_261-634_0_3_node_31 | 0.4 | n |  | TRUE
29 | bus_MV_389_0_node_69 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-634_0_3_load_0 | 0 | 0.031022 | 0.0077748 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-634_0_3_load_24 | 4 | 0.011542 | 0.0028927 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-634_0_3_load_22 | 6 | 0.020341 | 0.005098 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-634_0_3_load_18 | 7 | 0.010345 | 0.0025928 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-634_0_3_load_23 | 10 | 0.048015 | 0.012034 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-634_0_3_load_17 | 14 | 0.024607 | 0.0061671 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-634_0_3_load_29 | 15 | 0.055948 | 0.014022 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-634_0_3_load_27 | 18 | 0.00074757 | 0.00018736 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-634_0_3_load_28 | 21 | 0.021319 | 0.0053429 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-634_0_3_load_26 | 22 | 0.018468 | 0.0046284 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-634_0_3_load_25 | 24 | 0.038067 | 0.0095404 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-634_0_3_load_32 | 25 | 0.0064513 | 0.0016168 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-634_0_3_load_30 | 26 | 0.011037 | 0.0027662 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-634_0_3_load_33 | 27 | 0.014532 | 0.0036421 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-634_0_3_load_31 | 28 | 0.038257 | 0.0095881 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 28 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-634_0_3_line_0 |  | 0 | 1 | 0.023163 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-634_0_3_line_1 |  | 1 | 2 | 0.020514 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-634_0_3_line_2 |  | 2 | 3 | 0.025505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-634_0_3_line_3 |  | 2 | 4 | 0.0062539 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
4 | LV_261-634_0_3_line_4 |  | 3 | 20 | 0.07501 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_261-634_0_3_line_5 |  | 3 | 7 | 0.024987 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_261-634_0_3_line_6 |  | 4 | 8 | 0.012299 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
7 | LV_261-634_0_3_line_7 |  | 5 | 6 | 0.008923 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_261-634_0_3_line_8 |  | 5 | 7 | 0.034767 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_261-634_0_3_line_9 |  | 8 | 9 | 0.015708 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
10 | LV_261-634_0_3_line_10 |  | 8 | 10 | 0.025542 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_261-634_0_3_line_11 |  | 9 | 26 | 0.02618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
12 | LV_261-634_0_3_line_12 |  | 10 | 11 | 0.065017 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-634_0_3_line_13 |  | 11 | 12 | 0.069579 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_261-634_0_3_line_14 |  | 12 | 13 | 0.010848 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_261-634_0_3_line_15 |  | 12 | 14 | 0.044982 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_261-634_0_3_line_16 |  | 13 | 15 | 0.022203 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_261-634_0_3_line_17 |  | 16 | 17 | 0.025245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_261-634_0_3_line_18 |  | 16 | 18 | 0.049251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_261-634_0_3_line_19 |  | 17 | 22 | 0.0145 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_261-634_0_3_line_20 |  | 17 | 23 | 0.022976 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_261-634_0_3_line_21 |  | 17 | 24 | 0.026696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_261-634_0_3_line_22 |  | 19 | 20 | 0.028632 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_261-634_0_3_line_23 |  | 19 | 21 | 0.033247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_261-634_0_3_line_24 |  | 20 | 27 | 0.016204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_261-634_0_3_line_25 |  | 21 | 22 | 0.019607 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_261-634_0_3_line_26 |  | 23 | 25 | 0.024314 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_261-634_0_3_line_27 |  | 26 | 28 | 0.067332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-634_0_3_trafo_31 | 0.63 MVA 20/0.4 kV | 29 | 28 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10
0 | 2678895.3777 | 1249159.9057 | 2678894.3751 | 1249158.647 | 2678891.393 | 1249155.7608 | 2678886.9978 | 1249152.3887 | 2678877.1404 | 1249145.7859
1 | 2678895.3777 | 1249159.9057 | 2678902.8375 | 1249153.7338 | 2678911.183 | 1249146.8287
2 | 2678886.1892 | 1249141.659 | 2678893.1453 | 1249143.8198 | 2678903.2606 | 1249145.778 | 2678911.183 | 1249146.8287
3 | 2678911.183 | 1249146.8287 | 2678913.2259 | 1249146.5223 | 2678916.735 | 1249144.236
4 | 2678885.9355 | 1249071.6711 | 2678885.7537 | 1249085.3231 | 2678895.9395 | 1249104.6728 | 2678897.5604 | 1249115.6468 | 2678893.8189 | 1249124.9928 | 2678886.1892 | 1249141.659
5 | 2678886.1892 | 1249141.659 | 2678882.0743 | 1249139.9141 | 2678878.4426 | 1249137.6085 | 2678875.4489 | 1249135.6006 | 2678872.4378 | 1249132.625 | 2678866.7511 | 1249126.4729
6 | 2678925.941 | 1249136.4064 | 2678923.7455 | 1249139.6684 | 2678916.735 | 1249144.236
7 | 2678851.2968 | 1249095.55 | 2678843.9347 | 1249100.6225
8 | 2678843.9347 | 1249100.6225 | 2678850.6507 | 1249107.7837 | 2678860.0869 | 1249117.6498 | 2678860.5645 | 1249119.7799 | 2678866.7511 | 1249126.4729
9 | 2678917.8976 | 1249122.9006 | 2678925.941 | 1249136.4064
10 | 2678925.941 | 1249136.4064 | 2678928.3598 | 1249132.8249 | 2678937.9419 | 1249126.6257 | 2678946.3237 | 1249121.5336
11 | 2678917.8976 | 1249122.9006 | 2678903.4828 | 1249101.0468
12 | 2679005.5487 | 1249094.9029 | 2678997.9901 | 1249097.7154 | 2678983.529 | 1249103.4047 | 2678971.0808 | 1249108.7761 | 2678957.8995 | 1249115.3276 | 2678946.3237 | 1249121.5336
13 | 2678966.3088 | 1249133.6752 | 2678974.6777 | 1249128.9833 | 2678980.2386 | 1249126.4777 | 2678988.4738 | 1249122.7625 | 2678994.9463 | 1249119.8466 | 2679004.1553 | 1249116.1555 | 2679011.5365 | 1249114.1857 | 2679010.5084 | 1249110.8696 | 2679009.2922 | 1249106.9394 | 2679007.2866 | 1249100.4857 | 2679005.5487 | 1249094.9029
14 | 2678966.3088 | 1249133.6752 | 2678961.8041 | 1249136.2505 | 2678957.103 | 1249139.4013
15 | 2678966.3088 | 1249133.6752 | 2678983.7294 | 1249175.147
16 | 2678957.103 | 1249139.4013 | 2678962.6378 | 1249150.1829 | 2678966.5915 | 1249159.4595
17 | 2678942.5482 | 1249017.2404 | 2678946.6716 | 1249014.3821 | 2678958.08 | 1249024.7193 | 2678961.6723 | 1249021.487
18 | 2678961.6723 | 1249021.487 | 2678959.0098 | 1249019.5502 | 2678955.0771 | 1249016.5956 | 2678946.4991 | 1249008.6311 | 2678925.358 | 1248988.2955
19 | 2678942.5482 | 1249017.2404 | 2678930.6329 | 1249025.503
20 | 2678959.3674 | 1249032.9425 | 2678955.2848 | 1249029.341 | 2678942.5482 | 1249017.2404
21 | 2678942.5482 | 1249017.2404 | 2678936.6594 | 1249011.48 | 2678923.3684 | 1248998.6709
22 | 2678881.7108 | 1249043.5722 | 2678886.2762 | 1249063.0916 | 2678885.9355 | 1249071.6711
23 | 2678881.7108 | 1249043.5722 | 2678912.5319 | 1249036.4771 | 2678913.9711 | 1249035.7327
24 | 2678885.9355 | 1249071.6711 | 2678901.7024 | 1249067.9328
25 | 2678913.9711 | 1249035.7327 | 2678922.759 | 1249031.1871 | 2678927.0988 | 1249027.9536 | 2678930.6329 | 1249025.503
26 | 2678959.3674 | 1249032.9425 | 2678951.5006 | 1249041.8776 | 2678942.99 | 1249050.9079
27 | 2678903.4828 | 1249101.0468 | 2678896.8689 | 1249091.0196 | 2678897.6461 | 1249085.9596 | 2678911.2121 | 1249078.3012 | 2678927.2145 | 1249070.2861 | 2678936.233 | 1249084.3714

## bus_geodata
| x | y | coords
0 | 2678877.1404 | 1249145.7859
1 | 2678895.3777 | 1249159.9057
2 | 2678911.183 | 1249146.8287
3 | 2678886.1892 | 1249141.659
4 | 2678916.735 | 1249144.236
5 | 2678843.9347 | 1249100.6225
6 | 2678851.2968 | 1249095.55
7 | 2678866.7511 | 1249126.4729
8 | 2678925.941 | 1249136.4064
9 | 2678917.8976 | 1249122.9006
10 | 2678946.3237 | 1249121.5336
11 | 2679005.5487 | 1249094.9029
12 | 2678966.3088 | 1249133.6752
13 | 2678957.103 | 1249139.4013
14 | 2678983.7294 | 1249175.147
15 | 2678966.5915 | 1249159.4595
16 | 2678961.6723 | 1249021.487
17 | 2678942.5482 | 1249017.2404
18 | 2678925.358 | 1248988.2955
19 | 2678881.7108 | 1249043.5722
20 | 2678885.9355 | 1249071.6711
21 | 2678913.9711 | 1249035.7327
22 | 2678930.6329 | 1249025.503
23 | 2678959.3674 | 1249032.9425
24 | 2678923.3684 | 1248998.6709
25 | 2678942.99 | 1249050.9079
26 | 2678903.4828 | 1249101.0468
27 | 2678901.7024 | 1249067.9328
28 | 2678936.233 | 1249084.3714
29 | 2678941.9206 | 1249093.2543

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98722 | -0.24346 | 0.031022 | 0.0077748
1 | 0.98788 | -0.23062 | 0 | 0
2 | 0.98847 | -0.21926 | 0 | 0
3 | 0.98537 | -0.27872 | 0 | 0
4 | 0.98893 | -0.21027 | 0.011542 | 0.0028927
5 | 0.98402 | -0.30522 | 0 | 0
6 | 0.98385 | -0.30849 | 0.020341 | 0.005098
7 | 0.98467 | -0.2925 | 0.010345 | 0.0025928
8 | 0.98959 | -0.19765 | 0 | 0
9 | 0.99106 | -0.1696 | 0 | 0
10 | 0.98655 | -0.25628 | 0.048015 | 0.012034
11 | 0.98167 | -0.35054 | 0 | 0
12 | 0.97646 | -0.45246 | 0 | 0
13 | 0.9759 | -0.46356 | 0 | 0
14 | 0.97543 | -0.47272 | 0.024607 | 0.0061671
15 | 0.97474 | -0.48632 | 0.055948 | 0.014022
16 | 0.9717 | -0.54556 | 0 | 0
17 | 0.97172 | -0.54521 | 0 | 0
18 | 0.97166 | -0.54624 | 0.00074757 | 0.00018736
19 | 0.97613 | -0.45822 | 0 | 0
20 | 0.97841 | -0.41378 | 0 | 0
21 | 0.97349 | -0.51009 | 0.021319 | 0.0053429
22 | 0.97233 | -0.53311 | 0.018468 | 0.0046284
23 | 0.97158 | -0.54795 | 0 | 0
24 | 0.97077 | -0.56399 | 0.038067 | 0.0095404
25 | 0.97143 | -0.55085 | 0.0064513 | 0.0016168
26 | 0.9935 | -0.12304 | 0.011037 | 0.0027662
27 | 0.97819 | -0.41807 | 0.014532 | 0.0036421
28 | 1 | 0 | -0.32014 | -0.082161
29 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.031022 | -0.0077748 | 0.031041 | 0.0077866 | 1.8991e-05 | 1.1858e-05 | 0.046758 | 0.046758 | 0.046758 | 0.98722 | -0.24346 | 0.98788 | -0.23062 | 12.8457
1 | -0.031041 | -0.0077866 | 0.031058 | 0.0077971 | 1.6819e-05 | 1.0501e-05 | 0.046758 | 0.046758 | 0.046758 | 0.98788 | -0.23062 | 0.98847 | -0.21926 | 12.8456
2 | 0.13186 | 0.033664 | -0.13149 | -0.033423 | 0.00037772 | 0.00024142 | 0.19873 | 0.19873 | 0.19873 | 0.98847 | -0.21926 | 0.98537 | -0.27872 | 54.5954
3 | -0.16292 | -0.041461 | 0.16299 | 0.041506 | 7.0665e-05 | 4.5065e-05 | 0.24548 | 0.24548 | 0.24548 | 0.98847 | -0.21926 | 0.98893 | -0.21027 | 33.7204
4 | 0.10077 | 0.02571 | -0.10011 | -0.025293 | 0.00065271 | 0.00041678 | 0.15233 | 0.15233 | 0.15233 | 0.98537 | -0.27872 | 0.97841 | -0.41378 | 41.8488
5 | 0.030722 | 0.0077127 | -0.030702 | -0.0077001 | 2.0172e-05 | 1.2592e-05 | 0.046398 | 0.046398 | 0.046398 | 0.98537 | -0.27872 | 0.98467 | -0.2925 | 12.7468
6 | -0.17453 | -0.044399 | 0.17464 | 0.044466 | 0.00010622 | 6.7508e-05 | 0.26285 | 0.26285 | 0.26285 | 0.98893 | -0.21027 | 0.98959 | -0.19765 | 24.0706
7 | 0.020344 | 0.0050999 | -0.020341 | -0.005098 | 3.167e-06 | 1.9136e-06 | 0.030765 | 0.030765 | 0.030765 | 0.98402 | -0.30522 | 0.98385 | -0.30849 | 8.4519
8 | -0.020344 | -0.0050999 | 0.020357 | 0.0051073 | 1.234e-05 | 7.4555e-06 | 0.030765 | 0.030765 | 0.030765 | 0.98402 | -0.30522 | 0.98467 | -0.2925 | 8.4519
9 | -0.30445 | -0.077482 | 0.30487 | 0.077745 | 0.00041226 | 0.00026324 | 0.45822 | 0.45822 | 0.45822 | 0.98959 | -0.19765 | 0.99106 | -0.1696 | 41.9614
10 | 0.12981 | 0.033015 | -0.12945 | -0.032782 | 0.00036558 | 0.00023365 | 0.19537 | 0.19537 | 0.19537 | 0.98959 | -0.19765 | 0.98655 | -0.25628 | 53.6724
11 | -0.30487 | -0.077745 | 0.30555 | 0.078184 | 0.0006871 | 0.00043873 | 0.45822 | 0.45822 | 0.45822 | 0.99106 | -0.1696 | 0.9935 | -0.12304 | 41.9614
12 | 0.081432 | 0.020748 | -0.081064 | -0.020513 | 0.00036854 | 0.00023504 | 0.12295 | 0.12295 | 0.12295 | 0.98655 | -0.25628 | 0.98167 | -0.35054 | 33.7765
13 | 0.081064 | 0.020513 | -0.080669 | -0.020261 | 0.00039441 | 0.00025154 | 0.12295 | 0.12295 | 0.12295 | 0.98167 | -0.35054 | 0.97646 | -0.45246 | 33.7766
14 | 0.056038 | 0.014079 | -0.056009 | -0.014061 | 2.9675e-05 | 1.8857e-05 | 0.085409 | 0.085409 | 0.085409 | 0.97646 | -0.45246 | 0.9759 | -0.46356 | 23.464
15 | 0.024631 | 0.0061818 | -0.024607 | -0.0061671 | 2.3769e-05 | 1.465e-05 | 0.037538 | 0.037538 | 0.037538 | 0.97646 | -0.45246 | 0.97543 | -0.47272 | 10.3127
16 | 0.056009 | 0.014061 | -0.055948 | -0.014022 | 6.0738e-05 | 3.8595e-05 | 0.085409 | 0.085409 | 0.085409 | 0.9759 | -0.46356 | 0.97474 | -0.48632 | 23.464
17 | -0.0007476 | -0.00018676 | 0.00074761 | 0.00018646 | 1.2402e-08 | -3.0478e-07 | 0.0011446 | 0.0011445 | 0.0011446 | 0.9717 | -0.54556 | 0.97172 | -0.54521 | 0.31446
18 | 0.0007476 | 0.00018676 | -0.00074757 | -0.00018736 | 2.4202e-08 | -5.9457e-07 | 0.0011446 | 0.0011448 | 0.0011448 | 0.9717 | -0.54556 | 0.97166 | -0.54624 | 0.31452
19 | -0.045301 | -0.011366 | 0.045327 | 0.011382 | 2.617e-05 | 1.6569e-05 | 0.069376 | 0.069376 | 0.069376 | 0.97172 | -0.54521 | 0.97233 | -0.53311 | 19.0592
20 | 0.006453 | 0.0016174 | -0.0064522 | -0.0016171 | 8.4135e-07 | 2.5388e-07 | 0.0098817 | 0.0098818 | 0.0098818 | 0.97172 | -0.54521 | 0.97158 | -0.54795 | 2.7148
21 | 0.038101 | 0.0095619 | -0.038067 | -0.0095404 | 3.4085e-05 | 2.1484e-05 | 0.058349 | 0.058349 | 0.058349 | 0.97172 | -0.54521 | 0.97077 | -0.56399 | 16.0301
22 | -0.085395 | -0.021533 | 0.085577 | 0.021649 | 0.00018208 | 0.00011617 | 0.13022 | 0.13022 | 0.13022 | 0.97613 | -0.45822 | 0.97841 | -0.41378 | 35.7757
23 | 0.085395 | 0.021533 | -0.085184 | -0.021398 | 0.00021143 | 0.0001349 | 0.13022 | 0.13022 | 0.13022 | 0.97613 | -0.45822 | 0.97349 | -0.51009 | 35.7757
24 | 0.014535 | 0.0036438 | -0.014532 | -0.0036421 | 2.9695e-06 | 1.697e-06 | 0.022106 | 0.022106 | 0.022106 | 0.97841 | -0.41378 | 0.97819 | -0.41807 | 6.0732
25 | 0.063865 | 0.016055 | -0.063795 | -0.016011 | 7.0092e-05 | 4.4615e-05 | 0.097638 | 0.097638 | 0.097638 | 0.97349 | -0.51009 | 0.97233 | -0.53311 | 26.8236
26 | 0.0064522 | 0.0016171 | -0.0064513 | -0.0016168 | 8.9034e-07 | 2.6876e-07 | 0.0098818 | 0.0098819 | 0.0098819 | 0.97158 | -0.54795 | 0.97143 | -0.55085 | 2.7148
27 | -0.31659 | -0.08095 | 0.31849 | 0.082161 | 0.001897 | 0.0012114 | 0.47475 | 0.47475 | 0.47475 | 0.9935 | -0.12304 | 1 | 0 | 43.4751

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.35839 | 0.091749

## res_load
| p_mw | q_mvar
0 | 0.031022 | 0.0077748
1 | 0.011542 | 0.0028927
2 | 0.020341 | 0.005098
3 | 0.010345 | 0.0025928
4 | 0.048015 | 0.012034
5 | 0.024607 | 0.0061671
6 | 0.055948 | 0.014022
7 | 0.00074757 | 0.00018736
8 | 0.021319 | 0.0053429
9 | 0.018468 | 0.0046284
10 | 0.038067 | 0.0095404
11 | 0.0064513 | 0.0016168
12 | 0.011037 | 0.0027662
13 | 0.014532 | 0.0036421
14 | 0.038257 | 0.0095881

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1