## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-636_0_7_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-636_0_7_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-636_0_7_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_261-636_0_7_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_261-636_0_7_node_51 | 0.4 | n |  | TRUE
5 | bus_LV_261-636_0_7_node_48 | 0.4 | n |  | TRUE
6 | bus_LV_261-636_0_7_node_23 | 0.4 | n |  | TRUE
7 | bus_LV_261-636_0_7_node_25 | 0.4 | n |  | TRUE
8 | bus_LV_261-636_0_7_node_129 | 0.4 | n |  | TRUE
9 | bus_LV_261-636_0_7_node_8 | 0.4 | n |  | TRUE
10 | bus_LV_261-636_0_7_node_18 | 0.4 | n |  | TRUE
11 | bus_LV_261-636_0_7_node_26 | 0.4 | n |  | TRUE
12 | bus_LV_261-636_0_7_node_6 | 0.4 | n |  | TRUE
13 | bus_LV_261-636_0_7_node_24 | 0.4 | n |  | TRUE
14 | bus_LV_261-636_0_7_node_126 | 0.4 | n |  | TRUE
15 | bus_LV_261-636_0_7_node_14 | 0.4 | n |  | TRUE
16 | bus_LV_261-636_0_7_node_29 | 0.4 | n |  | TRUE
17 | bus_LV_261-636_0_7_node_34 | 0.4 | n |  | TRUE
18 | bus_LV_261-636_0_7_node_120 | 0.4 | n |  | TRUE
19 | bus_LV_261-636_0_7_node_28 | 0.4 | n |  | TRUE
20 | bus_LV_261-636_0_7_node_101 | 0.4 | n |  | TRUE
21 | bus_LV_261-636_0_7_node_103 | 0.4 | n |  | TRUE
22 | bus_LV_261-636_0_7_node_46 | 0.4 | n |  | TRUE
23 | bus_LV_261-636_0_7_node_19 | 0.4 | n |  | TRUE
24 | bus_LV_261-636_0_7_node_7 | 0.4 | n |  | TRUE
25 | bus_LV_261-636_0_7_node_9 | 0.4 | n |  | TRUE
26 | bus_LV_261-636_0_7_node_10 | 0.4 | n |  | TRUE
27 | bus_LV_261-636_0_7_node_5 | 0.4 | n |  | TRUE
28 | bus_LV_261-636_0_7_node_12 | 0.4 | n |  | TRUE
29 | bus_LV_261-636_0_7_node_97 | 0.4 | n |  | TRUE
30 | bus_LV_261-636_0_7_node_11 | 0.4 | n |  | TRUE
31 | bus_LV_261-636_0_7_node_96 | 0.4 | n |  | TRUE
32 | bus_LV_261-636_0_7_node_55 | 0.4 | n |  | TRUE
33 | bus_LV_261-636_0_7_node_47 | 0.4 | n |  | TRUE
34 | bus_LV_261-636_0_7_node_13 | 0.4 | n |  | TRUE
35 | bus_LV_261-636_0_7_node_111 | 0.4 | n |  | TRUE
36 | bus_LV_261-636_0_7_node_109 | 0.4 | n |  | TRUE
37 | bus_LV_261-636_0_7_node_76 | 0.4 | n |  | TRUE
38 | bus_LV_261-636_0_7_node_22 | 0.4 | n |  | TRUE
39 | bus_LV_261-636_0_7_node_73 | 0.4 | n |  | TRUE
40 | bus_LV_261-636_0_7_node_16 | 0.4 | n |  | TRUE
41 | bus_LV_261-636_0_7_node_31 | 0.4 | n |  | TRUE
42 | bus_LV_261-636_0_7_node_128 | 0.4 | n |  | TRUE
43 | bus_LV_261-636_0_7_node_17 | 0.4 | n |  | TRUE
44 | bus_LV_261-636_0_7_node_33 | 0.4 | n |  | TRUE
45 | bus_LV_261-636_0_7_node_53 | 0.4 | n |  | TRUE
46 | bus_LV_261-636_0_7_node_67 | 0.4 | n |  | TRUE
47 | bus_LV_261-636_0_7_node_84 | 0.4 | n |  | TRUE
48 | bus_LV_261-636_0_7_node_82 | 0.4 | n |  | TRUE
49 | bus_LV_261-636_0_7_node_20 | 0.4 | n |  | TRUE
50 | bus_LV_261-636_0_7_node_71 | 0.4 | n |  | TRUE
51 | bus_LV_261-636_0_7_node_54 | 0.4 | n |  | TRUE
52 | bus_LV_261-636_0_7_node_69 | 0.4 | n |  | TRUE
53 | bus_LV_261-636_0_7_node_42 | 0.4 | n |  | TRUE
54 | bus_LV_261-636_0_7_node_68 | 0.4 | n |  | TRUE
55 | bus_LV_261-636_0_7_node_43 | 0.4 | n |  | TRUE
56 | bus_LV_261-636_0_7_node_30 | 0.4 | n |  | TRUE
57 | bus_LV_261-636_0_7_node_70 | 0.4 | n |  | TRUE
58 | bus_LV_261-636_0_7_node_122 | 0.4 | n |  | TRUE
59 | bus_LV_261-636_0_7_node_121 | 0.4 | n |  | TRUE
60 | bus_LV_261-636_0_7_node_32 | 0.4 | n |  | TRUE
61 | bus_LV_261-636_0_7_node_112 | 0.4 | n |  | TRUE
62 | bus_LV_261-636_0_7_node_37 | 0.4 | n |  | TRUE
63 | bus_LV_261-636_0_7_node_98 | 0.4 | n |  | TRUE
64 | bus_LV_261-636_0_7_node_38 | 0.4 | n |  | TRUE
65 | bus_LV_261-636_0_7_node_81 | 0.4 | n |  | TRUE
66 | bus_LV_261-636_0_7_node_79 | 0.4 | n |  | TRUE
67 | bus_LV_261-636_0_7_node_94 | 0.4 | n |  | TRUE
68 | bus_LV_261-636_0_7_node_49 | 0.4 | n |  | TRUE
69 | bus_LV_261-636_0_7_node_65 | 0.4 | n |  | TRUE
70 | bus_LV_261-636_0_7_node_64 | 0.4 | n |  | TRUE
71 | bus_LV_261-636_0_7_node_39 | 0.4 | n |  | TRUE
72 | bus_LV_261-636_0_7_node_89 | 0.4 | n |  | TRUE
73 | bus_LV_261-636_0_7_node_99 | 0.4 | n |  | TRUE
74 | bus_LV_261-636_0_7_node_91 | 0.4 | n |  | TRUE
75 | bus_LV_261-636_0_7_node_63 | 0.4 | n |  | TRUE
76 | bus_LV_261-636_0_7_node_110 | 0.4 | n |  | TRUE
77 | bus_LV_261-636_0_7_node_123 | 0.4 | n |  | TRUE
78 | bus_LV_261-636_0_7_node_74 | 0.4 | n |  | TRUE
79 | bus_LV_261-636_0_7_node_125 | 0.4 | n |  | TRUE
80 | bus_LV_261-636_0_7_node_124 | 0.4 | n |  | TRUE
81 | bus_LV_261-636_0_7_node_66 | 0.4 | n |  | TRUE
82 | bus_LV_261-636_0_7_node_95 | 0.4 | n |  | TRUE
83 | bus_LV_261-636_0_7_node_83 | 0.4 | n |  | TRUE
84 | bus_LV_261-636_0_7_node_41 | 0.4 | n |  | TRUE
85 | bus_LV_261-636_0_7_node_100 | 0.4 | n |  | TRUE
86 | bus_LV_261-636_0_7_node_104 | 0.4 | n |  | TRUE
87 | bus_LV_261-636_0_7_node_102 | 0.4 | n |  | TRUE
88 | bus_LV_261-636_0_7_node_115 | 0.4 | n |  | TRUE
89 | bus_LV_261-636_0_7_node_116 | 0.4 | n |  | TRUE
90 | bus_LV_261-636_0_7_node_117 | 0.4 | n |  | TRUE
91 | bus_LV_261-636_0_7_node_119 | 0.4 | n |  | TRUE
92 | bus_LV_261-636_0_7_node_72 | 0.4 | n |  | TRUE
93 | bus_LV_261-636_0_7_node_114 | 0.4 | n |  | TRUE
94 | bus_LV_261-636_0_7_node_44 | 0.4 | n |  | TRUE
95 | bus_LV_261-636_0_7_node_45 | 0.4 | n |  | TRUE
96 | bus_LV_261-636_0_7_node_80 | 0.4 | n |  | TRUE
97 | bus_LV_261-636_0_7_node_90 | 0.4 | n |  | TRUE
98 | bus_LV_261-636_0_7_node_86 | 0.4 | n |  | TRUE
99 | bus_LV_261-636_0_7_node_88 | 0.4 | n |  | TRUE
100 | bus_LV_261-636_0_7_node_50 | 0.4 | n |  | TRUE
101 | bus_LV_261-636_0_7_node_56 | 0.4 | n |  | TRUE
102 | bus_LV_261-636_0_7_node_57 | 0.4 | n |  | TRUE
103 | bus_LV_261-636_0_7_node_58 | 0.4 | n |  | TRUE
104 | bus_LV_261-636_0_7_node_59 | 0.4 | n |  | TRUE
105 | bus_LV_261-636_0_7_node_60 | 0.4 | n |  | TRUE
106 | bus_LV_261-636_0_7_node_61 | 0.4 | n |  | TRUE
107 | bus_LV_261-636_0_7_node_62 | 0.4 | n |  | TRUE
108 | bus_LV_261-636_0_7_node_75 | 0.4 | n |  | TRUE
109 | bus_LV_261-636_0_7_node_77 | 0.4 | n |  | TRUE
110 | bus_LV_261-636_0_7_node_78 | 0.4 | n |  | TRUE
111 | bus_LV_261-636_0_7_node_105 | 0.4 | n |  | TRUE
112 | bus_LV_261-636_0_7_node_106 | 0.4 | n |  | TRUE
113 | bus_LV_261-636_0_7_node_85 | 0.4 | n |  | TRUE
114 | bus_LV_261-636_0_7_node_87 | 0.4 | n |  | TRUE
115 | bus_LV_261-636_0_7_node_107 | 0.4 | n |  | TRUE
116 | bus_LV_261-636_0_7_node_108 | 0.4 | n |  | TRUE
117 | bus_LV_261-636_0_7_node_113 | 0.4 | n |  | TRUE
118 | bus_LV_261-636_0_7_node_118 | 0.4 | n |  | TRUE
119 | bus_LV_261-636_0_7_node_130 | 0.4 | n |  | TRUE
120 | bus_MV_527_0_node_124 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-636_0_7_load_0 | 0 | 0.016648 | 0.0041723 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-636_0_7_load_1 | 1 | 0.016995 | 0.0042592 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-636_0_7_load_51 | 4 | 0.0021274 | 0.00053318 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-636_0_7_load_48 | 5 | 0.0042962 | 0.0010767 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-636_0_7_load_129 | 8 | 0.026666 | 0.0066832 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-636_0_7_load_6 | 12 | 0.01252 | 0.0031377 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-636_0_7_load_126 | 14 | 0.0030448 | 0.00076311 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-636_0_7_load_120 | 18 | 0.0011342 | 0.00028425 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-636_0_7_load_101 | 20 | 0.014454 | 0.0036226 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-636_0_7_load_46 | 22 | 0.0048444 | 0.0012141 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-636_0_7_load_5 | 27 | 0.021971 | 0.0055065 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-636_0_7_load_97 | 29 | 0.0057106 | 0.0014312 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-636_0_7_load_96 | 31 | 0.0023959 | 0.00060048 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-636_0_7_load_55 | 32 | 0.008195 | 0.0020539 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-636_0_7_load_47 | 33 | 0.0083858 | 0.0021017 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-636_0_7_load_111 | 35 | 0.0092893 | 0.0023281 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-636_0_7_load_109 | 36 | 0.0049233 | 0.0012339 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_261-636_0_7_load_76 | 37 | 0.0048551 | 0.0012168 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_261-636_0_7_load_73 | 39 | 0.0040445 | 0.0010137 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_261-636_0_7_load_128 | 42 | 0.0038483 | 0.00096447 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_261-636_0_7_load_53 | 45 | 0.0047983 | 0.0012026 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_261-636_0_7_load_67 | 46 | 0.0094345 | 0.0023645 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_261-636_0_7_load_84 | 47 | 0.0055733 | 0.0013968 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_261-636_0_7_load_82 | 48 | 0.013002 | 0.0032586 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_261-636_0_7_load_71 | 50 | 0.0074397 | 0.0018646 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_261-636_0_7_load_54 | 51 | 0.0049037 | 0.001229 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_261-636_0_7_load_69 | 52 | 0.0018144 | 0.00045473 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_261-636_0_7_load_42 | 53 | 0.0070343 | 0.001763 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_261-636_0_7_load_68 | 54 | 0.01106 | 0.002772 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_261-636_0_7_load_43 | 55 | 0.0043851 | 0.001099 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_261-636_0_7_load_70 | 57 | 0.002267 | 0.00056816 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_261-636_0_7_load_121 | 59 | 0.015137 | 0.0037938 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_261-636_0_7_load_112 | 61 | 0.0027311 | 0.00068447 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_261-636_0_7_load_98 | 63 | 0.0039654 | 0.00099383 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_261-636_0_7_load_81 | 65 | 0.0048871 | 0.0012248 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_261-636_0_7_load_79 | 66 | 0.017777 | 0.0044553 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_261-636_0_7_load_94 | 67 | 0.0023949 | 0.00060023 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_261-636_0_7_load_49 | 68 | 0.0025192 | 0.00063137 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_261-636_0_7_load_65 | 69 | 0.0036448 | 0.00091347 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_261-636_0_7_load_64 | 70 | 0.0029856 | 0.00074825 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_261-636_0_7_load_99 | 73 | 0.01354 | 0.0033934 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_261-636_0_7_load_91 | 74 | 0.0037576 | 0.00094175 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_261-636_0_7_load_63 | 75 | 0.0025841 | 0.00064763 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_261-636_0_7_load_110 | 76 | 0.0083287 | 0.0020874 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_261-636_0_7_load_123 | 77 | 0.0049737 | 0.0012465 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_261-636_0_7_load_74 | 78 | 0.0041626 | 0.0010433 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_261-636_0_7_load_125 | 79 | 0.0093364 | 0.0023399 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_261-636_0_7_load_124 | 80 | 0.0040862 | 0.0010241 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_261-636_0_7_load_66 | 81 | 0.0068918 | 0.0017272 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_261-636_0_7_load_95 | 82 | 0.0048349 | 0.0012117 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_261-636_0_7_load_83 | 83 | 0.0019586 | 0.00049088 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_261-636_0_7_load_41 | 84 | 0.004202 | 0.0010531 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_261-636_0_7_load_100 | 85 | 0.013575 | 0.0034022 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_261-636_0_7_load_104 | 86 | 0.0025278 | 0.00063352 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_261-636_0_7_load_102 | 87 | 0.013244 | 0.0033193 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_261-636_0_7_load_117 | 90 | 0.011141 | 0.0027922 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_261-636_0_7_load_72 | 92 | 0.0019247 | 0.00048236 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_261-636_0_7_load_114 | 93 | 0.0058133 | 0.001457 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_261-636_0_7_load_44 | 94 | 0.0051132 | 0.0012815 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_261-636_0_7_load_45 | 95 | 0.0037132 | 0.00093062 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_261-636_0_7_load_80 | 96 | 0.0048656 | 0.0012194 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_261-636_0_7_load_90 | 97 | 0.0064874 | 0.0016259 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_261-636_0_7_load_86 | 98 | 0.0054637 | 0.0013693 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_261-636_0_7_load_88 | 99 | 0.011989 | 0.0030047 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_261-636_0_7_load_50 | 100 | 0.0032284 | 0.00080912 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_261-636_0_7_load_56 | 101 | 0.002583 | 0.00064737 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_261-636_0_7_load_58 | 103 | 0.0025173 | 0.00063091 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_261-636_0_7_load_59 | 104 | 0.019802 | 0.0049629 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_261-636_0_7_load_60 | 105 | 0.0024252 | 0.00060782 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_261-636_0_7_load_61 | 106 | 0.0022582 | 0.00056597 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_261-636_0_7_load_62 | 107 | 0.0021988 | 0.00055108 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_261-636_0_7_load_75 | 108 | 0.0040195 | 0.0010074 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_261-636_0_7_load_77 | 109 | 0.002995 | 0.00075063 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_261-636_0_7_load_78 | 110 | 0.0032896 | 0.00082445 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_261-636_0_7_load_105 | 111 | 0.0015312 | 0.00038374 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_261-636_0_7_load_106 | 112 | 0.0061313 | 0.0015367 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_261-636_0_7_load_85 | 113 | 0.0074693 | 0.001872 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_261-636_0_7_load_87 | 114 | 0.0019401 | 0.00048624 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_261-636_0_7_load_107 | 115 | 0.010057 | 0.0025205 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_261-636_0_7_load_113 | 117 | 0.01111 | 0.0027844 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_261-636_0_7_load_118 | 118 | 0.0027413 | 0.00068703 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_261-636_0_7_load_130 | 119 | 0.012669 | 0.0031752 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 49 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-636_0_7_line_0 |  | 0 | 1 | 0.039545 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-636_0_7_line_1 |  | 0 | 2 | 0.010828 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-636_0_7_line_2 |  | 2 | 3 | 0.009143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-636_0_7_line_3 |  | 3 | 4 | 0.034804 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-636_0_7_line_4 |  | 3 | 5 | 0.020945 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_261-636_0_7_line_5 |  | 4 | 67 | 0.0031225 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_261-636_0_7_line_6 |  | 5 | 68 | 0.01845 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_261-636_0_7_line_7 |  | 6 | 7 | 0.014403 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_261-636_0_7_line_8 |  | 6 | 8 | 0.011748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_261-636_0_7_line_9 |  | 7 | 54 | 0.024924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_261-636_0_7_line_10 |  | 7 | 38 | 0.015246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_261-636_0_7_line_11 |  | 9 | 10 | 0.017625 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_261-636_0_7_line_12 |  | 9 | 11 | 0.011304 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-636_0_7_line_13 |  | 9 | 12 | 0.0044354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_261-636_0_7_line_14 |  | 10 | 46 | 0.029076 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_261-636_0_7_line_15 |  | 11 | 55 | 0.022621 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
16 | LV_261-636_0_7_line_16 |  | 11 | 43 | 0.0098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
17 | LV_261-636_0_7_line_17 |  | 13 | 14 | 0.037573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_261-636_0_7_line_18 |  | 13 | 15 | 0.017097 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_261-636_0_7_line_19 |  | 14 | 80 | 0.028499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_261-636_0_7_line_20 |  | 15 | 37 | 0.049295 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_261-636_0_7_line_21 |  | 15 | 38 | 0.034492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
22 | LV_261-636_0_7_line_22 |  | 15 | 39 | 0.013884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
23 | LV_261-636_0_7_line_23 |  | 16 | 17 | 0.012958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
24 | LV_261-636_0_7_line_24 |  | 16 | 18 | 0.032165 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
25 | LV_261-636_0_7_line_25 |  | 16 | 19 | 0.030674 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_261-636_0_7_line_26 |  | 17 | 22 | 0.0019217 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_261-636_0_7_line_27 |  | 17 | 23 | 0.035162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
28 | LV_261-636_0_7_line_28 |  | 18 | 91 | 0.018735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
29 | LV_261-636_0_7_line_29 |  | 19 | 20 | 0.044116 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_261-636_0_7_line_30 |  | 19 | 21 | 0.003434 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_261-636_0_7_line_31 |  | 20 | 85 | 0.028627 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_261-636_0_7_line_32 |  | 21 | 86 | 0.0055368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_261-636_0_7_line_33 |  | 21 | 87 | 0.0083119 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_261-636_0_7_line_34 |  | 22 | 95 | 0.022329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_261-636_0_7_line_35 |  | 23 | 47 | 0.021443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_261-636_0_7_line_36 |  | 23 | 48 | 0.0017454 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_261-636_0_7_line_37 |  | 24 | 25 | 0.023575 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_261-636_0_7_line_38 |  | 24 | 26 | 0.014602 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_261-636_0_7_line_39 |  | 24 | 27 | 0.027033 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_261-636_0_7_line_40 |  | 25 | 69 | 0.032713 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_261-636_0_7_line_41 |  | 25 | 70 | 0.01013 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_261-636_0_7_line_42 |  | 25 | 30 | 0.004856 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_261-636_0_7_line_43 |  | 26 | 28 | 0.011084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_261-636_0_7_line_44 |  | 26 | 29 | 0.011352 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_261-636_0_7_line_45 |  | 28 | 32 | 0.01422 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_261-636_0_7_line_46 |  | 28 | 33 | 0.030259 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_261-636_0_7_line_47 |  | 29 | 62 | 0.012834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_261-636_0_7_line_48 |  | 30 | 31 | 0.027308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_261-636_0_7_line_49 |  | 33 | 44 | 0.0285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
50 | LV_261-636_0_7_line_50 |  | 34 | 35 | 0.019351 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_261-636_0_7_line_51 |  | 34 | 36 | 0.044488 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_261-636_0_7_line_52 |  | 36 | 76 | 0.0034548 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_261-636_0_7_line_53 |  | 37 | 77 | 0.017728 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_261-636_0_7_line_54 |  | 38 | 53 | 0.0070971 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
55 | LV_261-636_0_7_line_55 |  | 39 | 78 | 0.012785 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
56 | LV_261-636_0_7_line_56 |  | 40 | 41 | 0.046391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_261-636_0_7_line_57 |  | 40 | 42 | 0.015518 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_261-636_0_7_line_58 |  | 41 | 58 | 0.009716 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_261-636_0_7_line_59 |  | 41 | 59 | 0.016224 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_261-636_0_7_line_60 |  | 43 | 44 | 0.013398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
61 | LV_261-636_0_7_line_61 |  | 43 | 45 | 0.0029671 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
62 | LV_261-636_0_7_line_62 |  | 45 | 51 | 0.029515 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
63 | LV_261-636_0_7_line_63 |  | 46 | 81 | 0.0058405 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_261-636_0_7_line_64 |  | 47 | 82 | 0.017594 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_261-636_0_7_line_65 |  | 48 | 83 | 0.02689 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_261-636_0_7_line_66 |  | 49 | 50 | 0.035768 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_261-636_0_7_line_67 |  | 49 | 51 | 0.015611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
68 | LV_261-636_0_7_line_68 |  | 49 | 52 | 0.011003 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_261-636_0_7_line_69 |  | 52 | 56 | 0.018709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_261-636_0_7_line_70 |  | 53 | 84 | 0.026363 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
71 | LV_261-636_0_7_line_71 |  | 55 | 84 | 0.018797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
72 | LV_261-636_0_7_line_72 |  | 56 | 57 | 0.010525 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_261-636_0_7_line_73 |  | 57 | 92 | 0.01499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_261-636_0_7_line_74 |  | 58 | 93 | 0.037853 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_261-636_0_7_line_75 |  | 59 | 60 | 0.036768 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_261-636_0_7_line_76 |  | 60 | 61 | 0.017296 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_261-636_0_7_line_77 |  | 62 | 63 | 0.024428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_261-636_0_7_line_78 |  | 64 | 65 | 0.027415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_261-636_0_7_line_79 |  | 64 | 66 | 0.01647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_261-636_0_7_line_80 |  | 65 | 98 | 0.018293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_261-636_0_7_line_81 |  | 68 | 100 | 0.016463 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_261-636_0_7_line_82 |  | 69 | 74 | 0.0005329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_261-636_0_7_line_83 |  | 70 | 75 | 0.018205 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_261-636_0_7_line_84 |  | 71 | 72 | 0.037472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_261-636_0_7_line_85 |  | 71 | 73 | 0.020686 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_261-636_0_7_line_86 |  | 72 | 97 | 0.022156 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_261-636_0_7_line_87 |  | 72 | 99 | 0.01602 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_261-636_0_7_line_88 |  | 75 | 107 | 0.012503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_261-636_0_7_line_89 |  | 76 | 116 | 0.0413 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_261-636_0_7_line_90 |  | 78 | 108 | 0.015622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
91 | LV_261-636_0_7_line_91 |  | 79 | 80 | 0.029472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_261-636_0_7_line_92 |  | 83 | 113 | 0.013256 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_261-636_0_7_line_93 |  | 83 | 98 | 0.01637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_261-636_0_7_line_94 |  | 86 | 88 | 0.0036366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_261-636_0_7_line_95 |  | 88 | 89 | 0.034089 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_261-636_0_7_line_96 |  | 88 | 90 | 0.026095 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_261-636_0_7_line_97 |  | 89 | 119 | 0.016825 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_261-636_0_7_line_98 |  | 91 | 118 | 0.00082623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
99 | LV_261-636_0_7_line_99 |  | 93 | 116 | 0.020666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_261-636_0_7_line_100 |  | 94 | 95 | 0.027941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_261-636_0_7_line_101 |  | 96 | 97 | 0.016453 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_261-636_0_7_line_102 |  | 99 | 114 | 0.017062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_261-636_0_7_line_103 |  | 100 | 101 | 0.0011995 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_261-636_0_7_line_104 |  | 101 | 102 | 0.011712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_261-636_0_7_line_105 |  | 102 | 103 | 0.006469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_261-636_0_7_line_106 |  | 102 | 104 | 0.020055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_261-636_0_7_line_107 |  | 103 | 105 | 0.00011291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_261-636_0_7_line_108 |  | 105 | 106 | 0.01036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_261-636_0_7_line_109 |  | 106 | 107 | 0.0055742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_261-636_0_7_line_110 |  | 108 | 109 | 0.0066659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
111 | LV_261-636_0_7_line_111 |  | 109 | 110 | 0.0086515 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
112 | LV_261-636_0_7_line_112 |  | 110 | 111 | 0.017903 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
113 | LV_261-636_0_7_line_113 |  | 111 | 112 | 0.030192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
114 | LV_261-636_0_7_line_114 |  | 112 | 115 | 0.00044689 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
115 | LV_261-636_0_7_line_115 |  | 113 | 114 | 0.0183 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_261-636_0_7_line_116 |  | 115 | 116 | 0.022786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
117 | LV_261-636_0_7_line_117 |  | 116 | 117 | 0.022187 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
118 | LV_261-636_0_7_line_118 |  | 117 | 118 | 0.023432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-636_0_7_trafo_20 | 0.63 MVA 20/0.4 kV | 120 | 49 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2678825.8235 | 1248547.0379 | 2678856.1366 | 1248572.4325
1 | 2678817.5231 | 1248540.0844 | 2678825.8235 | 1248547.0379
2 | 2678812.0778 | 1248532.7289 | 2678817.5231 | 1248540.0844
3 | 2678812.0778 | 1248532.7289 | 2678798.4305 | 1248512.3438 | 2678792.015 | 1248504.321
4 | 2678812.0778 | 1248532.7289 | 2678814.5421 | 1248528.5808 | 2678823.5836 | 1248515.2355
5 | 2678792.015 | 1248504.321 | 2678791.1059 | 1248503.1842 | 2678789.9268 | 1248502.0061
6 | 2678823.5836 | 1248515.2355 | 2678833.9324 | 1248499.9606
7 | 2678932.2105 | 1248565.9955 | 2678930.2477 | 1248576.7105 | 2678928.2308 | 1248579.5858
8 | 2678928.2308 | 1248579.5858 | 2678919.0988 | 1248585.3796 | 2678918.2858 | 1248585.8368
9 | 2678932.2105 | 1248565.9955 | 2678932.4272 | 1248555.9577 | 2678932.3238 | 1248546.7163 | 2678931.0652 | 1248541.2165
10 | 2678932.2105 | 1248565.9955 | 2678941.1429 | 1248565.5474 | 2678947.4378 | 1248565.2421
11 | 2678920.5281 | 1248495.0772 | 2678924.4377 | 1248512.264
12 | 2678920.5281 | 1248495.0772 | 2678925.8559 | 1248493.6693 | 2678931.4567 | 1248492.1872
13 | 2678920.5281 | 1248495.0772 | 2678919.5272 | 1248490.7562
14 | 2678924.4377 | 1248512.264 | 2678907.5861 | 1248515.8868 | 2678905.9474 | 1248516.4431 | 2678904.8246 | 1248516.8285 | 2678902.6315 | 1248518.7563 | 2678901.8764 | 1248521.0145 | 2678900.7297 | 1248524.4483
15 | 2678931.4567 | 1248492.1872 | 2678936.4181 | 1248514.2575
16 | 2678933.8109 | 1248483.2676 | 2678931.3153 | 1248486.3588 | 2678931.4567 | 1248492.1872
17 | 2678985.609 | 1248576.3141 | 2679020.2116 | 1248561.6729
18 | 2678979.7968 | 1248560.236 | 2678983.0635 | 1248568.9859 | 2678985.609 | 1248576.3141
19 | 2679046.4581 | 1248550.5673 | 2679020.2116 | 1248561.6729
20 | 2678979.7968 | 1248560.236 | 2678990.2115 | 1248556.2385 | 2679025.3074 | 1248541.31
21 | 2678947.4378 | 1248565.2421 | 2678949.8898 | 1248567.1206 | 2678952.5445 | 1248567.9565 | 2678958.6705 | 1248567.8602 | 2678968.671 | 1248564.9024 | 2678979.7968 | 1248560.236
22 | 2678979.7968 | 1248560.236 | 2678977.6568 | 1248553.6472 | 2678977.927 | 1248550.3706 | 2678979.3166 | 1248546.9755
23 | 2678998.0881 | 1248392.5351 | 2679004.1892 | 1248394.3177 | 2679008.7479 | 1248396.2354 | 2679009.8817 | 1248395.0274
24 | 2679009.8817 | 1248395.0274 | 2679012.7617 | 1248397.1006 | 2679021.9289 | 1248417.5711 | 2679025.3416 | 1248422.7314
25 | 2679034.7371 | 1248380.2256 | 2679033.9768 | 1248382.873 | 2679032.9052 | 1248382.8142 | 2679026.5295 | 1248384.6306 | 2679019.85 | 1248386.5763 | 2679017.2515 | 1248387.7536 | 2679014.0239 | 1248390.2235 | 2679009.8817 | 1248395.0274
26 | 2678998.0881 | 1248392.5351 | 2678997.5828 | 1248394.3892
27 | 2678999.5332 | 1248362.3212 | 2679003.7887 | 1248384.7054 | 2678998.5677 | 1248385.4586 | 2678998.5236 | 1248388.7604 | 2678998.0881 | 1248392.5351
28 | 2679035.6761 | 1248438.3583 | 2679025.3416 | 1248422.7314
29 | 2679034.7371 | 1248380.2256 | 2679033.7192 | 1248375.5753 | 2679032.1259 | 1248368.7602 | 2679028.675 | 1248354.0035 | 2679030.0223 | 1248345.8488 | 2679027.1715 | 1248337.3787
30 | 2679038.021 | 1248379.1909 | 2679034.7371 | 1248380.2256
31 | 2679023.8053 | 1248310.2845 | 2679024.7857 | 1248312.6548 | 2679021.8571 | 1248321.589 | 2679027.1715 | 1248337.3787
32 | 2679038.021 | 1248379.1909 | 2679039.756 | 1248384.4488
33 | 2679038.021 | 1248379.1909 | 2679035.5714 | 1248371.2481
34 | 2678984.7217 | 1248412.3632 | 2678985.2576 | 1248411.7449 | 2678994.1758 | 1248401.0559 | 2678996.8018 | 1248397.2548 | 2678997.5828 | 1248394.3892
35 | 2678999.5332 | 1248362.3212 | 2678995.6933 | 1248363.1374 | 2678991.9772 | 1248363.7327 | 2678985.3093 | 1248365.9455 | 2678979.4547 | 1248369.2612
36 | 2678999.5332 | 1248362.3212 | 2678999.2085 | 1248360.6063
37 | 2678885.9375 | 1248423.1867 | 2678889.0733 | 1248425.33 | 2678889.9144 | 1248425.1188 | 2678891.3575 | 1248425.0713 | 2678894.1904 | 1248427.2772 | 2678898.0376 | 1248429.3077 | 2678903.2177 | 1248431.0668 | 2678907.2881 | 1248431.6436
38 | 2678907.2881 | 1248431.6436 | 2678906.7538 | 1248427.5335 | 2678905.9789 | 1248417.1045
39 | 2678907.2881 | 1248431.6436 | 2678907.7946 | 1248435.5754 | 2678908.5971 | 1248441.6683 | 2678909.6131 | 1248447.6084 | 2678912.0406 | 1248458.2315
40 | 2678885.9375 | 1248423.1867 | 2678883.1012 | 1248421.2364 | 2678883.1922 | 1248419.503 | 2678882.044 | 1248417.8199 | 2678869.4459 | 1248407.6894 | 2678868.5273 | 1248406.9099 | 2678863.1175 | 1248402.557 | 2678862.2039 | 1248401.8057
41 | 2678885.9375 | 1248423.1867 | 2678880.2564 | 1248431.5742
42 | 2678885.9375 | 1248423.1867 | 2678888.6645 | 1248419.1645
43 | 2678905.9789 | 1248417.1045 | 2678910.9173 | 1248416.592 | 2678917.005 | 1248415.9726
44 | 2678905.9789 | 1248417.1045 | 2678905.1371 | 1248405.7836
45 | 2678917.005 | 1248415.9726 | 2678915.974 | 1248401.7903
46 | 2678917.005 | 1248415.9726 | 2678917.8821 | 1248426.6698 | 2678918.4306 | 1248433.6823 | 2678919.7529 | 1248440.4381 | 2678920.7205 | 1248445.9618
47 | 2678904.1854 | 1248392.9852 | 2678905.1371 | 1248405.7836
48 | 2678888.6645 | 1248419.1645 | 2678869.7987 | 1248405.0143 | 2678866.922 | 1248402.6481
49 | 2678931.1614 | 1248470.1338 | 2678929.6299 | 1248470.0134 | 2678928.0734 | 1248469.5034 | 2678926.3047 | 1248468.4791 | 2678924.9224 | 1248465.6698 | 2678920.8618 | 1248446.7686 | 2678920.7205 | 1248445.9618
50 | 2679141.4645 | 1248424.3924 | 2679136.4987 | 1248421.3017 | 2679130.6735 | 1248409.1208
51 | 2679141.4645 | 1248424.3924 | 2679137.7072 | 1248426.377 | 2679133.0951 | 1248429.0397 | 2679116.8085 | 1248438.9629 | 2679103.5303 | 1248447.6021
52 | 2679103.5303 | 1248447.6021 | 2679100.6345 | 1248449.4863
53 | 2679025.3074 | 1248541.31 | 2679034.4909 | 1248537.4037 | 2679041.7142 | 1248534.5997
54 | 2678947.4378 | 1248565.2421 | 2678946.3475 | 1248563.1816 | 2678945.4688 | 1248558.4974
55 | 2678979.3166 | 1248546.9755 | 2678985.9522 | 1248539.236 | 2678987.675 | 1248537.3016
56 | 2679111.6146 | 1248507.8216 | 2679114.1876 | 1248515.9063 | 2679116.5216 | 1248523.2317 | 2679111.8876 | 1248525.8384 | 2679110.9944 | 1248528.2505 | 2679111.7004 | 1248532.5075 | 2679121.6269 | 1248547.5398
57 | 2679121.6269 | 1248547.5398 | 2679125.5489 | 1248545.6574 | 2679131.9919 | 1248541.0511 | 2679134.8004 | 1248539.4207
58 | 2679102.4258 | 1248511.057 | 2679111.6146 | 1248507.8216
59 | 2679111.6146 | 1248507.8216 | 2679126.7782 | 1248502.0532
60 | 2678931.1614 | 1248470.1338 | 2678932.1245 | 1248474.939 | 2678933.8109 | 1248483.2676
61 | 2678933.8109 | 1248483.2676 | 2678935.769 | 1248481.0384
62 | 2678955.1874 | 1248458.8117 | 2678950.8885 | 1248463.8252 | 2678935.769 | 1248481.0384
63 | 2678898.8796 | 1248529.9881 | 2678900.7297 | 1248524.4483
64 | 2678964.1451 | 1248377.9314 | 2678979.4547 | 1248369.2612
65 | 2678994.2063 | 1248334.1853 | 2678999.2085 | 1248360.6063
66 | 2678986.2198 | 1248473.2693 | 2678983.1433 | 1248469.5144 | 2678983.0697 | 1248461.4409 | 2678965.349 | 1248446.961
67 | 2678965.349 | 1248446.961 | 2678955.1874 | 1248458.8117
68 | 2678965.349 | 1248446.961 | 2678972.6768 | 1248438.7532
69 | 2678985.1365 | 1248424.7972 | 2678972.6768 | 1248438.7532
70 | 2678940.4135 | 1248532.6251 | 2678941.9687 | 1248539.8396 | 2678945.4688 | 1248558.4974
71 | 2678940.4135 | 1248532.6251 | 2678937.2958 | 1248518.1616 | 2678936.4181 | 1248514.2575
72 | 2678985.1365 | 1248424.7972 | 2678992.9931 | 1248431.8001
73 | 2679004.1833 | 1248441.7745 | 2678992.9931 | 1248431.8001
74 | 2679102.4258 | 1248511.057 | 2679092.2853 | 1248482.6232 | 2679085.1781 | 1248479.7515
75 | 2679161.1436 | 1248488.98 | 2679126.7782 | 1248502.0532
76 | 2679161.1436 | 1248488.98 | 2679156.1025 | 1248472.4348
77 | 2678904.1854 | 1248392.9852 | 2678902.3699 | 1248368.6243
78 | 2678938.4013 | 1248355.2464 | 2678943.4485 | 1248354.502 | 2678947.5041 | 1248352.7992 | 2678950.0481 | 1248350.0533 | 2678953.2661 | 1248347.7277 | 2678957.3152 | 1248346.5141 | 2678962.3081 | 1248343.2342
79 | 2678938.4013 | 1248355.2464 | 2678933.6159 | 1248353.3369 | 2678932.5107 | 1248342.0738
80 | 2678962.3081 | 1248343.2342 | 2678964.2332 | 1248341.9696 | 2678967.4206 | 1248341.9453 | 2678971.7494 | 1248339.579 | 2678977.32 | 1248336.4065 | 2678978.527 | 1248335.5887
81 | 2678843.1666 | 1248486.3308 | 2678833.9324 | 1248499.9606
82 | 2678861.7923 | 1248401.4672 | 2678862.2039 | 1248401.8057
83 | 2678870.0474 | 1248446.6468 | 2678880.2564 | 1248431.5742
84 | 2678974.3356 | 1248273.0316 | 2679004.2805 | 1248250.3918
85 | 2679004.2805 | 1248250.3918 | 2679005.4475 | 1248252.3643 | 2679005.7584 | 1248263.0318 | 2679008.096 | 1248270.3915
86 | 2678974.3356 | 1248273.0316 | 2678956.6384 | 1248286.3623
87 | 2678974.3356 | 1248273.0316 | 2678976.1333 | 1248275.2794 | 2678979.9718 | 1248287.8478
88 | 2678870.0474 | 1248446.6468 | 2678863.0356 | 1248456.9991
89 | 2679066.0172 | 1248472.0096 | 2679100.6345 | 1248449.4863
90 | 2678987.675 | 1248537.3016 | 2678998.0648 | 1248525.6354
91 | 2679046.4581 | 1248550.5673 | 2679049.8084 | 1248549.1497 | 2679073.7997 | 1248539.5675
92 | 2678994.2063 | 1248334.1853 | 2678992.6123 | 1248324.5904 | 2678991.3309 | 1248321.3019
93 | 2678994.2063 | 1248334.1853 | 2678990.8301 | 1248334.7741 | 2678987.0089 | 1248333.6224 | 2678982.4623 | 1248333.6285 | 2678979.1871 | 1248335.1415 | 2678978.527 | 1248335.5887
94 | 2679040.8955 | 1248387.9022 | 2679039.756 | 1248384.4488
95 | 2679060.3666 | 1248415.5264 | 2679043.4447 | 1248389.2927 | 2679040.8955 | 1248387.9022
96 | 2679045.5729 | 1248410.9258 | 2679047.3034 | 1248408.5805 | 2679047.7072 | 1248406.6178 | 2679045.3419 | 1248402.7612 | 2679040.2079 | 1248395.8544 | 2679040.1772 | 1248390.2277 | 2679040.8955 | 1248387.9022
97 | 2679075.5023 | 1248408.0894 | 2679060.3666 | 1248415.5264
98 | 2679036.1316 | 1248439.0476 | 2679035.6761 | 1248438.3583
99 | 2679066.0172 | 1248472.0096 | 2679085.1781 | 1248479.7515
100 | 2678966.4215 | 1248433.477 | 2678966.4888 | 1248433.3996 | 2678984.7217 | 1248412.3632
101 | 2678943.4963 | 1248296.2619 | 2678956.6384 | 1248286.3623
102 | 2678979.9718 | 1248287.8478 | 2678984.0645 | 1248301.2484 | 2678984.8627 | 1248304.1926
103 | 2678843.1666 | 1248486.3308 | 2678843.8394 | 1248485.3378
104 | 2678850.4088 | 1248475.6413 | 2678843.8394 | 1248485.3378
105 | 2678850.4088 | 1248475.6413 | 2678854.0366 | 1248470.2852
106 | 2678850.4088 | 1248475.6413 | 2678867.27 | 1248486.4997
107 | 2678854.0366 | 1248470.2852 | 2678854.0999 | 1248470.1918
108 | 2678854.0999 | 1248470.1918 | 2678859.9096 | 1248461.6143
109 | 2678863.0356 | 1248456.9991 | 2678859.9096 | 1248461.6143
110 | 2678998.0648 | 1248525.6354 | 2679001.3855 | 1248521.9068 | 2679002.7097 | 1248520.8845
111 | 2679009.5578 | 1248515.5976 | 2679002.7097 | 1248520.8845
112 | 2679009.5578 | 1248515.5976 | 2679023.7287 | 1248504.6573
113 | 2679047.6271 | 1248486.2072 | 2679023.7287 | 1248504.6573
114 | 2679047.6271 | 1248486.2072 | 2679047.9809 | 1248485.9341
115 | 2678991.3309 | 1248321.3019 | 2678985.3171 | 1248305.8685 | 2678984.8627 | 1248304.1926
116 | 2679066.0172 | 1248472.0096 | 2679047.9809 | 1248485.9341
117 | 2679066.0172 | 1248472.0096 | 2679053.0195 | 1248454.0281
118 | 2679036.1316 | 1248439.0476 | 2679040.5619 | 1248445.7511 | 2679050.2079 | 1248450.1384 | 2679053.0195 | 1248454.0281

## bus_geodata
| x | y | coords
0 | 2678825.8235 | 1248547.0379
1 | 2678856.1366 | 1248572.4325
2 | 2678817.5231 | 1248540.0844
3 | 2678812.0778 | 1248532.7289
4 | 2678792.015 | 1248504.321
5 | 2678823.5836 | 1248515.2355
6 | 2678928.2308 | 1248579.5858
7 | 2678932.2105 | 1248565.9955
8 | 2678918.2858 | 1248585.8368
9 | 2678920.5281 | 1248495.0772
10 | 2678924.4377 | 1248512.264
11 | 2678931.4567 | 1248492.1872
12 | 2678919.5272 | 1248490.7562
13 | 2678985.609 | 1248576.3141
14 | 2679020.2116 | 1248561.6729
15 | 2678979.7968 | 1248560.236
16 | 2679009.8817 | 1248395.0274
17 | 2678998.0881 | 1248392.5351
18 | 2679025.3416 | 1248422.7314
19 | 2679034.7371 | 1248380.2256
20 | 2679027.1715 | 1248337.3787
21 | 2679038.021 | 1248379.1909
22 | 2678997.5828 | 1248394.3892
23 | 2678999.5332 | 1248362.3212
24 | 2678907.2881 | 1248431.6436
25 | 2678885.9375 | 1248423.1867
26 | 2678905.9789 | 1248417.1045
27 | 2678912.0406 | 1248458.2315
28 | 2678917.005 | 1248415.9726
29 | 2678905.1371 | 1248405.7836
30 | 2678888.6645 | 1248419.1645
31 | 2678866.922 | 1248402.6481
32 | 2678915.974 | 1248401.7903
33 | 2678920.7205 | 1248445.9618
34 | 2679141.4645 | 1248424.3924
35 | 2679130.6735 | 1248409.1208
36 | 2679103.5303 | 1248447.6021
37 | 2679025.3074 | 1248541.31
38 | 2678947.4378 | 1248565.2421
39 | 2678979.3166 | 1248546.9755
40 | 2679121.6269 | 1248547.5398
41 | 2679111.6146 | 1248507.8216
42 | 2679134.8004 | 1248539.4207
43 | 2678933.8109 | 1248483.2676
44 | 2678931.1614 | 1248470.1338
45 | 2678935.769 | 1248481.0384
46 | 2678900.7297 | 1248524.4483
47 | 2678979.4547 | 1248369.2612
48 | 2678999.2085 | 1248360.6063
49 | 2678965.349 | 1248446.961
50 | 2678986.2198 | 1248473.2693
51 | 2678955.1874 | 1248458.8117
52 | 2678972.6768 | 1248438.7532
53 | 2678945.4688 | 1248558.4974
54 | 2678931.0652 | 1248541.2165
55 | 2678936.4181 | 1248514.2575
56 | 2678985.1365 | 1248424.7972
57 | 2678992.9931 | 1248431.8001
58 | 2679102.4258 | 1248511.057
59 | 2679126.7782 | 1248502.0532
60 | 2679161.1436 | 1248488.98
61 | 2679156.1025 | 1248472.4348
62 | 2678904.1854 | 1248392.9852
63 | 2678902.3699 | 1248368.6243
64 | 2678938.4013 | 1248355.2464
65 | 2678962.3081 | 1248343.2342
66 | 2678932.5107 | 1248342.0738
67 | 2678789.9268 | 1248502.0061
68 | 2678833.9324 | 1248499.9606
69 | 2678862.2039 | 1248401.8057
70 | 2678880.2564 | 1248431.5742
71 | 2679004.2805 | 1248250.3918
72 | 2678974.3356 | 1248273.0316
73 | 2679008.096 | 1248270.3915
74 | 2678861.7923 | 1248401.4672
75 | 2678870.0474 | 1248446.6468
76 | 2679100.6345 | 1248449.4863
77 | 2679041.7142 | 1248534.5997
78 | 2678987.675 | 1248537.3016
79 | 2679073.7997 | 1248539.5675
80 | 2679046.4581 | 1248550.5673
81 | 2678898.8796 | 1248529.9881
82 | 2678964.1451 | 1248377.9314
83 | 2678994.2063 | 1248334.1853
84 | 2678940.4135 | 1248532.6251
85 | 2679023.8053 | 1248310.2845
86 | 2679039.756 | 1248384.4488
87 | 2679035.5714 | 1248371.2481
88 | 2679040.8955 | 1248387.9022
89 | 2679060.3666 | 1248415.5264
90 | 2679045.5729 | 1248410.9258
91 | 2679035.6761 | 1248438.3583
92 | 2679004.1833 | 1248441.7745
93 | 2679085.1781 | 1248479.7515
94 | 2678966.4215 | 1248433.477
95 | 2678984.7217 | 1248412.3632
96 | 2678943.4963 | 1248296.2619
97 | 2678956.6384 | 1248286.3623
98 | 2678978.527 | 1248335.5887
99 | 2678979.9718 | 1248287.8478
100 | 2678843.1666 | 1248486.3308
101 | 2678843.8394 | 1248485.3378
102 | 2678850.4088 | 1248475.6413
103 | 2678854.0366 | 1248470.2852
104 | 2678867.27 | 1248486.4997
105 | 2678854.0999 | 1248470.1918
106 | 2678859.9096 | 1248461.6143
107 | 2678863.0356 | 1248456.9991
108 | 2678998.0648 | 1248525.6354
109 | 2679002.7097 | 1248520.8845
110 | 2679009.5578 | 1248515.5976
111 | 2679023.7287 | 1248504.6573
112 | 2679047.6271 | 1248486.2072
113 | 2678991.3309 | 1248321.3019
114 | 2678984.8627 | 1248304.1926
115 | 2679047.9809 | 1248485.9341
116 | 2679066.0172 | 1248472.0096
117 | 2679053.0195 | 1248454.0281
118 | 2679036.1316 | 1248439.0476
119 | 2679075.5023 | 1248408.0894
120 | 2678962.3756 | 1248444.5307

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9761 | -0.46055 | 0.016648 | 0.0041723
1 | 0.97548 | -0.47285 | 0.016995 | 0.0042592
2 | 0.97644 | -0.45389 | 0 | 0
3 | 0.97673 | -0.44827 | 0 | 0
4 | 0.97658 | -0.45114 | 0.0021274 | 0.00053318
5 | 0.97747 | -0.43367 | 0.0042962 | 0.0010767
6 | 0.98865 | -0.21622 | 0 | 0
7 | 0.989 | -0.20937 | 0 | 0
8 | 0.98836 | -0.22181 | 0.026666 | 0.0066832
9 | 0.99418 | -0.11032 | 0 | 0
10 | 0.99392 | -0.1154 | 0 | 0
11 | 0.99448 | -0.10457 | 0 | 0
12 | 0.99413 | -0.1113 | 0.01252 | 0.0031377
13 | 0.98729 | -0.24215 | 0 | 0
14 | 0.98672 | -0.25322 | 0.0030448 | 0.00076311
15 | 0.98755 | -0.23711 | 0 | 0
16 | 0.97782 | -0.42599 | 0 | 0
17 | 0.97755 | -0.43135 | 0 | 0
18 | 0.9789 | -0.40477 | 0.0011342 | 0.00028425
19 | 0.97589 | -0.46387 | 0 | 0
20 | 0.97474 | -0.48653 | 0.014454 | 0.0036226
21 | 0.97576 | -0.46636 | 0 | 0
22 | 0.97752 | -0.43183 | 0.0048444 | 0.0012141
23 | 0.97591 | -0.4634 | 0 | 0
24 | 0.98626 | -0.26233 | 0 | 0
25 | 0.98418 | -0.30271 | 0 | 0
26 | 0.98785 | -0.23168 | 0 | 0
27 | 0.98572 | -0.27298 | 0.021971 | 0.0055065
28 | 0.98915 | -0.20657 | 0 | 0
29 | 0.98775 | -0.23364 | 0.0057106 | 0.0014312
30 | 0.98417 | -0.30292 | 0 | 0
31 | 0.98411 | -0.30409 | 0.0023959 | 0.00060048
32 | 0.98905 | -0.20864 | 0.008195 | 0.0020539
33 | 0.99294 | -0.13396 | 0.0083858 | 0.0021017
34 | 0.9799 | -0.38558 | 0 | 0
35 | 0.97973 | -0.38884 | 0.0092893 | 0.0023281
36 | 0.98028 | -0.37808 | 0.0049233 | 0.0012339
37 | 0.98711 | -0.24578 | 0.0048551 | 0.0012168
38 | 0.98953 | -0.19913 | 0 | 0
39 | 0.98682 | -0.25114 | 0.0040445 | 0.0010137
40 | 0.97954 | -0.39261 | 0 | 0
41 | 0.9797 | -0.38937 | 0 | 0
42 | 0.97948 | -0.3937 | 0.0038483 | 0.00096447
43 | 0.99519 | -0.091076 | 0 | 0
44 | 0.99483 | -0.097851 | 0 | 0
45 | 0.99548 | -0.085496 | 0.0047983 | 0.0012026
46 | 0.99348 | -0.12377 | 0.0094345 | 0.0023645
47 | 0.9757 | -0.46749 | 0.0055733 | 0.0013968
48 | 0.97576 | -0.46626 | 0.013002 | 0.0032586
49 | 1 | 0 | -0.5689 | -0.14588
50 | 0.99976 | -0.0046395 | 0.0074397 | 0.0018646
51 | 0.99843 | -0.029664 | 0.0049037 | 0.001229
52 | 0.99994 | -0.0011522 | 0.0018144 | 0.00045473
53 | 0.98998 | -0.19038 | 0.0070343 | 0.001763
54 | 0.98875 | -0.21429 | 0.01106 | 0.002772
55 | 0.99296 | -0.13349 | 0.0043851 | 0.001099
56 | 0.99987 | -0.0025196 | 0 | 0
57 | 0.99983 | -0.0032889 | 0.002267 | 0.00056816
58 | 0.9799 | -0.38554 | 0 | 0
59 | 0.97943 | -0.39464 | 0.015137 | 0.0037938
60 | 0.97934 | -0.39646 | 0 | 0
61 | 0.9793 | -0.39732 | 0.0027311 | 0.00068447
62 | 0.9877 | -0.23455 | 0 | 0
63 | 0.98761 | -0.23628 | 0.0039654 | 0.00099383
64 | 0.97258 | -0.52901 | 0 | 0
65 | 0.97303 | -0.52003 | 0.0048871 | 0.0012248
66 | 0.97231 | -0.5344 | 0.017777 | 0.0044553
67 | 0.97658 | -0.45128 | 0.0023949 | 0.00060023
68 | 0.9782 | -0.41939 | 0.0025192 | 0.00063137
69 | 0.98396 | -0.30707 | 0.0036448 | 0.00091347
70 | 0.98338 | -0.31832 | 0.0029856 | 0.00074825
71 | 0.97118 | -0.55664 | 0 | 0
72 | 0.97165 | -0.54726 | 0 | 0
73 | 0.97092 | -0.56181 | 0.01354 | 0.0033934
74 | 0.98395 | -0.3071 | 0.0037576 | 0.00094175
75 | 0.98198 | -0.34545 | 0.0025841 | 0.00064763
76 | 0.98032 | -0.37719 | 0.0083287 | 0.0020874
77 | 0.98702 | -0.24736 | 0.0049737 | 0.0012465
78 | 0.98616 | -0.26389 | 0.0041626 | 0.0010433
79 | 0.98612 | -0.265 | 0.0093364 | 0.0023399
80 | 0.98637 | -0.26007 | 0.0040862 | 0.0010241
81 | 0.99345 | -0.12449 | 0.0068918 | 0.0017272
82 | 0.97562 | -0.46905 | 0.0048349 | 0.0012117
83 | 0.97385 | -0.50394 | 0.0019586 | 0.00049088
84 | 0.99171 | -0.15729 | 0.004202 | 0.0010531
85 | 0.97438 | -0.49366 | 0.013575 | 0.0034022
86 | 0.97563 | -0.46903 | 0.0025278 | 0.00063352
87 | 0.97566 | -0.46837 | 0.013244 | 0.0033193
88 | 0.97555 | -0.47061 | 0 | 0
89 | 0.97515 | -0.47853 | 0 | 0
90 | 0.97528 | -0.47594 | 0.011141 | 0.0027922
91 | 0.97954 | -0.39236 | 0 | 0
92 | 0.9998 | -0.003792 | 0.0019247 | 0.00048236
93 | 0.98066 | -0.37062 | 0.0058133 | 0.001457
94 | 0.97721 | -0.43803 | 0.0051132 | 0.0012815
95 | 0.97734 | -0.43542 | 0.0037132 | 0.00093062
96 | 0.97134 | -0.55339 | 0.0048656 | 0.0012194
97 | 0.97142 | -0.55191 | 0.0064874 | 0.0016259
98 | 0.97342 | -0.5124 | 0.0054637 | 0.0013693
99 | 0.97203 | -0.5399 | 0.011989 | 0.0030047
100 | 0.97889 | -0.40591 | 0.0032284 | 0.00080912
101 | 0.97894 | -0.40486 | 0.002583 | 0.00064737
102 | 0.97949 | -0.39405 | 0 | 0
103 | 0.97992 | -0.38575 | 0.0025173 | 0.00063091
104 | 0.97913 | -0.40126 | 0.019802 | 0.0049629
105 | 0.97992 | -0.3856 | 0.0024252 | 0.00060782
106 | 0.98065 | -0.37141 | 0.0022582 | 0.00056597
107 | 0.98105 | -0.36355 | 0.0021988 | 0.00055108
108 | 0.98536 | -0.27926 | 0.0040195 | 0.0010074
109 | 0.98503 | -0.28572 | 0.002995 | 0.00075063
110 | 0.9846 | -0.29403 | 0.0032896 | 0.00082445
111 | 0.98372 | -0.31104 | 0.0015312 | 0.00038374
112 | 0.98225 | -0.33961 | 0.0061313 | 0.0015367
113 | 0.97328 | -0.51522 | 0.0074693 | 0.001872
114 | 0.97261 | -0.5283 | 0.0019401 | 0.00048624
115 | 0.98223 | -0.34003 | 0.010057 | 0.0025205
116 | 0.98118 | -0.36032 | 0 | 0
117 | 0.98037 | -0.37608 | 0.01111 | 0.0027844
118 | 0.97957 | -0.39182 | 0.0027413 | 0.00068703
119 | 0.97495 | -0.48244 | 0.012669 | 0.0031752
120 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.017005 | 0.0042651 | -0.016995 | -0.0042592 | 9.9659e-06 | 5.8842e-06 | 0.025924 | 0.025924 | 0.025924 | 0.9761 | -0.46055 | 0.97548 | -0.47285 | 7.122
1 | -0.033652 | -0.0084374 | 0.033663 | 0.0084441 | 1.0687e-05 | 6.7042e-06 | 0.051302 | 0.051302 | 0.051302 | 0.9761 | -0.46055 | 0.97644 | -0.45389 | 14.0939
2 | -0.033663 | -0.0084441 | 0.033672 | 0.0084498 | 9.0237e-06 | 5.6608e-06 | 0.051302 | 0.051302 | 0.051302 | 0.97644 | -0.45389 | 0.97673 | -0.44827 | 14.0939
3 | 0.004523 | 0.0011333 | -0.0045224 | -0.0011334 | 6.197e-07 | -3.8926e-08 | 0.0068906 | 0.0068907 | 0.0068907 | 0.97673 | -0.44827 | 0.97658 | -0.45114 | 1.8931
4 | -0.038195 | -0.0095831 | 0.038221 | 0.0095999 | 2.6597e-05 | 1.676e-05 | 0.058192 | 0.058192 | 0.058192 | 0.97673 | -0.44827 | 0.97747 | -0.43367 | 15.9869
5 | 0.002395 | 0.0006002 | -0.0023949 | -0.00060023 | 1.5593e-08 | -2.9089e-08 | 0.0036492 | 0.0036492 | 0.0036492 | 0.97658 | -0.45114 | 0.97658 | -0.45128 | 1.0025
6 | -0.042518 | -0.010677 | 0.042547 | 0.010695 | 2.8992e-05 | 1.8324e-05 | 0.064732 | 0.064732 | 0.064732 | 0.97747 | -0.43367 | 0.9782 | -0.41939 | 17.7836
7 | -0.026673 | -0.0066876 | 0.026682 | 0.006693 | 8.7055e-06 | 5.3867e-06 | 0.040147 | 0.040147 | 0.040147 | 0.98865 | -0.21622 | 0.989 | -0.20937 | 11.0294
8 | 0.026673 | 0.0066876 | -0.026666 | -0.0066832 | 7.1005e-06 | 4.3937e-06 | 0.040147 | 0.040147 | 0.040147 | 0.98865 | -0.21622 | 0.98836 | -0.22181 | 11.0294
9 | 0.011063 | 0.0027733 | -0.01106 | -0.002772 | 2.5896e-06 | 1.3376e-06 | 0.016645 | 0.016645 | 0.016645 | 0.989 | -0.20937 | 0.98875 | -0.21429 | 4.5729
10 | -0.037745 | -0.0094663 | 0.037763 | 0.0094779 | 1.844e-05 | 1.1606e-05 | 0.056792 | 0.056792 | 0.056792 | 0.989 | -0.20937 | 0.98953 | -0.19913 | 15.6023
11 | 0.016337 | 0.0040979 | -0.016333 | -0.0040956 | 3.9522e-06 | 2.3009e-06 | 0.024453 | 0.024453 | 0.024453 | 0.99418 | -0.11032 | 0.99392 | -0.1154 | 6.7179
12 | -0.028857 | -0.007236 | 0.028865 | 0.0072409 | 7.9085e-06 | 4.9148e-06 | 0.043193 | 0.043193 | 0.043193 | 0.99418 | -0.11032 | 0.99448 | -0.10457 | 11.8661
13 | 0.01252 | 0.003138 | -0.01252 | -0.0031377 | 5.8409e-07 | 3.1631e-07 | 0.01874 | 0.01874 | 0.01874 | 0.99418 | -0.11032 | 0.99413 | -0.1113 | 5.1482
14 | 0.016333 | 0.0040956 | -0.016326 | -0.0040918 | 6.5199e-06 | 3.796e-06 | 0.024453 | 0.024453 | 0.024453 | 0.99392 | -0.1154 | 0.99348 | -0.12377 | 6.718
15 | 0.36716 | 0.093988 | -0.36664 | -0.093661 | 0.00051335 | 0.00032708 | 0.55007 | 0.55007 | 0.55007 | 0.99448 | -0.10457 | 0.99296 | -0.13349 | 30.2237
16 | -0.39602 | -0.10123 | 0.39628 | 0.10139 | 0.00025869 | 0.00016493 | 0.59326 | 0.59326 | 0.59326 | 0.99448 | -0.10457 | 0.99519 | -0.091076 | 32.5969
17 | 0.016483 | 0.0041357 | -0.016474 | -0.0041306 | 8.6966e-06 | 5.0856e-06 | 0.024844 | 0.024844 | 0.024844 | 0.98729 | -0.24215 | 0.98672 | -0.25322 | 6.8253
18 | -0.016483 | -0.0041357 | 0.016487 | 0.004138 | 3.9573e-06 | 2.314e-06 | 0.024844 | 0.024844 | 0.024844 | 0.98729 | -0.24215 | 0.98755 | -0.23711 | 6.8253
19 | 0.013429 | 0.0033675 | -0.013425 | -0.0033651 | 4.3835e-06 | 2.4415e-06 | 0.020252 | 0.020253 | 0.020253 | 0.98672 | -0.25322 | 0.98637 | -0.26007 | 5.5639
20 | 0.0098332 | 0.0024653 | -0.0098292 | -0.0024633 | 4.0583e-06 | 1.9669e-06 | 0.014817 | 0.014817 | 0.014817 | 0.98755 | -0.23711 | 0.98711 | -0.24578 | 4.0706
21 | -0.31155 | -0.079182 | 0.31212 | 0.079545 | 0.00057105 | 0.00036326 | 0.46983 | 0.46983 | 0.46983 | 0.98755 | -0.23711 | 0.98953 | -0.19913 | 25.815
22 | 0.28523 | 0.072579 | -0.28504 | -0.072456 | 0.00019269 | 0.00012243 | 0.43017 | 0.43017 | 0.43017 | 0.98755 | -0.23711 | 0.98682 | -0.25114 | 23.6359
23 | 0.11392 | 0.028724 | -0.11389 | -0.028706 | 2.9229e-05 | 1.7894e-05 | 0.17342 | 0.17342 | 0.17342 | 0.97782 | -0.42599 | 0.97755 | -0.43135 | 9.5286
24 | -0.18171 | -0.04578 | 0.18189 | 0.045896 | 0.00018457 | 0.0001161 | 0.2766 | 0.2766 | 0.2766 | 0.97782 | -0.42599 | 0.9789 | -0.40477 | 15.1981
25 | 0.06779 | 0.017057 | -0.067667 | -0.016979 | 0.00012247 | 7.7998e-05 | 0.10318 | 0.10318 | 0.10318 | 0.97782 | -0.42599 | 0.97589 | -0.46387 | 28.3474
26 | 0.013673 | 0.0034271 | -0.013673 | -0.003427 | 3.1219e-07 | 1.7571e-07 | 0.020813 | 0.020813 | 0.020813 | 0.97755 | -0.43135 | 0.97752 | -0.43183 | 5.718
27 | 0.10022 | 0.025279 | -0.10006 | -0.025181 | 0.00015354 | 9.7386e-05 | 0.15261 | 0.15261 | 0.15261 | 0.97755 | -0.43135 | 0.97591 | -0.4634 | 20.9625
28 | -0.18303 | -0.046181 | 0.18314 | 0.046249 | 0.00010885 | 6.8486e-05 | 0.27833 | 0.27833 | 0.27833 | 0.9789 | -0.40477 | 0.97954 | -0.39236 | 15.2927
29 | 0.028064 | 0.0070462 | -0.028034 | -0.0070274 | 3.03e-05 | 1.8842e-05 | 0.042796 | 0.042796 | 0.042796 | 0.97589 | -0.46387 | 0.97474 | -0.48653 | 11.7573
30 | 0.039603 | 0.0099325 | -0.039598 | -0.0099295 | 4.6961e-06 | 2.9626e-06 | 0.060388 | 0.060388 | 0.060388 | 0.97589 | -0.46387 | 0.97576 | -0.46636 | 16.5902
31 | 0.01358 | 0.0034048 | -0.013575 | -0.0034022 | 4.6136e-06 | 2.596e-06 | 0.020731 | 0.020731 | 0.020731 | 0.97474 | -0.48653 | 0.97438 | -0.49366 | 5.6953
32 | 0.026353 | 0.0066095 | -0.02635 | -0.0066075 | 3.3536e-06 | 2.0772e-06 | 0.04019 | 0.04019 | 0.04019 | 0.97576 | -0.46636 | 0.97563 | -0.46903 | 11.0411
33 | 0.013245 | 0.00332 | -0.013244 | -0.0033193 | 1.2717e-06 | 7.1008e-07 | 0.020199 | 0.020199 | 0.020199 | 0.97576 | -0.46636 | 0.97566 | -0.46837 | 5.5492
34 | 0.0088285 | 0.0022128 | -0.008827 | -0.0022122 | 1.5123e-06 | 6.8803e-07 | 0.013439 | 0.013439 | 0.013439 | 0.97752 | -0.43183 | 0.97734 | -0.43542 | 3.6921
35 | 0.010411 | 0.0026096 | -0.010409 | -0.0026086 | 2.0262e-06 | 1.0289e-06 | 0.015874 | 0.015874 | 0.015874 | 0.97591 | -0.4634 | 0.9757 | -0.46749 | 4.3609
36 | 0.089652 | 0.022572 | -0.08964 | -0.022564 | 1.2237e-05 | 7.81e-06 | 0.13673 | 0.13673 | 0.13673 | 0.97591 | -0.4634 | 0.97576 | -0.46626 | 37.5641
37 | 0.09605 | 0.024336 | -0.095864 | -0.024218 | 0.0001859 | 0.00011867 | 0.14501 | 0.14501 | 0.14501 | 0.98626 | -0.26233 | 0.98418 | -0.30271 | 39.8377
38 | -0.11803 | -0.02985 | 0.11821 | 0.029961 | 0.00017384 | 0.00011107 | 0.17818 | 0.17818 | 0.17818 | 0.98626 | -0.26233 | 0.98785 | -0.23168 | 48.9495
39 | 0.021982 | 0.0055133 | -0.021971 | -0.0055065 | 1.1152e-05 | 6.7923e-06 | 0.033167 | 0.033167 | 0.033167 | 0.98626 | -0.26233 | 0.98572 | -0.27298 | 9.1118
40 | 0.007404 | 0.0018558 | -0.0074024 | -0.0018552 | 1.5373e-06 | 5.6826e-07 | 0.011194 | 0.011195 | 0.011195 | 0.98418 | -0.30271 | 0.98396 | -0.30707 | 3.0754
41 | 0.086064 | 0.021762 | -0.086 | -0.021721 | 6.4391e-05 | 4.1082e-05 | 0.13019 | 0.13019 | 0.13019 | 0.98418 | -0.30271 | 0.98338 | -0.31832 | 35.7671
42 | 0.0023961 | 0.00060017 | -0.0023961 | -0.00060022 | 2.3898e-08 | -4.6412e-08 | 0.0036226 | 0.0036226 | 0.0036226 | 0.98418 | -0.30271 | 0.98417 | -0.30292 | 0.99523
43 | -0.12788 | -0.032386 | 0.12804 | 0.032485 | 0.00015443 | 9.8694e-05 | 0.19275 | 0.19275 | 0.19275 | 0.98785 | -0.23168 | 0.98915 | -0.20657 | 52.9542
44 | 0.0096774 | 0.0024253 | -0.0096765 | -0.0024249 | 9.0461e-07 | 4.3363e-07 | 0.014577 | 0.014577 | 0.014577 | 0.98785 | -0.23168 | 0.98775 | -0.23364 | 4.0048
45 | 0.0081958 | 0.0020542 | -0.008195 | -0.0020539 | 8.106e-07 | 3.3627e-07 | 0.012329 | 0.012329 | 0.012329 | 0.98915 | -0.20657 | 0.98905 | -0.20864 | 3.3872
46 | -0.13623 | -0.034539 | 0.13671 | 0.034844 | 0.00047724 | 0.00030505 | 0.20508 | 0.20508 | 0.20508 | 0.98915 | -0.20657 | 0.99294 | -0.13396 | 56.3413
47 | 0.0039659 | 0.00099367 | -0.0039658 | -0.00099373 | 1.7178e-07 | -5.4319e-08 | 0.0059745 | 0.0059745 | 0.0059745 | 0.98775 | -0.23364 | 0.9877 | -0.23455 | 1.6413
48 | 0.0023961 | 0.00060022 | -0.0023959 | -0.00060048 | 1.3439e-07 | -2.6097e-07 | 0.0036226 | 0.0036228 | 0.0036228 | 0.98417 | -0.30292 | 0.98411 | -0.30409 | 0.99527
49 | -0.1451 | -0.036946 | 0.14535 | 0.037107 | 0.00025314 | 0.00016127 | 0.21765 | 0.21765 | 0.21765 | 0.99294 | -0.13396 | 0.99483 | -0.097851 | 29.8969
50 | 0.0092907 | 0.0023288 | -0.0092893 | -0.0023281 | 1.4445e-06 | 6.8072e-07 | 0.014109 | 0.014109 | 0.014109 | 0.9799 | -0.38558 | 0.97973 | -0.38884 | 3.876
51 | -0.0092907 | -0.0023288 | 0.0092941 | 0.0023304 | 3.3207e-06 | 1.5646e-06 | 0.014109 | 0.014108 | 0.014109 | 0.9799 | -0.38558 | 0.98028 | -0.37808 | 3.876
52 | -0.014217 | -0.0035643 | 0.014218 | 0.0035646 | 6.0342e-07 | 3.4263e-07 | 0.021582 | 0.021582 | 0.021582 | 0.98028 | -0.37808 | 0.98032 | -0.37719 | 5.929
53 | 0.0049741 | 0.0012465 | -0.0049737 | -0.0012465 | 3.7378e-07 | 1.2613e-08 | 0.0074982 | 0.0074983 | 0.0074983 | 0.98711 | -0.24578 | 0.98702 | -0.24736 | 2.06
54 | -0.34989 | -0.089023 | 0.35003 | 0.089117 | 0.00014762 | 9.402e-05 | 0.52662 | 0.52662 | 0.52662 | 0.98953 | -0.19913 | 0.98998 | -0.19038 | 28.9354
55 | 0.281 | 0.071443 | -0.28082 | -0.071333 | 0.00017244 | 0.00010955 | 0.42407 | 0.42407 | 0.42407 | 0.98682 | -0.25114 | 0.98616 | -0.26389 | 23.3008
56 | -0.0038485 | -0.0009644 | 0.0038491 | 0.0009642 | 5.9455e-07 | -2.0354e-07 | 0.0058462 | 0.005846 | 0.0058462 | 0.97954 | -0.39261 | 0.9797 | -0.38937 | 1.6061
57 | 0.0038485 | 0.0009644 | -0.0038483 | -0.00096447 | 1.9889e-07 | -6.8037e-08 | 0.0058462 | 0.0058462 | 0.0058462 | 0.97954 | -0.39261 | 0.97948 | -0.3937 | 1.6061
58 | -0.021722 | -0.0054446 | 0.021726 | 0.005447 | 3.966e-06 | 2.4159e-06 | 0.032993 | 0.032993 | 0.032993 | 0.9797 | -0.38937 | 0.9799 | -0.38554 | 9.064
59 | 0.017873 | 0.0044804 | -0.017869 | -0.0044778 | 4.4836e-06 | 2.6653e-06 | 0.027147 | 0.027147 | 0.027147 | 0.9797 | -0.38937 | 0.97943 | -0.39464 | 7.458
60 | 0.1454 | 0.037137 | -0.14535 | -0.037107 | 4.7602e-05 | 2.9595e-05 | 0.21765 | 0.21765 | 0.21765 | 0.99519 | -0.091076 | 0.99483 | -0.097851 | 11.9587
61 | -0.54168 | -0.13853 | 0.54182 | 0.13862 | 0.00014633 | 9.3459e-05 | 0.81091 | 0.81091 | 0.81091 | 0.99519 | -0.091076 | 0.99548 | -0.085496 | 44.5556
62 | -0.54662 | -0.13983 | 0.5481 | 0.14077 | 0.0014815 | 0.00094622 | 0.81808 | 0.81808 | 0.81808 | 0.99548 | -0.085496 | 0.99843 | -0.029664 | 44.9497
63 | 0.006892 | 0.0017273 | -0.0068918 | -0.0017272 | 2.3338e-07 | 7.374e-08 | 0.010323 | 0.010323 | 0.010323 | 0.99348 | -0.12377 | 0.99345 | -0.12449 | 2.8359
64 | 0.0048352 | 0.0012117 | -0.0048349 | -0.0012117 | 3.5877e-07 | 9.8891e-09 | 0.0073741 | 0.0073741 | 0.0073741 | 0.9757 | -0.46749 | 0.97562 | -0.46905 | 2.0259
65 | 0.076638 | 0.019305 | -0.0765 | -0.019217 | 0.00013782 | 8.7867e-05 | 0.11691 | 0.11691 | 0.11691 | 0.97576 | -0.46626 | 0.97385 | -0.50394 | 32.1169
66 | 0.0074413 | 0.0018651 | -0.0074397 | -0.0018646 | 1.6446e-06 | 5.8338e-07 | 0.011073 | 0.011073 | 0.011073 | 1 | 0 | 0.99976 | -0.0046395 | 3.042
67 | 0.55381 | 0.14251 | -0.55301 | -0.142 | 0.00079764 | 0.00050947 | 0.82539 | 0.82539 | 0.82539 | 1 | 0 | 0.99843 | -0.029664 | 45.3512
68 | 0.0060068 | 0.001505 | -0.0060065 | -0.001505 | 3.2963e-07 | 6.6624e-08 | 0.0089381 | 0.0089382 | 0.0089382 | 1 | 0 | 0.99994 | -0.0011522 | 2.4555
69 | 0.0041921 | 0.0010502 | -0.0041918 | -0.0010503 | 2.7302e-07 | -7.0666e-08 | 0.0062381 | 0.0062382 | 0.0062382 | 0.99994 | -0.0011522 | 0.99987 | -0.0025196 | 1.7138
70 | -0.35707 | -0.09088 | 0.35764 | 0.091244 | 0.0005706 | 0.00036349 | 0.5372 | 0.5372 | 0.5372 | 0.98998 | -0.19038 | 0.99171 | -0.15729 | 29.5163
71 | 0.36226 | 0.092562 | -0.36184 | -0.092297 | 0.00041644 | 0.00026531 | 0.5435 | 0.5435 | 0.5435 | 0.99296 | -0.13349 | 0.99171 | -0.15729 | 29.8627
72 | 0.0041918 | 0.0010503 | -0.0041917 | -0.0010504 | 1.5359e-07 | -3.9736e-08 | 0.0062382 | 0.0062383 | 0.0062383 | 0.99987 | -0.0025196 | 0.99983 | -0.0032889 | 1.7138
73 | 0.0019247 | 0.0004822 | -0.0019247 | -0.00048236 | 4.6124e-08 | -1.6707e-07 | 0.0028644 | 0.0028645 | 0.0028645 | 0.99983 | -0.0032889 | 0.9998 | -0.003792 | 0.78695
74 | -0.021726 | -0.005447 | 0.021742 | 0.0054565 | 1.5452e-05 | 9.4118e-06 | 0.032993 | 0.032993 | 0.032993 | 0.9799 | -0.38554 | 0.98066 | -0.37062 | 9.064
75 | 0.0027314 | 0.00068401 | -0.0027312 | -0.00068432 | 2.3742e-07 | -3.1074e-07 | 0.0041495 | 0.0041497 | 0.0041497 | 0.97943 | -0.39464 | 0.97934 | -0.39646 | 1.14
76 | 0.0027312 | 0.00068432 | -0.0027311 | -0.00068447 | 1.1169e-07 | -1.4614e-07 | 0.0041497 | 0.0041498 | 0.0041498 | 0.97934 | -0.39646 | 0.9793 | -0.39732 | 1.14
77 | 0.0039658 | 0.00099373 | -0.0039654 | -0.00099383 | 3.2699e-07 | -1.0335e-07 | 0.0059745 | 0.0059746 | 0.0059746 | 0.9877 | -0.23455 | 0.98761 | -0.23628 | 1.6414
78 | -0.017781 | -0.004458 | 0.017789 | 0.0044625 | 7.6091e-06 | 4.5294e-06 | 0.027206 | 0.027205 | 0.027206 | 0.97258 | -0.52901 | 0.97303 | -0.52003 | 7.474
79 | 0.017781 | 0.004458 | -0.017777 | -0.0044553 | 4.5712e-06 | 2.7212e-06 | 0.027206 | 0.027206 | 0.027206 | 0.97258 | -0.52901 | 0.97231 | -0.5344 | 7.4741
80 | -0.022676 | -0.0056874 | 0.022684 | 0.0056924 | 8.2498e-06 | 5.0525e-06 | 0.034679 | 0.034679 | 0.034679 | 0.97303 | -0.52003 | 0.97342 | -0.5124 | 9.5272
81 | -0.045066 | -0.011326 | 0.045095 | 0.011345 | 2.9023e-05 | 1.8368e-05 | 0.068564 | 0.068564 | 0.068564 | 0.9782 | -0.41939 | 0.97889 | -0.40591 | 18.8364
82 | 0.0037577 | 0.00094175 | -0.0037576 | -0.00094175 | 6.4531e-09 | -2.6387e-09 | 0.0056826 | 0.0056826 | 0.0056826 | 0.98396 | -0.30707 | 0.98395 | -0.3071 | 1.5612
83 | 0.083014 | 0.020972 | -0.082906 | -0.020904 | 0.00010782 | 6.8775e-05 | 0.12567 | 0.12567 | 0.12567 | 0.98338 | -0.31832 | 0.98198 | -0.34545 | 34.526
84 | -0.013543 | -0.0033953 | 0.013549 | 0.0033987 | 6.0507e-06 | 3.4085e-06 | 0.020751 | 0.020751 | 0.020751 | 0.97118 | -0.55664 | 0.97165 | -0.54726 | 5.7008
85 | 0.013543 | 0.0033953 | -0.01354 | -0.0033934 | 3.3402e-06 | 1.8819e-06 | 0.020751 | 0.020751 | 0.020751 | 0.97118 | -0.55664 | 0.97092 | -0.56181 | 5.7008
86 | 0.011356 | 0.0028467 | -0.011353 | -0.0028453 | 2.5129e-06 | 1.3339e-06 | 0.017391 | 0.017391 | 0.017391 | 0.97165 | -0.54726 | 0.97142 | -0.55191 | 4.7777
87 | -0.024905 | -0.0062454 | 0.024914 | 0.0062508 | 8.7394e-06 | 5.3947e-06 | 0.038142 | 0.038141 | 0.038142 | 0.97165 | -0.54726 | 0.97203 | -0.5399 | 10.4784
88 | 0.080322 | 0.020256 | -0.080253 | -0.020212 | 6.9513e-05 | 4.433e-05 | 0.12176 | 0.12176 | 0.12176 | 0.98198 | -0.34545 | 0.98105 | -0.36355 | 33.4503
89 | -0.022547 | -0.005652 | 0.022565 | 0.005663 | 1.814e-05 | 1.1088e-05 | 0.034224 | 0.034223 | 0.034224 | 0.98032 | -0.37719 | 0.98118 | -0.36032 | 9.4021
90 | 0.27666 | 0.07029 | -0.27646 | -0.07016 | 0.00020451 | 0.00012989 | 0.41779 | 0.41779 | 0.41779 | 0.98616 | -0.26389 | 0.98536 | -0.27926 | 22.9557
91 | -0.0093364 | -0.0023399 | 0.0093386 | 0.002341 | 2.1936e-06 | 1.0278e-06 | 0.014088 | 0.014088 | 0.014088 | 0.98612 | -0.265 | 0.98637 | -0.26007 | 3.8704
92 | 0.046382 | 0.011658 | -0.046357 | -0.011642 | 2.4975e-05 | 1.5819e-05 | 0.070882 | 0.070882 | 0.070882 | 0.97385 | -0.50394 | 0.97328 | -0.51522 | 19.4731
93 | 0.028159 | 0.0070688 | -0.028148 | -0.0070617 | 1.1367e-05 | 7.0712e-06 | 0.043031 | 0.043031 | 0.043031 | 0.97385 | -0.50394 | 0.97342 | -0.5124 | 11.8217
94 | 0.023822 | 0.0059739 | -0.02382 | -0.0059728 | 1.8003e-06 | 1.1068e-06 | 0.036334 | 0.036334 | 0.036334 | 0.97563 | -0.46903 | 0.97555 | -0.47061 | 9.982
95 | 0.012676 | 0.0031791 | -0.012671 | -0.0031765 | 4.7795e-06 | 2.6334e-06 | 0.019336 | 0.019336 | 0.019336 | 0.97555 | -0.47061 | 0.97515 | -0.47853 | 5.3121
96 | 0.011144 | 0.0027937 | -0.011141 | -0.0027922 | 2.8275e-06 | 1.4839e-06 | 0.016998 | 0.016998 | 0.016998 | 0.97555 | -0.47061 | 0.97528 | -0.47594 | 4.6699
97 | 0.012671 | 0.0031765 | -0.012669 | -0.0031752 | 2.359e-06 | 1.2999e-06 | 0.019336 | 0.019336 | 0.019336 | 0.97515 | -0.47853 | 0.97495 | -0.48244 | 5.3121
98 | -0.18314 | -0.046249 | 0.18314 | 0.046252 | 4.8004e-06 | 3.0202e-06 | 0.27833 | 0.27833 | 0.27833 | 0.97954 | -0.39236 | 0.97957 | -0.39182 | 15.2927
99 | -0.027555 | -0.0069134 | 0.027569 | 0.0069218 | 1.3549e-05 | 8.4107e-06 | 0.041814 | 0.041813 | 0.041814 | 0.98066 | -0.37062 | 0.98118 | -0.36032 | 11.4872
100 | -0.0051132 | -0.0012815 | 0.0051138 | 0.0012815 | 6.3517e-07 | 5.6416e-08 | 0.007786 | 0.0077858 | 0.007786 | 0.97721 | -0.43803 | 0.97734 | -0.43542 | 2.139
101 | -0.0048656 | -0.0012194 | 0.0048659 | 0.0012194 | 3.4278e-07 | 1.5701e-08 | 0.0074536 | 0.0074535 | 0.0074536 | 0.97134 | -0.55339 | 0.97142 | -0.55191 | 2.0477
102 | -0.036903 | -0.0092554 | 0.036923 | 0.0092683 | 2.0421e-05 | 1.2858e-05 | 0.056494 | 0.056494 | 0.056494 | 0.97203 | -0.5399 | 0.97261 | -0.5283 | 15.5204
103 | -0.048323 | -0.012154 | 0.048326 | 0.012155 | 2.4281e-06 | 1.5389e-06 | 0.073472 | 0.073472 | 0.073472 | 0.97889 | -0.40591 | 0.97894 | -0.40486 | 20.1846
104 | -0.050909 | -0.012803 | 0.050935 | 0.012819 | 2.6311e-05 | 1.6692e-05 | 0.077398 | 0.077398 | 0.077398 | 0.97894 | -0.40486 | 0.97949 | -0.39405 | 21.2632
105 | -0.070744 | -0.017786 | 0.070772 | 0.017804 | 2.803e-05 | 1.7858e-05 | 0.10749 | 0.10749 | 0.10749 | 0.97949 | -0.39405 | 0.97992 | -0.38575 | 29.5308
106 | 0.019809 | 0.004967 | -0.019802 | -0.0049629 | 6.8111e-06 | 4.1068e-06 | 0.030094 | 0.030094 | 0.030094 | 0.97949 | -0.39405 | 0.97913 | -0.40126 | 8.2676
107 | -0.073289 | -0.018435 | 0.07329 | 0.018435 | 5.2463e-07 | 3.3434e-07 | 0.11131 | 0.11131 | 0.11131 | 0.97992 | -0.38575 | 0.97992 | -0.3856 | 30.581
108 | -0.075715 | -0.019043 | 0.075766 | 0.019076 | 5.1376e-05 | 3.275e-05 | 0.115 | 0.115 | 0.115 | 0.97992 | -0.3856 | 0.98065 | -0.37141 | 31.5927
109 | -0.078025 | -0.019642 | 0.078054 | 0.019661 | 2.9315e-05 | 1.8691e-05 | 0.11842 | 0.11842 | 0.11842 | 0.98065 | -0.37141 | 0.98105 | -0.36355 | 32.5341
110 | 0.27244 | 0.069153 | -0.27235 | -0.069099 | 8.4748e-05 | 5.3814e-05 | 0.41172 | 0.41172 | 0.41172 | 0.98536 | -0.27926 | 0.98503 | -0.28572 | 22.6222
111 | 0.26936 | 0.068348 | -0.26925 | -0.06828 | 0.00010759 | 6.8307e-05 | 0.4072 | 0.4072 | 0.4072 | 0.98503 | -0.28572 | 0.9846 | -0.29403 | 22.3736
112 | 0.26596 | 0.067455 | -0.26574 | -0.067318 | 0.00021723 | 0.00013789 | 0.40223 | 0.40223 | 0.40223 | 0.9846 | -0.29403 | 0.98372 | -0.31104 | 22.1005
113 | 0.26421 | 0.066934 | -0.26385 | -0.066704 | 0.00036214 | 0.00022986 | 0.39991 | 0.39991 | 0.39991 | 0.98372 | -0.31104 | 0.98225 | -0.33961 | 21.9733
114 | 0.25772 | 0.065167 | -0.25771 | -0.065164 | 5.1143e-06 | 3.2448e-06 | 0.39063 | 0.39063 | 0.39063 | 0.98225 | -0.33961 | 0.98223 | -0.34003 | 21.4629
115 | 0.038887 | 0.0097698 | -0.038863 | -0.0097545 | 2.4265e-05 | 1.5302e-05 | 0.059462 | 0.059463 | 0.059463 | 0.97328 | -0.51522 | 0.97261 | -0.5283 | 16.3359
116 | 0.24766 | 0.062644 | -0.24741 | -0.062491 | 0.00024082 | 0.00015268 | 0.37539 | 0.37539 | 0.37539 | 0.98223 | -0.34003 | 0.98118 | -0.36032 | 20.6258
117 | 0.19728 | 0.049906 | -0.19713 | -0.049812 | 0.00014912 | 9.4036e-05 | 0.29935 | 0.29935 | 0.29935 | 0.98118 | -0.36032 | 0.98037 | -0.37608 | 16.448
118 | 0.18602 | 0.047028 | -0.18588 | -0.046939 | 0.00014024 | 8.8278e-05 | 0.28249 | 0.28249 | 0.28249 | 0.98037 | -0.37608 | 0.97957 | -0.39182 | 15.5215

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.5689 | 0.14588

## res_load
| p_mw | q_mvar
0 | 0.016648 | 0.0041723
1 | 0.016995 | 0.0042592
2 | 0.0021274 | 0.00053318
3 | 0.0042962 | 0.0010767
4 | 0.026666 | 0.0066832
5 | 0.01252 | 0.0031377
6 | 0.0030448 | 0.00076311
7 | 0.0011342 | 0.00028425
8 | 0.014454 | 0.0036226
9 | 0.0048444 | 0.0012141
10 | 0.021971 | 0.0055065
11 | 0.0057106 | 0.0014312
12 | 0.0023959 | 0.00060048
13 | 0.008195 | 0.0020539
14 | 0.0083858 | 0.0021017
15 | 0.0092893 | 0.0023281
16 | 0.0049233 | 0.0012339
17 | 0.0048551 | 0.0012168
18 | 0.0040445 | 0.0010137
19 | 0.0038483 | 0.00096447
20 | 0.0047983 | 0.0012026
21 | 0.0094345 | 0.0023645
22 | 0.0055733 | 0.0013968
23 | 0.013002 | 0.0032586
24 | 0.0074397 | 0.0018646
25 | 0.0049037 | 0.001229
26 | 0.0018144 | 0.00045473
27 | 0.0070343 | 0.001763
28 | 0.01106 | 0.002772
29 | 0.0043851 | 0.001099
30 | 0.002267 | 0.00056816
31 | 0.015137 | 0.0037938
32 | 0.0027311 | 0.00068447
33 | 0.0039654 | 0.00099383
34 | 0.0048871 | 0.0012248
35 | 0.017777 | 0.0044553
36 | 0.0023949 | 0.00060023
37 | 0.0025192 | 0.00063137
38 | 0.0036448 | 0.00091347
39 | 0.0029856 | 0.00074825
40 | 0.01354 | 0.0033934
41 | 0.0037576 | 0.00094175
42 | 0.0025841 | 0.00064763
43 | 0.0083287 | 0.0020874
44 | 0.0049737 | 0.0012465
45 | 0.0041626 | 0.0010433
46 | 0.0093364 | 0.0023399
47 | 0.0040862 | 0.0010241
48 | 0.0068918 | 0.0017272
49 | 0.0048349 | 0.0012117
50 | 0.0019586 | 0.00049088
51 | 0.004202 | 0.0010531
52 | 0.013575 | 0.0034022
53 | 0.0025278 | 0.00063352
54 | 0.013244 | 0.0033193
55 | 0.011141 | 0.0027922
56 | 0.0019247 | 0.00048236
57 | 0.0058133 | 0.001457
58 | 0.0051132 | 0.0012815
59 | 0.0037132 | 0.00093062
60 | 0.0048656 | 0.0012194
61 | 0.0064874 | 0.0016259
62 | 0.0054637 | 0.0013693
63 | 0.011989 | 0.0030047
64 | 0.0032284 | 0.00080912
65 | 0.002583 | 0.00064737
66 | 0.0025173 | 0.00063091
67 | 0.019802 | 0.0049629
68 | 0.0024252 | 0.00060782
69 | 0.0022582 | 0.00056597
70 | 0.0021988 | 0.00055108
71 | 0.0040195 | 0.0010074
72 | 0.002995 | 0.00075063
73 | 0.0032896 | 0.00082445
74 | 0.0015312 | 0.00038374
75 | 0.0061313 | 0.0015367
76 | 0.0074693 | 0.001872
77 | 0.0019401 | 0.00048624
78 | 0.010057 | 0.0025205
79 | 0.01111 | 0.0027844
80 | 0.0027413 | 0.00068703
81 | 0.012669 | 0.0031752

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1