## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-656_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-656_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-656_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_261-656_0_5_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_261-656_0_5_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_261-656_0_5_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_261-656_0_5_node_30 | 0.4 | n |  | TRUE
7 | bus_LV_261-656_0_5_node_6 | 0.4 | n |  | TRUE
8 | bus_LV_261-656_0_5_node_7 | 0.4 | n |  | TRUE
9 | bus_LV_261-656_0_5_node_29 | 0.4 | n |  | TRUE
10 | bus_LV_261-656_0_5_node_33 | 0.4 | n |  | TRUE
11 | bus_LV_261-656_0_5_node_47 | 0.4 | n |  | TRUE
12 | bus_LV_261-656_0_5_node_44 | 0.4 | n |  | TRUE
13 | bus_LV_261-656_0_5_node_10 | 0.4 | n |  | TRUE
14 | bus_LV_261-656_0_5_node_39 | 0.4 | n |  | TRUE
15 | bus_LV_261-656_0_5_node_37 | 0.4 | n |  | TRUE
16 | bus_LV_261-656_0_5_node_11 | 0.4 | n |  | TRUE
17 | bus_LV_261-656_0_5_node_58 | 0.4 | n |  | TRUE
18 | bus_LV_261-656_0_5_node_63 | 0.4 | n |  | TRUE
19 | bus_LV_261-656_0_5_node_12 | 0.4 | n |  | TRUE
20 | bus_LV_261-656_0_5_node_53 | 0.4 | n |  | TRUE
21 | bus_LV_261-656_0_5_node_13 | 0.4 | n |  | TRUE
22 | bus_LV_261-656_0_5_node_21 | 0.4 | n |  | TRUE
23 | bus_LV_261-656_0_5_node_62 | 0.4 | n |  | TRUE
24 | bus_LV_261-656_0_5_node_15 | 0.4 | n |  | TRUE
25 | bus_LV_261-656_0_5_node_19 | 0.4 | n |  | TRUE
26 | bus_LV_261-656_0_5_node_34 | 0.4 | n |  | TRUE
27 | bus_LV_261-656_0_5_node_55 | 0.4 | n |  | TRUE
28 | bus_LV_261-656_0_5_node_16 | 0.4 | n |  | TRUE
29 | bus_LV_261-656_0_5_node_20 | 0.4 | n |  | TRUE
30 | bus_LV_261-656_0_5_node_18 | 0.4 | n |  | TRUE
31 | bus_LV_261-656_0_5_node_42 | 0.4 | n |  | TRUE
32 | bus_LV_261-656_0_5_node_17 | 0.4 | n |  | TRUE
33 | bus_LV_261-656_0_5_node_25 | 0.4 | n |  | TRUE
34 | bus_LV_261-656_0_5_node_61 | 0.4 | n |  | TRUE
35 | bus_LV_261-656_0_5_node_51 | 0.4 | n |  | TRUE
36 | bus_LV_261-656_0_5_node_48 | 0.4 | n |  | TRUE
37 | bus_LV_261-656_0_5_node_43 | 0.4 | n |  | TRUE
38 | bus_LV_261-656_0_5_node_64 | 0.4 | n |  | TRUE
39 | bus_LV_261-656_0_5_node_40 | 0.4 | n |  | TRUE
40 | bus_LV_261-656_0_5_node_41 | 0.4 | n |  | TRUE
41 | bus_LV_261-656_0_5_node_49 | 0.4 | n |  | TRUE
42 | bus_LV_261-656_0_5_node_27 | 0.4 | n |  | TRUE
43 | bus_LV_261-656_0_5_node_28 | 0.4 | n |  | TRUE
44 | bus_LV_261-656_0_5_node_31 | 0.4 | n |  | TRUE
45 | bus_LV_261-656_0_5_node_45 | 0.4 | n |  | TRUE
46 | bus_LV_261-656_0_5_node_36 | 0.4 | n |  | TRUE
47 | bus_LV_261-656_0_5_node_56 | 0.4 | n |  | TRUE
48 | bus_LV_261-656_0_5_node_52 | 0.4 | n |  | TRUE
49 | bus_LV_261-656_0_5_node_54 | 0.4 | n |  | TRUE
50 | bus_LV_261-656_0_5_node_24 | 0.4 | n |  | TRUE
51 | bus_LV_261-656_0_5_node_60 | 0.4 | n |  | TRUE
52 | bus_LV_261-656_0_5_node_50 | 0.4 | n |  | TRUE
53 | bus_LV_261-656_0_5_node_46 | 0.4 | n |  | TRUE
54 | bus_LV_261-656_0_5_node_35 | 0.4 | n |  | TRUE
55 | bus_LV_261-656_0_5_node_23 | 0.4 | n |  | TRUE
56 | bus_LV_261-656_0_5_node_26 | 0.4 | n |  | TRUE
57 | bus_LV_261-656_0_5_node_32 | 0.4 | n |  | TRUE
58 | bus_LV_261-656_0_5_node_57 | 0.4 | n |  | TRUE
59 | bus_LV_261-656_0_5_node_59 | 0.4 | n |  | TRUE
60 | bus_MV_533_0_node_75 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-656_0_5_load_0 | 0 | 0.0088869 | 0.0022273 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-656_0_5_load_1 | 1 | 0.0083517 | 0.0020931 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-656_0_5_load_4 | 4 | 0.012267 | 0.0030745 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-656_0_5_load_30 | 6 | 0.019455 | 0.0048759 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-656_0_5_load_29 | 9 | 0.017608 | 0.0044129 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-656_0_5_load_33 | 10 | 0.0096221 | 0.0024115 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-656_0_5_load_47 | 11 | 0.0065052 | 0.0016304 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-656_0_5_load_44 | 12 | 0.01038 | 0.0026015 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-656_0_5_load_39 | 14 | 0.0066989 | 0.0016789 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-656_0_5_load_37 | 15 | 0.0095842 | 0.002402 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-656_0_5_load_63 | 18 | 0.007286 | 0.0018261 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-656_0_5_load_53 | 20 | 0.017018 | 0.0042652 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-656_0_5_load_62 | 23 | 0.0075315 | 0.0018876 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-656_0_5_load_34 | 26 | 0.020617 | 0.0051671 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-656_0_5_load_55 | 27 | 0.010531 | 0.0026393 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-656_0_5_load_42 | 31 | 0.021889 | 0.0054859 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-656_0_5_load_25 | 33 | 0.017162 | 0.0043011 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_261-656_0_5_load_61 | 34 | 0.018301 | 0.0045866 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_261-656_0_5_load_51 | 35 | 0.023102 | 0.00579 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_261-656_0_5_load_48 | 36 | 0.013837 | 0.003468 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_261-656_0_5_load_43 | 37 | 0.016414 | 0.0041138 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_261-656_0_5_load_64 | 38 | 0.0085214 | 0.0021357 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_261-656_0_5_load_40 | 39 | 0.0083009 | 0.0020804 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_261-656_0_5_load_41 | 40 | 0.011417 | 0.0028614 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_261-656_0_5_load_49 | 41 | 0.010634 | 0.0026651 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_261-656_0_5_load_27 | 42 | 0.016066 | 0.0040265 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_261-656_0_5_load_28 | 43 | 0.0095395 | 0.0023908 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_261-656_0_5_load_31 | 44 | 0.029688 | 0.0074405 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_261-656_0_5_load_45 | 45 | 0.0071052 | 0.0017807 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_261-656_0_5_load_36 | 46 | 0.0077502 | 0.0019424 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_261-656_0_5_load_56 | 47 | 0.010974 | 0.0027504 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_261-656_0_5_load_52 | 48 | 0.0026727 | 0.00066983 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_261-656_0_5_load_54 | 49 | 0.018876 | 0.0047308 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_261-656_0_5_load_60 | 51 | 0.018104 | 0.0045373 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_261-656_0_5_load_50 | 52 | 0.017353 | 0.0043491 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_261-656_0_5_load_46 | 53 | 0.0077711 | 0.0019476 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_261-656_0_5_load_35 | 54 | 0.014181 | 0.0035542 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_261-656_0_5_load_23 | 55 | 0.011959 | 0.0029972 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_261-656_0_5_load_26 | 56 | 0.0224 | 0.005614 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_261-656_0_5_load_32 | 57 | 0.016255 | 0.0040738 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_261-656_0_5_load_57 | 58 | 0.012223 | 0.0030634 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_261-656_0_5_load_59 | 59 | 0.018065 | 0.0045275 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 27 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-656_0_5_line_0 |  | 0 | 1 | 0.015743 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-656_0_5_line_1 |  | 0 | 2 | 0.020901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-656_0_5_line_2 |  | 1 | 3 | 0.011704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-656_0_5_line_3 |  | 2 | 4 | 0.011042 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-656_0_5_line_4 |  | 3 | 5 | 0.006899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_261-656_0_5_line_5 |  | 5 | 6 | 0.010518 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_261-656_0_5_line_6 |  | 6 | 41 | 0.013149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_261-656_0_5_line_7 |  | 7 | 8 | 0.0076199 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_261-656_0_5_line_8 |  | 7 | 9 | 0.01125 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_261-656_0_5_line_9 |  | 7 | 10 | 0.023563 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_261-656_0_5_line_10 |  | 8 | 11 | 0.023427 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_261-656_0_5_line_11 |  | 8 | 12 | 0.010504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
12 | LV_261-656_0_5_line_12 |  | 9 | 43 | 0.011843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-656_0_5_line_13 |  | 10 | 44 | 0.011013 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_261-656_0_5_line_14 |  | 11 | 14 | 0.01266 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_261-656_0_5_line_15 |  | 12 | 45 | 0.015018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
16 | LV_261-656_0_5_line_16 |  | 13 | 14 | 0.022315 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_261-656_0_5_line_17 |  | 13 | 15 | 0.012128 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_261-656_0_5_line_18 |  | 15 | 46 | 0.015642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_261-656_0_5_line_19 |  | 16 | 17 | 0.005647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_261-656_0_5_line_20 |  | 16 | 18 | 0.06214 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_261-656_0_5_line_21 |  | 17 | 47 | 0.015844 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
22 | LV_261-656_0_5_line_22 |  | 17 | 19 | 0.007943 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
23 | LV_261-656_0_5_line_23 |  | 18 | 23 | 0.016892 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_261-656_0_5_line_24 |  | 19 | 20 | 0.005691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
25 | LV_261-656_0_5_line_25 |  | 20 | 48 | 0.013765 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_261-656_0_5_line_26 |  | 20 | 25 | 0.015206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
27 | LV_261-656_0_5_line_27 |  | 21 | 22 | 0.009007 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_261-656_0_5_line_28 |  | 21 | 23 | 0.021747 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_261-656_0_5_line_29 |  | 22 | 38 | 0.0016828 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_261-656_0_5_line_30 |  | 24 | 25 | 0.0073181 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
31 | LV_261-656_0_5_line_31 |  | 24 | 26 | 0.012985 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_261-656_0_5_line_32 |  | 24 | 27 | 0.021108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
33 | LV_261-656_0_5_line_33 |  | 25 | 36 | 0.021054 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
34 | LV_261-656_0_5_line_34 |  | 27 | 49 | 0.013156 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_261-656_0_5_line_35 |  | 28 | 29 | 0.003406 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_261-656_0_5_line_36 |  | 28 | 30 | 0.0071243 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_261-656_0_5_line_37 |  | 28 | 31 | 0.014073 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_261-656_0_5_line_38 |  | 29 | 37 | 0.020292 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_261-656_0_5_line_39 |  | 30 | 35 | 0.013218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_261-656_0_5_line_40 |  | 30 | 32 | 0.013453 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
41 | LV_261-656_0_5_line_41 |  | 31 | 40 | 0.015399 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_261-656_0_5_line_42 |  | 32 | 33 | 0.0090937 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_261-656_0_5_line_43 |  | 32 | 34 | 0.011157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
44 | LV_261-656_0_5_line_44 |  | 33 | 50 | 0.018579 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_261-656_0_5_line_45 |  | 34 | 51 | 0.016395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
46 | LV_261-656_0_5_line_46 |  | 35 | 52 | 0.018732 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_261-656_0_5_line_47 |  | 36 | 53 | 0.014384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
48 | LV_261-656_0_5_line_48 |  | 39 | 40 | 0.013251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_261-656_0_5_line_49 |  | 41 | 52 | 0.01301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_261-656_0_5_line_50 |  | 42 | 43 | 0.011954 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_261-656_0_5_line_51 |  | 44 | 57 | 0.0017707 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_261-656_0_5_line_52 |  | 45 | 53 | 0.013682 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
53 | LV_261-656_0_5_line_53 |  | 46 | 54 | 0.0071496 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_261-656_0_5_line_54 |  | 47 | 58 | 0.011573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
55 | LV_261-656_0_5_line_55 |  | 50 | 56 | 0.0060135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_261-656_0_5_line_56 |  | 50 | 55 | 0.019226 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_261-656_0_5_line_57 |  | 51 | 59 | 0.016282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
58 | LV_261-656_0_5_line_58 |  | 58 | 59 | 0.013564 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-656_0_5_trafo_55 | 0.63 MVA 20/0.4 kV | 60 | 27 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2681833.3412 | 1246738.3969 | 2681824.2579 | 1246751.2546
1 | 2681844.992 | 1246721.0976 | 2681844.1253 | 1246723.1316 | 2681833.3412 | 1246738.3969
2 | 2681817.5046 | 1246760.8141 | 2681824.2579 | 1246751.2546
3 | 2681844.992 | 1246721.0976 | 2681842.5521 | 1246717.25 | 2681839.4534 | 1246711.5516
4 | 2681817.5046 | 1246760.8141 | 2681815.532 | 1246763.6112 | 2681813.5287 | 1246766.4523
5 | 2681813.5287 | 1246766.4523 | 2681805.3327 | 1246759.8596
6 | 2681805.3327 | 1246759.8596 | 2681795.0873 | 1246751.6183
7 | 2681774.7654 | 1246821.3245 | 2681776.8226 | 1246818.4174 | 2681779.1648 | 1246815.1028
8 | 2681779.1648 | 1246815.1028 | 2681781.0834 | 1246812.3828 | 2681785.654 | 1246805.9126
9 | 2681779.1648 | 1246815.1028 | 2681776.057 | 1246812.5804 | 2681760.8804 | 1246800.24
10 | 2681774.7654 | 1246821.3245 | 2681772.0148 | 1246825.2228 | 2681761.2508 | 1246840.4605
11 | 2681774.7654 | 1246821.3245 | 2681771.6954 | 1246818.8025 | 2681766.6435 | 1246814.6636
12 | 2681792.4868 | 1246796.2398 | 2681785.654 | 1246805.9126
13 | 2681760.8804 | 1246800.24 | 2681752.3359 | 1246793.2923
14 | 2681761.2508 | 1246840.4605 | 2681753.9462 | 1246850.801
15 | 2681766.6435 | 1246814.6636 | 2681755.0267 | 1246805.1462
16 | 2681741.0725 | 1246869.0283 | 2681742.8986 | 1246866.4404 | 2681753.9462 | 1246850.801
17 | 2681741.0725 | 1246869.0283 | 2681738.4355 | 1246866.8793 | 2681731.6625 | 1246861.3765
18 | 2681719.522 | 1246851.5128 | 2681731.6625 | 1246861.3765
19 | 2681696.673 | 1246777.7276 | 2681693.6571 | 1246779.4985 | 2681691.515 | 1246779.8025
20 | 2681691.515 | 1246779.8025 | 2681689.7882 | 1246779.5786 | 2681688.3667 | 1246778.5694 | 2681687.4325 | 1246776.7441 | 2681686.7887 | 1246771.9317 | 2681680.3372 | 1246720.586
21 | 2681696.673 | 1246777.7276 | 2681704.9922 | 1246770.4702 | 2681708.1793 | 1246766.875
22 | 2681703.0282 | 1246782.5186 | 2681702.1161 | 1246781.8278 | 2681697.7422 | 1246778.5318 | 2681696.673 | 1246777.7276
23 | 2681678.2313 | 1246703.8258 | 2681680.3372 | 1246720.586
24 | 2681703.0282 | 1246782.5186 | 2681703.7385 | 1246783.051 | 2681707.1403 | 1246785.622 | 2681707.5815 | 1246785.9505
25 | 2681707.5815 | 1246785.9505 | 2681699.5712 | 1246797.1446
26 | 2681707.5815 | 1246785.9505 | 2681717.0304 | 1246774.0164
27 | 2681681.8822 | 1246676.8168 | 2681679.2762 | 1246677.348 | 2681677.0765 | 1246679.0856 | 2681675.9899 | 1246680.6385 | 2681675.5599 | 1246682.2448
28 | 2681675.5599 | 1246682.2448 | 2681676.0548 | 1246686.8995 | 2681677.1081 | 1246694.8865 | 2681678.2313 | 1246703.8258
29 | 2681681.8822 | 1246676.8168 | 2681683.531 | 1246676.4801
30 | 2681717.0304 | 1246774.0164 | 2681719.0124 | 1246771.6198 | 2681721.6936 | 1246768.3766
31 | 2681721.6936 | 1246768.3766 | 2681731.7686 | 1246776.5687
32 | 2681721.6936 | 1246768.3766 | 2681730.0828 | 1246758.2403 | 2681735.2712 | 1246752.216
33 | 2681717.0304 | 1246774.0164 | 2681733.3166 | 1246787.3594
34 | 2681743.8567 | 1246742.2473 | 2681735.2712 | 1246752.216
35 | 2681766.9341 | 1246715.4614 | 2681764.7077 | 1246718.0437
36 | 2681760.0552 | 1246723.439 | 2681761.7672 | 1246721.4612 | 2681764.7077 | 1246718.0437
37 | 2681764.7077 | 1246718.0437 | 2681775.643 | 1246726.9023
38 | 2681766.9341 | 1246715.4614 | 2681775.6941 | 1246705.2858 | 2681780.1794 | 1246700.0885
39 | 2681760.0552 | 1246723.439 | 2681770.3544 | 1246731.7235
40 | 2681753.2936 | 1246714.7061 | 2681758.2918 | 1246718.7446 | 2681761.7672 | 1246721.4612 | 2681760.0552 | 1246723.439
41 | 2681787.6086 | 1246736.5955 | 2681775.643 | 1246726.9023
42 | 2681753.2936 | 1246714.7061 | 2681750.5525 | 1246712.4334 | 2681746.3636 | 1246708.8185
43 | 2681753.2936 | 1246714.7061 | 2681746.0066 | 1246723.1548
44 | 2681730.4922 | 1246699.5141 | 2681736.4368 | 1246701.7644 | 2681742.1984 | 1246705.2241 | 2681746.3636 | 1246708.8185
45 | 2681735.2987 | 1246735.5696 | 2681746.0066 | 1246723.1548
46 | 2681784.9502 | 1246743.4642 | 2681770.3544 | 1246731.7235
47 | 2681744.4431 | 1246796.4752 | 2681733.3166 | 1246787.3594
48 | 2681797.9052 | 1246744.9368 | 2681787.6086 | 1246736.5955
49 | 2681784.9502 | 1246743.4642 | 2681795.0873 | 1246751.6183
50 | 2681799.3841 | 1246786.4758 | 2681792.4868 | 1246796.2398
51 | 2681750.9621 | 1246792.1752 | 2681752.3359 | 1246793.2923
52 | 2681755.0267 | 1246805.1462 | 2681744.4431 | 1246796.4752
53 | 2681719.522 | 1246851.5128 | 2681713.973 | 1246847.0045
54 | 2681708.1793 | 1246766.875 | 2681712.5585 | 1246761.9349 | 2681715.8053 | 1246758.1705
55 | 2681730.4922 | 1246699.5141 | 2681727.4936 | 1246698.3831 | 2681727.0441 | 1246695.6107
56 | 2681730.4922 | 1246699.5141 | 2681717.9085 | 1246714.0505
57 | 2681724.6642 | 1246747.8994 | 2681735.2987 | 1246735.5696
58 | 2681715.8053 | 1246758.1705 | 2681724.6642 | 1246747.8994

## bus_geodata
| x | y | coords
0 | 2681833.3412 | 1246738.3969
1 | 2681824.2579 | 1246751.2546
2 | 2681844.992 | 1246721.0976
3 | 2681817.5046 | 1246760.8141
4 | 2681839.4534 | 1246711.5516
5 | 2681813.5287 | 1246766.4523
6 | 2681805.3327 | 1246759.8596
7 | 2681779.1648 | 1246815.1028
8 | 2681774.7655 | 1246821.3245
9 | 2681785.654 | 1246805.9126
10 | 2681760.8804 | 1246800.24
11 | 2681761.2508 | 1246840.4605
12 | 2681766.6435 | 1246814.6636
13 | 2681741.0725 | 1246869.0283
14 | 2681753.9462 | 1246850.801
15 | 2681731.6625 | 1246861.3765
16 | 2681691.515 | 1246779.8025
17 | 2681696.673 | 1246777.7276
18 | 2681680.3372 | 1246720.586
19 | 2681703.0282 | 1246782.5186
20 | 2681707.5815 | 1246785.9505
21 | 2681675.5599 | 1246682.2448
22 | 2681681.8822 | 1246676.8168
23 | 2681678.2313 | 1246703.8258
24 | 2681721.6936 | 1246768.3766
25 | 2681717.0304 | 1246774.0164
26 | 2681731.7686 | 1246776.5687
27 | 2681735.2712 | 1246752.216
28 | 2681764.7077 | 1246718.0437
29 | 2681766.9341 | 1246715.4614
30 | 2681760.0552 | 1246723.439
31 | 2681775.643 | 1246726.9023
32 | 2681753.2936 | 1246714.7061
33 | 2681746.3636 | 1246708.8185
34 | 2681746.0066 | 1246723.1548
35 | 2681770.3544 | 1246731.7235
36 | 2681733.3166 | 1246787.3594
37 | 2681780.1794 | 1246700.0885
38 | 2681683.531 | 1246676.4801
39 | 2681797.9052 | 1246744.9368
40 | 2681787.6086 | 1246736.5955
41 | 2681795.0873 | 1246751.6183
42 | 2681799.3841 | 1246786.4758
43 | 2681792.4868 | 1246796.2398
44 | 2681752.3359 | 1246793.2923
45 | 2681755.0267 | 1246805.1462
46 | 2681719.522 | 1246851.5128
47 | 2681708.1793 | 1246766.875
48 | 2681699.5712 | 1246797.1446
49 | 2681743.8567 | 1246742.2473
50 | 2681730.4922 | 1246699.5141
51 | 2681735.2987 | 1246735.5696
52 | 2681784.9502 | 1246743.4642
53 | 2681744.4431 | 1246796.4752
54 | 2681713.973 | 1246847.0045
55 | 2681717.9085 | 1246714.0505
56 | 2681727.0441 | 1246695.6107
57 | 2681750.9621 | 1246792.1752
58 | 2681715.8053 | 1246758.1705
59 | 2681724.6642 | 1246747.8994
60 | 2681721.6936 | 1246768.3766

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98359 | -0.31648 | 0.0088869 | 0.0022273
1 | 0.9839 | -0.31048 | 0.0083517 | 0.0020931
2 | 0.98335 | -0.3211 | 0 | 0
3 | 0.98422 | -0.30426 | 0 | 0
4 | 0.98323 | -0.32354 | 0.012267 | 0.0030745
5 | 0.9844 | -0.3006 | 0 | 0
6 | 0.98469 | -0.29502 | 0.019455 | 0.0048759
7 | 0.99272 | -0.1397 | 0 | 0
8 | 0.99341 | -0.1264 | 0 | 0
9 | 0.99227 | -0.1483 | 0.017608 | 0.0044129
10 | 0.99152 | -0.16288 | 0.0096221 | 0.0024115
11 | 0.99245 | -0.14492 | 0.0065052 | 0.0016304
12 | 0.9941 | -0.11309 | 0.01038 | 0.0026015
13 | 0.99136 | -0.16595 | 0 | 0
14 | 0.992 | -0.15348 | 0.0066989 | 0.0016789
15 | 0.99101 | -0.17273 | 0.0095842 | 0.002402
16 | 0.99432 | -0.10868 | 0 | 0
17 | 0.99444 | -0.10636 | 0 | 0
18 | 0.99299 | -0.13429 | 0.007286 | 0.0018261
19 | 0.995 | -0.095495 | 0 | 0
20 | 0.99541 | -0.087718 | 0.017018 | 0.0042652
21 | 0.99257 | -0.14236 | 0 | 0
22 | 0.9925 | -0.14372 | 0 | 0
23 | 0.99274 | -0.13908 | 0.0075315 | 0.0018876
24 | 0.99742 | -0.0492 | 0 | 0
25 | 0.99656 | -0.065655 | 0 | 0
26 | 0.99718 | -0.053892 | 0.020617 | 0.0051671
27 | 1 | 0 | -0.55883 | -0.14149
28 | 0.98816 | -0.2275 | 0 | 0
29 | 0.98811 | -0.22849 | 0 | 0
30 | 0.98854 | -0.22012 | 0 | 0
31 | 0.98762 | -0.23795 | 0.021889 | 0.0054859
32 | 0.98952 | -0.20117 | 0 | 0
33 | 0.98909 | -0.20952 | 0.017162 | 0.0043011
34 | 0.99006 | -0.19077 | 0.018301 | 0.0045866
35 | 0.98732 | -0.24374 | 0.023102 | 0.00579
36 | 0.99568 | -0.082538 | 0.013837 | 0.003468
37 | 0.98781 | -0.23444 | 0.016414 | 0.0041138
38 | 0.99249 | -0.14397 | 0.0085214 | 0.0021357
39 | 0.98725 | -0.24535 | 0.0083009 | 0.0020804
40 | 0.98735 | -0.24338 | 0.011417 | 0.0028614
41 | 0.98528 | -0.28346 | 0.010634 | 0.0026651
42 | 0.99182 | -0.15707 | 0.016066 | 0.0040265
43 | 0.992 | -0.15367 | 0.0095395 | 0.0023908
44 | 0.99106 | -0.17186 | 0.029688 | 0.0074405
45 | 0.99462 | -0.10291 | 0.0071052 | 0.0017807
46 | 0.9907 | -0.17882 | 0.0077502 | 0.0019424
47 | 0.99339 | -0.12644 | 0.010974 | 0.0027504
48 | 0.99537 | -0.088365 | 0.0026727 | 0.00066983
49 | 0.99977 | -0.0043294 | 0.018876 | 0.0047308
50 | 0.9885 | -0.2209 | 0 | 0
51 | 0.99092 | -0.17418 | 0.018104 | 0.0045373
52 | 0.986 | -0.26954 | 0.017353 | 0.0043491
53 | 0.99513 | -0.093213 | 0.0077711 | 0.0019476
54 | 0.9906 | -0.18062 | 0.014181 | 0.0035542
55 | 0.98829 | -0.225 | 0.011959 | 0.0029972
56 | 0.98838 | -0.2233 | 0.0224 | 0.005614
57 | 0.99103 | -0.17237 | 0.016255 | 0.0040738
58 | 0.99266 | -0.14057 | 0.012223 | 0.0030634
59 | 0.99184 | -0.15642 | 0.018065 | 0.0045275
60 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.021158 | -0.005304 | 0.021165 | 0.0053077 | 6.0488e-06 | 3.6714e-06 | 0.03201 | 0.03201 | 0.03201 | 0.98359 | -0.31648 | 0.9839 | -0.31048 | 8.7939
1 | 0.012272 | 0.0030768 | -0.012269 | -0.0030753 | 2.7016e-06 | 1.4638e-06 | 0.018565 | 0.018566 | 0.018566 | 0.98359 | -0.31648 | 0.98335 | -0.3211 | 5.1004
2 | -0.029516 | -0.0074008 | 0.029525 | 0.0074063 | 8.7466e-06 | 5.4491e-06 | 0.044641 | 0.044641 | 0.044641 | 0.9839 | -0.31048 | 0.98422 | -0.30426 | 12.2639
3 | 0.012269 | 0.0030753 | -0.012267 | -0.0030745 | 1.4273e-06 | 7.7339e-07 | 0.018566 | 0.018566 | 0.018566 | 0.98335 | -0.3211 | 0.98323 | -0.32354 | 5.1004
4 | -0.029525 | -0.0074063 | 0.02953 | 0.0074095 | 5.1556e-06 | 3.2119e-06 | 0.044641 | 0.044641 | 0.044641 | 0.98422 | -0.30426 | 0.9844 | -0.3006 | 12.2639
5 | -0.02953 | -0.0074095 | 0.029538 | 0.0074144 | 7.8603e-06 | 4.8968e-06 | 0.044641 | 0.044641 | 0.044641 | 0.9844 | -0.3006 | 0.98469 | -0.29502 | 12.2639
6 | -0.048993 | -0.01229 | 0.04902 | 0.012307 | 2.703e-05 | 1.7132e-05 | 0.07404 | 0.07404 | 0.07404 | 0.98469 | -0.29502 | 0.98528 | -0.28346 | 20.3407
7 | -0.098886 | -0.024825 | 0.098949 | 0.024865 | 6.2792e-05 | 4.0088e-05 | 0.14824 | 0.14824 | 0.14824 | 0.99272 | -0.1397 | 0.99341 | -0.1264 | 40.7249
8 | 0.04324 | 0.010847 | -0.043222 | -0.010836 | 1.7725e-05 | 1.1199e-05 | 0.064818 | 0.064818 | 0.064818 | 0.99272 | -0.1397 | 0.99227 | -0.1483 | 17.8071
9 | 0.055646 | 0.013978 | -0.055585 | -0.013939 | 6.1492e-05 | 3.905e-05 | 0.083421 | 0.083421 | 0.083421 | 0.99272 | -0.1397 | 0.99152 | -0.16288 | 22.9179
10 | 0.044812 | 0.011265 | -0.044772 | -0.01124 | 3.9597e-05 | 2.5039e-05 | 0.067136 | 0.067136 | 0.067136 | 0.99341 | -0.1264 | 0.99245 | -0.14492 | 18.4439
11 | -0.14376 | -0.03613 | 0.14385 | 0.036188 | 9.1357e-05 | 5.8196e-05 | 0.21537 | 0.21537 | 0.21537 | 0.99341 | -0.1264 | 0.9941 | -0.11309 | 29.5844
12 | 0.025615 | 0.0064229 | -0.025608 | -0.0064189 | 6.553e-06 | 4.041e-06 | 0.038413 | 0.038413 | 0.038413 | 0.99227 | -0.1483 | 0.992 | -0.15367 | 10.553
13 | 0.045963 | 0.011527 | -0.045943 | -0.011515 | 1.9651e-05 | 1.2435e-05 | 0.068981 | 0.068981 | 0.068981 | 0.99152 | -0.16288 | 0.99106 | -0.17186 | 18.9508
14 | 0.038267 | 0.00961 | -0.038251 | -0.0096002 | 1.5632e-05 | 9.8413e-06 | 0.057382 | 0.057382 | 0.057382 | 0.99245 | -0.14492 | 0.992 | -0.15348 | 15.7643
15 | -0.15423 | -0.03879 | 0.15431 | 0.038837 | 7.507e-05 | 4.7266e-05 | 0.23091 | 0.23091 | 0.23091 | 0.9941 | -0.11309 | 0.99462 | -0.10291 | 15.8593
16 | -0.031534 | -0.0079095 | 0.031552 | 0.0079213 | 1.8749e-05 | 1.1711e-05 | 0.047334 | 0.047334 | 0.047334 | 0.99136 | -0.16595 | 0.992 | -0.15348 | 13.0038
17 | 0.031534 | 0.0079095 | -0.031523 | -0.0079032 | 1.019e-05 | 6.3653e-06 | 0.047334 | 0.047334 | 0.047334 | 0.99136 | -0.16595 | 0.99101 | -0.17273 | 13.0038
18 | 0.021939 | 0.0055012 | -0.021933 | -0.0054973 | 6.3659e-06 | 3.8727e-06 | 0.032943 | 0.032943 | 0.032943 | 0.99101 | -0.17273 | 0.9907 | -0.17882 | 9.0503
19 | -0.023373 | -0.0058697 | 0.023376 | 0.0058713 | 2.5915e-06 | 1.5853e-06 | 0.034982 | 0.034982 | 0.034982 | 0.99432 | -0.10868 | 0.99444 | -0.10636 | 9.6106
20 | 0.023373 | 0.0058697 | -0.023345 | -0.0058523 | 2.8517e-05 | 1.7446e-05 | 0.034982 | 0.034983 | 0.034983 | 0.99432 | -0.10868 | 0.99299 | -0.13429 | 9.6107
21 | 0.28897 | 0.07308 | -0.28869 | -0.072903 | 0.00027802 | 0.00017711 | 0.43263 | 0.43263 | 0.43263 | 0.99444 | -0.10636 | 0.99339 | -0.12644 | 29.7135
22 | -0.31234 | -0.078951 | 0.31251 | 0.079055 | 0.00016283 | 0.0001038 | 0.46761 | 0.46761 | 0.46761 | 0.99444 | -0.10636 | 0.995 | -0.095495 | 32.1162
23 | 0.016059 | 0.0040262 | -0.016055 | -0.0040241 | 3.6683e-06 | 2.1293e-06 | 0.024065 | 0.024065 | 0.024065 | 0.99299 | -0.13429 | 0.99274 | -0.13908 | 6.6112
24 | -0.31251 | -0.079055 | 0.31262 | 0.07913 | 0.00011666 | 7.4368e-05 | 0.46761 | 0.46761 | 0.46761 | 0.995 | -0.095495 | 0.99541 | -0.087718 | 32.1162
25 | 0.0026727 | 0.0006697 | -0.0026727 | -0.00066983 | 8.2399e-08 | -1.2619e-07 | 0.0039954 | 0.0039954 | 0.0039954 | 0.99541 | -0.087718 | 0.99537 | -0.088365 | 1.0976
26 | -0.33232 | -0.084064 | 0.33267 | 0.084289 | 0.00035219 | 0.00022461 | 0.49705 | 0.49705 | 0.49705 | 0.99541 | -0.087718 | 0.99656 | -0.065655 | 34.1378
27 | 0.0085221 | 0.0021359 | -0.0085215 | -0.0021357 | 5.5131e-07 | 2.3643e-07 | 0.012776 | 0.012776 | 0.012776 | 0.99257 | -0.14236 | 0.9925 | -0.14372 | 3.5099
28 | -0.0085221 | -0.0021359 | 0.0085234 | 0.0021365 | 1.3311e-06 | 5.7076e-07 | 0.012776 | 0.012776 | 0.012776 | 0.99257 | -0.14236 | 0.99274 | -0.13908 | 3.5099
29 | 0.0085215 | 0.0021357 | -0.0085214 | -0.0021357 | 1.03e-07 | 4.4174e-08 | 0.012776 | 0.012776 | 0.012776 | 0.9925 | -0.14372 | 0.99249 | -0.14397 | 3.5099
30 | 0.51641 | 0.13078 | -0.516 | -0.13052 | 0.00040771 | 0.00026055 | 0.77089 | 0.77089 | 0.77089 | 0.99742 | -0.0492 | 0.99656 | -0.065655 | 52.9455
31 | 0.020622 | 0.0051699 | -0.020617 | -0.0051671 | 4.609e-06 | 2.7803e-06 | 0.030765 | 0.030765 | 0.030765 | 0.99742 | -0.0492 | 0.99718 | -0.053892 | 8.452
32 | -0.53703 | -0.13595 | 0.5383 | 0.13676 | 0.0012717 | 0.0008128 | 0.80165 | 0.80165 | 0.80165 | 0.99742 | -0.0492 | 1 | 0 | 55.0585
33 | 0.18333 | 0.046229 | -0.18318 | -0.046135 | 0.00014801 | 9.3633e-05 | 0.27384 | 0.27384 | 0.27384 | 0.99656 | -0.065655 | 0.99568 | -0.082538 | 18.8077
34 | 0.01888 | 0.0047331 | -0.018876 | -0.0047308 | 3.8939e-06 | 2.3196e-06 | 0.028094 | 0.028094 | 0.028094 | 1 | 0 | 0.99977 | -0.0043294 | 7.7181
35 | 0.01642 | 0.0041169 | -0.016419 | -0.0041165 | 7.8087e-07 | 4.5613e-07 | 0.024726 | 0.024726 | 0.024726 | 0.98816 | -0.2275 | 0.98811 | -0.22849 | 6.7928
36 | -0.058053 | -0.014561 | 0.058073 | 0.014574 | 2.0418e-05 | 1.2976e-05 | 0.087422 | 0.087422 | 0.087422 | 0.98816 | -0.2275 | 0.98854 | -0.22012 | 24.0171
37 | 0.041633 | 0.010444 | -0.041613 | -0.010431 | 2.0745e-05 | 1.3097e-05 | 0.062697 | 0.062697 | 0.062697 | 0.98816 | -0.2275 | 0.98762 | -0.23795 | 17.2244
38 | 0.016419 | 0.0041165 | -0.016414 | -0.0041138 | 4.6522e-06 | 2.7176e-06 | 0.024726 | 0.024726 | 0.024726 | 0.98811 | -0.22849 | 0.98781 | -0.23444 | 6.7928
39 | 0.10036 | 0.02527 | -0.10024 | -0.025197 | 0.00011317 | 7.2263e-05 | 0.15111 | 0.15111 | 0.15111 | 0.98854 | -0.22012 | 0.98732 | -0.24374 | 41.5128
40 | -0.15843 | -0.039844 | 0.15857 | 0.039935 | 0.00014351 | 9.1504e-05 | 0.23853 | 0.23853 | 0.23853 | 0.98854 | -0.22012 | 0.98952 | -0.20117 | 32.7649
41 | 0.019724 | 0.0049451 | -0.019719 | -0.0049421 | 5.0998e-06 | 3.0669e-06 | 0.029718 | 0.029718 | 0.029718 | 0.98762 | -0.23795 | 0.98735 | -0.24338 | 8.1642
42 | 0.051565 | 0.01294 | -0.051544 | -0.012927 | 2.0508e-05 | 1.3008e-05 | 0.077548 | 0.077548 | 0.077548 | 0.98952 | -0.20117 | 0.98909 | -0.20952 | 21.3044
43 | -0.21014 | -0.052875 | 0.21024 | 0.052941 | 0.0001045 | 6.6305e-05 | 0.31608 | 0.31608 | 0.31608 | 0.98952 | -0.20117 | 0.99006 | -0.19077 | 21.7086
44 | 0.034383 | 0.0086258 | -0.034364 | -0.0086141 | 1.8643e-05 | 1.1693e-05 | 0.05173 | 0.05173 | 0.05173 | 0.98909 | -0.20952 | 0.9885 | -0.2209 | 14.2115
45 | -0.22854 | -0.057528 | 0.22873 | 0.057643 | 0.00018144 | 0.00011528 | 0.34358 | 0.34358 | 0.34358 | 0.99006 | -0.19077 | 0.99092 | -0.17418 | 23.5976
46 | 0.077142 | 0.019407 | -0.077047 | -0.019347 | 9.4991e-05 | 6.0555e-05 | 0.11629 | 0.11629 | 0.11629 | 0.98732 | -0.24374 | 0.986 | -0.26954 | 31.9474
47 | 0.16935 | 0.042667 | -0.16926 | -0.042613 | 8.6425e-05 | 5.4564e-05 | 0.25316 | 0.25316 | 0.25316 | 0.99568 | -0.082538 | 0.99513 | -0.093213 | 17.3875
48 | -0.0083009 | -0.0020804 | 0.0083017 | 0.0020807 | 7.7786e-07 | 3.2837e-07 | 0.012511 | 0.012511 | 0.012511 | 0.98725 | -0.24535 | 0.98735 | -0.24338 | 3.4372
49 | -0.059654 | -0.014973 | 0.059694 | 0.014998 | 3.9604e-05 | 2.5181e-05 | 0.0901 | 0.0901 | 0.0901 | 0.98528 | -0.28346 | 0.986 | -0.26954 | 24.7527
50 | -0.016066 | -0.0040265 | 0.016069 | 0.004028 | 2.6045e-06 | 1.5126e-06 | 0.024104 | 0.024104 | 0.024104 | 0.99182 | -0.15707 | 0.992 | -0.15367 | 6.6219
51 | 0.016255 | 0.0040741 | -0.016255 | -0.0040738 | 3.9553e-07 | 2.3032e-07 | 0.024406 | 0.024406 | 0.024406 | 0.99106 | -0.17186 | 0.99103 | -0.17237 | 6.705
52 | -0.16141 | -0.040618 | 0.16149 | 0.040665 | 7.4836e-05 | 4.7184e-05 | 0.24154 | 0.24154 | 0.24154 | 0.99462 | -0.10291 | 0.99513 | -0.093213 | 16.5894
53 | 0.014183 | 0.0035549 | -0.014181 | -0.0035542 | 1.2167e-06 | 6.866e-07 | 0.021302 | 0.021302 | 0.021302 | 0.9907 | -0.17882 | 0.9906 | -0.18062 | 5.8523
54 | 0.27772 | 0.070153 | -0.27753 | -0.070033 | 0.00018793 | 0.00011968 | 0.41619 | 0.41619 | 0.41619 | 0.99339 | -0.12644 | 0.99266 | -0.14057 | 28.5845
55 | 0.022403 | 0.0056156 | -0.0224 | -0.005614 | 2.5647e-06 | 1.5643e-06 | 0.033724 | 0.033724 | 0.033724 | 0.9885 | -0.2209 | 0.98838 | -0.2233 | 9.2648
56 | 0.011961 | 0.0029985 | -0.011959 | -0.0029972 | 2.3375e-06 | 1.2496e-06 | 0.018006 | 0.018006 | 0.018006 | 0.9885 | -0.2209 | 0.98829 | -0.225 | 4.9467
57 | -0.24683 | -0.06218 | 0.24704 | 0.062314 | 0.00020984 | 0.00013346 | 0.37077 | 0.37077 | 0.37077 | 0.99092 | -0.17418 | 0.99184 | -0.15642 | 25.4648
58 | 0.26531 | 0.06697 | -0.2651 | -0.066841 | 0.00020129 | 0.00012813 | 0.39787 | 0.39787 | 0.39787 | 0.99266 | -0.14057 | 0.99184 | -0.15642 | 27.3262

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.56936 | 0.14413

## res_load
| p_mw | q_mvar
0 | 0.0088869 | 0.0022273
1 | 0.0083517 | 0.0020931
2 | 0.012267 | 0.0030745
3 | 0.019455 | 0.0048759
4 | 0.017608 | 0.0044129
5 | 0.0096221 | 0.0024115
6 | 0.0065052 | 0.0016304
7 | 0.01038 | 0.0026015
8 | 0.0066989 | 0.0016789
9 | 0.0095842 | 0.002402
10 | 0.007286 | 0.0018261
11 | 0.017018 | 0.0042652
12 | 0.0075315 | 0.0018876
13 | 0.020617 | 0.0051671
14 | 0.010531 | 0.0026393
15 | 0.021889 | 0.0054859
16 | 0.017162 | 0.0043011
17 | 0.018301 | 0.0045866
18 | 0.023102 | 0.00579
19 | 0.013837 | 0.003468
20 | 0.016414 | 0.0041138
21 | 0.0085214 | 0.0021357
22 | 0.0083009 | 0.0020804
23 | 0.011417 | 0.0028614
24 | 0.010634 | 0.0026651
25 | 0.016066 | 0.0040265
26 | 0.0095395 | 0.0023908
27 | 0.029688 | 0.0074405
28 | 0.0071052 | 0.0017807
29 | 0.0077502 | 0.0019424
30 | 0.010974 | 0.0027504
31 | 0.0026727 | 0.00066983
32 | 0.018876 | 0.0047308
33 | 0.018104 | 0.0045373
34 | 0.017353 | 0.0043491
35 | 0.0077711 | 0.0019476
36 | 0.014181 | 0.0035542
37 | 0.011959 | 0.0029972
38 | 0.0224 | 0.005614
39 | 0.016255 | 0.0040738
40 | 0.012223 | 0.0030634
41 | 0.018065 | 0.0045275

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1