## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-663_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-663_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-663_0_6_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_261-663_0_6_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_261-663_0_6_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_261-663_0_6_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_261-663_0_6_node_60 | 0.4 | n |  | TRUE
7 | bus_LV_261-663_0_6_node_136 | 0.4 | n |  | TRUE
8 | bus_LV_261-663_0_6_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_261-663_0_6_node_61 | 0.4 | n |  | TRUE
10 | bus_LV_261-663_0_6_node_7 | 0.4 | n |  | TRUE
11 | bus_LV_261-663_0_6_node_16 | 0.4 | n |  | TRUE
12 | bus_LV_261-663_0_6_node_17 | 0.4 | n |  | TRUE
13 | bus_LV_261-663_0_6_node_8 | 0.4 | n |  | TRUE
14 | bus_LV_261-663_0_6_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_261-663_0_6_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_261-663_0_6_node_30 | 0.4 | n |  | TRUE
17 | bus_LV_261-663_0_6_node_11 | 0.4 | n |  | TRUE
18 | bus_LV_261-663_0_6_node_43 | 0.4 | n |  | TRUE
19 | bus_LV_261-663_0_6_node_31 | 0.4 | n |  | TRUE
20 | bus_LV_261-663_0_6_node_32 | 0.4 | n |  | TRUE
21 | bus_LV_261-663_0_6_node_42 | 0.4 | n |  | TRUE
22 | bus_LV_261-663_0_6_node_12 | 0.4 | n |  | TRUE
23 | bus_LV_261-663_0_6_node_13 | 0.4 | n |  | TRUE
24 | bus_LV_261-663_0_6_node_14 | 0.4 | n |  | TRUE
25 | bus_LV_261-663_0_6_node_15 | 0.4 | n |  | TRUE
26 | bus_LV_261-663_0_6_node_44 | 0.4 | n |  | TRUE
27 | bus_LV_261-663_0_6_node_139 | 0.4 | n |  | TRUE
28 | bus_LV_261-663_0_6_node_45 | 0.4 | n |  | TRUE
29 | bus_LV_261-663_0_6_node_140 | 0.4 | n |  | TRUE
30 | bus_LV_261-663_0_6_node_36 | 0.4 | n |  | TRUE
31 | bus_LV_261-663_0_6_node_35 | 0.4 | n |  | TRUE
32 | bus_LV_261-663_0_6_node_18 | 0.4 | n |  | TRUE
33 | bus_LV_261-663_0_6_node_19 | 0.4 | n |  | TRUE
34 | bus_LV_261-663_0_6_node_20 | 0.4 | n |  | TRUE
35 | bus_LV_261-663_0_6_node_21 | 0.4 | n |  | TRUE
36 | bus_LV_261-663_0_6_node_22 | 0.4 | n |  | TRUE
37 | bus_LV_261-663_0_6_node_23 | 0.4 | n |  | TRUE
38 | bus_LV_261-663_0_6_node_24 | 0.4 | n |  | TRUE
39 | bus_LV_261-663_0_6_node_58 | 0.4 | n |  | TRUE
40 | bus_LV_261-663_0_6_node_27 | 0.4 | n |  | TRUE
41 | bus_LV_261-663_0_6_node_25 | 0.4 | n |  | TRUE
42 | bus_LV_261-663_0_6_node_146 | 0.4 | n |  | TRUE
43 | bus_LV_261-663_0_6_node_79 | 0.4 | n |  | TRUE
44 | bus_LV_261-663_0_6_node_80 | 0.4 | n |  | TRUE
45 | bus_LV_261-663_0_6_node_57 | 0.4 | n |  | TRUE
46 | bus_LV_261-663_0_6_node_49 | 0.4 | n |  | TRUE
47 | bus_LV_261-663_0_6_node_26 | 0.4 | n |  | TRUE
48 | bus_LV_261-663_0_6_node_28 | 0.4 | n |  | TRUE
49 | bus_LV_261-663_0_6_node_29 | 0.4 | n |  | TRUE
50 | bus_LV_261-663_0_6_node_33 | 0.4 | n |  | TRUE
51 | bus_LV_261-663_0_6_node_34 | 0.4 | n |  | TRUE
52 | bus_LV_261-663_0_6_node_39 | 0.4 | n |  | TRUE
53 | bus_LV_261-663_0_6_node_62 | 0.4 | n |  | TRUE
54 | bus_LV_261-663_0_6_node_40 | 0.4 | n |  | TRUE
55 | bus_LV_261-663_0_6_node_37 | 0.4 | n |  | TRUE
56 | bus_LV_261-663_0_6_node_38 | 0.4 | n |  | TRUE
57 | bus_LV_261-663_0_6_node_48 | 0.4 | n |  | TRUE
58 | bus_LV_261-663_0_6_node_144 | 0.4 | n |  | TRUE
59 | bus_LV_261-663_0_6_node_41 | 0.4 | n |  | TRUE
60 | bus_LV_261-663_0_6_node_59 | 0.4 | n |  | TRUE
61 | bus_LV_261-663_0_6_node_47 | 0.4 | n |  | TRUE
62 | bus_LV_261-663_0_6_node_111 | 0.4 | n |  | TRUE
63 | bus_LV_261-663_0_6_node_97 | 0.4 | n |  | TRUE
64 | bus_LV_261-663_0_6_node_135 | 0.4 | n |  | TRUE
65 | bus_LV_261-663_0_6_node_110 | 0.4 | n |  | TRUE
66 | bus_LV_261-663_0_6_node_95 | 0.4 | n |  | TRUE
67 | bus_LV_261-663_0_6_node_50 | 0.4 | n |  | TRUE
68 | bus_LV_261-663_0_6_node_51 | 0.4 | n |  | TRUE
69 | bus_LV_261-663_0_6_node_52 | 0.4 | n |  | TRUE
70 | bus_LV_261-663_0_6_node_53 | 0.4 | n |  | TRUE
71 | bus_LV_261-663_0_6_node_54 | 0.4 | n |  | TRUE
72 | bus_LV_261-663_0_6_node_71 | 0.4 | n |  | TRUE
73 | bus_LV_261-663_0_6_node_55 | 0.4 | n |  | TRUE
74 | bus_LV_261-663_0_6_node_65 | 0.4 | n |  | TRUE
75 | bus_LV_261-663_0_6_node_56 | 0.4 | n |  | TRUE
76 | bus_LV_261-663_0_6_node_64 | 0.4 | n |  | TRUE
77 | bus_LV_261-663_0_6_node_72 | 0.4 | n |  | TRUE
78 | bus_LV_261-663_0_6_node_78 | 0.4 | n |  | TRUE
79 | bus_LV_261-663_0_6_node_66 | 0.4 | n |  | TRUE
80 | bus_LV_261-663_0_6_node_67 | 0.4 | n |  | TRUE
81 | bus_LV_261-663_0_6_node_68 | 0.4 | n |  | TRUE
82 | bus_LV_261-663_0_6_node_69 | 0.4 | n |  | TRUE
83 | bus_LV_261-663_0_6_node_70 | 0.4 | n |  | TRUE
84 | bus_LV_261-663_0_6_node_77 | 0.4 | n |  | TRUE
85 | bus_LV_261-663_0_6_node_73 | 0.4 | n |  | TRUE
86 | bus_LV_261-663_0_6_node_84 | 0.4 | n |  | TRUE
87 | bus_LV_261-663_0_6_node_74 | 0.4 | n |  | TRUE
88 | bus_LV_261-663_0_6_node_75 | 0.4 | n |  | TRUE
89 | bus_LV_261-663_0_6_node_76 | 0.4 | n |  | TRUE
90 | bus_LV_261-663_0_6_node_115 | 0.4 | n |  | TRUE
91 | bus_LV_261-663_0_6_node_120 | 0.4 | n |  | TRUE
92 | bus_LV_261-663_0_6_node_82 | 0.4 | n |  | TRUE
93 | bus_LV_261-663_0_6_node_113 | 0.4 | n |  | TRUE
94 | bus_LV_261-663_0_6_node_118 | 0.4 | n |  | TRUE
95 | bus_LV_261-663_0_6_node_83 | 0.4 | n |  | TRUE
96 | bus_LV_261-663_0_6_node_81 | 0.4 | n |  | TRUE
97 | bus_LV_261-663_0_6_node_124 | 0.4 | n |  | TRUE
98 | bus_LV_261-663_0_6_node_126 | 0.4 | n |  | TRUE
99 | bus_LV_261-663_0_6_node_122 | 0.4 | n |  | TRUE
100 | bus_LV_261-663_0_6_node_87 | 0.4 | n |  | TRUE
101 | bus_LV_261-663_0_6_node_89 | 0.4 | n |  | TRUE
102 | bus_LV_261-663_0_6_node_86 | 0.4 | n |  | TRUE
103 | bus_LV_261-663_0_6_node_143 | 0.4 | n |  | TRUE
104 | bus_LV_261-663_0_6_node_92 | 0.4 | n |  | TRUE
105 | bus_LV_261-663_0_6_node_142 | 0.4 | n |  | TRUE
106 | bus_LV_261-663_0_6_node_125 | 0.4 | n |  | TRUE
107 | bus_LV_261-663_0_6_node_90 | 0.4 | n |  | TRUE
108 | bus_LV_261-663_0_6_node_91 | 0.4 | n |  | TRUE
109 | bus_LV_261-663_0_6_node_93 | 0.4 | n |  | TRUE
110 | bus_LV_261-663_0_6_node_123 | 0.4 | n |  | TRUE
111 | bus_LV_261-663_0_6_node_94 | 0.4 | n |  | TRUE
112 | bus_LV_261-663_0_6_node_108 | 0.4 | n |  | TRUE
113 | bus_LV_261-663_0_6_node_96 | 0.4 | n |  | TRUE
114 | bus_LV_261-663_0_6_node_98 | 0.4 | n |  | TRUE
115 | bus_LV_261-663_0_6_node_99 | 0.4 | n |  | TRUE
116 | bus_LV_261-663_0_6_node_100 | 0.4 | n |  | TRUE
117 | bus_LV_261-663_0_6_node_101 | 0.4 | n |  | TRUE
118 | bus_LV_261-663_0_6_node_102 | 0.4 | n |  | TRUE
119 | bus_LV_261-663_0_6_node_105 | 0.4 | n |  | TRUE
120 | bus_LV_261-663_0_6_node_103 | 0.4 | n |  | TRUE
121 | bus_LV_261-663_0_6_node_109 | 0.4 | n |  | TRUE
122 | bus_LV_261-663_0_6_node_106 | 0.4 | n |  | TRUE
123 | bus_LV_261-663_0_6_node_104 | 0.4 | n |  | TRUE
124 | bus_LV_261-663_0_6_node_107 | 0.4 | n |  | TRUE
125 | bus_LV_261-663_0_6_node_133 | 0.4 | n |  | TRUE
126 | bus_LV_261-663_0_6_node_138 | 0.4 | n |  | TRUE
127 | bus_LV_261-663_0_6_node_132 | 0.4 | n |  | TRUE
128 | bus_LV_261-663_0_6_node_137 | 0.4 | n |  | TRUE
129 | bus_LV_261-663_0_6_node_134 | 0.4 | n |  | TRUE
130 | bus_LV_261-663_0_6_node_112 | 0.4 | n |  | TRUE
131 | bus_LV_261-663_0_6_node_114 | 0.4 | n |  | TRUE
132 | bus_LV_261-663_0_6_node_116 | 0.4 | n |  | TRUE
133 | bus_LV_261-663_0_6_node_117 | 0.4 | n |  | TRUE
134 | bus_LV_261-663_0_6_node_119 | 0.4 | n |  | TRUE
135 | bus_LV_261-663_0_6_node_121 | 0.4 | n |  | TRUE
136 | bus_LV_261-663_0_6_node_127 | 0.4 | n |  | TRUE
137 | bus_LV_261-663_0_6_node_128 | 0.4 | n |  | TRUE
138 | bus_LV_261-663_0_6_node_129 | 0.4 | n |  | TRUE
139 | bus_LV_261-663_0_6_node_130 | 0.4 | n |  | TRUE
140 | bus_LV_261-663_0_6_node_131 | 0.4 | n |  | TRUE
141 | bus_MV_493_0_node_73 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-663_0_6_load_0 | 0 | 0.0024475 | 0.00061341 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-663_0_6_load_3 | 3 | 0.0028822 | 0.00072235 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-663_0_6_load_4 | 4 | 0.0027876 | 0.00069863 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-663_0_6_load_5 | 5 | 0.0013398 | 0.00033578 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-663_0_6_load_136 | 7 | 0.0034008 | 0.00085232 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-663_0_6_load_7 | 10 | 0.0026224 | 0.00065723 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-663_0_6_load_16 | 11 | 0.0025475 | 0.00063845 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-663_0_6_load_17 | 12 | 0.0042492 | 0.0010649 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-663_0_6_load_8 | 13 | 0.0012531 | 0.00031407 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-663_0_6_load_10 | 15 | 0.0029151 | 0.0007306 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-663_0_6_load_11 | 17 | 0.00075923 | 0.00019028 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-663_0_6_load_43 | 18 | 0.00075783 | 0.00018993 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-663_0_6_load_31 | 19 | 0.003996 | 0.0010015 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-663_0_6_load_32 | 20 | 0.0019482 | 0.00048825 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-663_0_6_load_42 | 21 | 0.0011982 | 0.00030031 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-663_0_6_load_12 | 22 | 0.0014914 | 0.00037377 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-663_0_6_load_15 | 25 | 0.0017584 | 0.0004407 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_261-663_0_6_load_139 | 27 | 0.0025833 | 0.00064745 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_261-663_0_6_load_140 | 29 | 0.0024997 | 0.00062649 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_261-663_0_6_load_36 | 30 | 0.0059411 | 0.001489 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_261-663_0_6_load_35 | 31 | 0.0026125 | 0.00065475 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_261-663_0_6_load_18 | 32 | 0.0038343 | 0.00096097 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_261-663_0_6_load_22 | 36 | 0.0014509 | 0.00036363 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_261-663_0_6_load_58 | 39 | 0.0010995 | 0.00027555 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_261-663_0_6_load_27 | 40 | 0.0017787 | 0.00044578 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_261-663_0_6_load_25 | 41 | 0.0033218 | 0.00083253 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_261-663_0_6_load_146 | 42 | 0.015578 | 0.0039043 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_261-663_0_6_load_79 | 43 | 0.0068248 | 0.0017104 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_261-663_0_6_load_80 | 44 | 0.0025936 | 0.00065002 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_261-663_0_6_load_57 | 45 | 0.0033745 | 0.00084572 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_261-663_0_6_load_49 | 46 | 0.0040603 | 0.0010176 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_261-663_0_6_load_28 | 48 | 0.0071375 | 0.0017888 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_261-663_0_6_load_29 | 49 | 0.0068892 | 0.0017266 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_261-663_0_6_load_33 | 50 | 0.0061721 | 0.0015469 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_261-663_0_6_load_34 | 51 | 0.0062644 | 0.00157 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_261-663_0_6_load_39 | 52 | 0.0028245 | 0.00070787 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_261-663_0_6_load_62 | 53 | 0.0043313 | 0.0010855 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_261-663_0_6_load_40 | 54 | 0.0028459 | 0.00071324 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_261-663_0_6_load_37 | 55 | 0.003244 | 0.00081302 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_261-663_0_6_load_38 | 56 | 0.0030096 | 0.00075426 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_261-663_0_6_load_48 | 57 | 0.0036273 | 0.0009091 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_261-663_0_6_load_144 | 58 | 0.0029303 | 0.0007344 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_261-663_0_6_load_41 | 59 | 0.0033933 | 0.00085044 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_261-663_0_6_load_59 | 60 | 0.0037845 | 0.00094848 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_261-663_0_6_load_97 | 63 | 0.0089357 | 0.0022395 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_261-663_0_6_load_135 | 64 | 0.001772 | 0.00044411 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_261-663_0_6_load_95 | 66 | 0.0038398 | 0.00096235 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_261-663_0_6_load_50 | 67 | 0.0024606 | 0.00061667 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_261-663_0_6_load_51 | 68 | 0.0028995 | 0.00072668 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_261-663_0_6_load_52 | 69 | 0.0023704 | 0.00059408 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_261-663_0_6_load_53 | 70 | 0.001224 | 0.00030677 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_261-663_0_6_load_54 | 71 | 0.0043177 | 0.0010821 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_261-663_0_6_load_71 | 72 | 0.0040406 | 0.0010127 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_261-663_0_6_load_55 | 73 | 0.0025632 | 0.00064241 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_261-663_0_6_load_56 | 75 | 0.0036563 | 0.00091636 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_261-663_0_6_load_64 | 76 | 0.0083309 | 0.0020879 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_261-663_0_6_load_72 | 77 | 0.001301 | 0.00032605 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_261-663_0_6_load_78 | 78 | 0.0016465 | 0.00041264 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_261-663_0_6_load_66 | 79 | 0.0020309 | 0.00050899 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_261-663_0_6_load_67 | 80 | 0.0018492 | 0.00046346 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_261-663_0_6_load_69 | 82 | 0.0018494 | 0.00046351 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_261-663_0_6_load_77 | 84 | 0.002276 | 0.00057042 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_261-663_0_6_load_73 | 85 | 0.0026812 | 0.00067197 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_261-663_0_6_load_84 | 86 | 0.0048614 | 0.0012184 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_261-663_0_6_load_76 | 89 | 0.0050581 | 0.0012677 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_261-663_0_6_load_120 | 91 | 0.0010311 | 0.00025843 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_261-663_0_6_load_82 | 92 | 0.0015339 | 0.00038444 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_261-663_0_6_load_113 | 93 | 0.0012456 | 0.00031218 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_261-663_0_6_load_118 | 94 | 0.0019226 | 0.00048186 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_261-663_0_6_load_83 | 95 | 0.002615 | 0.00065539 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_261-663_0_6_load_126 | 98 | 0.0024577 | 0.00061596 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_261-663_0_6_load_122 | 99 | 0.002426 | 0.00060801 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_261-663_0_6_load_89 | 101 | 0.0091767 | 0.0022999 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_261-663_0_6_load_143 | 103 | 0.0014291 | 0.00035816 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_261-663_0_6_load_142 | 105 | 0.0025046 | 0.00062771 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_261-663_0_6_load_125 | 106 | 0.0024589 | 0.00061626 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_261-663_0_6_load_90 | 107 | 0.0076249 | 0.001911 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_261-663_0_6_load_91 | 108 | 0.0024589 | 0.00061626 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_261-663_0_6_load_93 | 109 | 0.0025057 | 0.00062799 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_261-663_0_6_load_94 | 111 | 0.0075758 | 0.0018987 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_261-663_0_6_load_108 | 112 | 0.004208 | 0.0010546 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_261-663_0_6_load_96 | 113 | 0.0074536 | 0.001868 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_261-663_0_6_load_98 | 114 | 0.0091487 | 0.0022929 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_261-663_0_6_load_99 | 115 | 0.011982 | 0.003003 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_261-663_0_6_load_102 | 118 | 0.0071702 | 0.001797 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_261-663_0_6_load_109 | 121 | 0.0078224 | 0.0019605 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_261-663_0_6_load_106 | 122 | 0.0076763 | 0.0019239 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_261-663_0_6_load_104 | 123 | 0.0091337 | 0.0022891 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_261-663_0_6_load_133 | 125 | 0.0068626 | 0.0017199 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_261-663_0_6_load_138 | 126 | 0.008703 | 0.0021812 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_261-663_0_6_load_132 | 127 | 0.0063717 | 0.0015969 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_261-663_0_6_load_137 | 128 | 0.0024468 | 0.00061323 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_261-663_0_6_load_134 | 129 | 0.0019473 | 0.00048804 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_261-663_0_6_load_112 | 130 | 0.0023724 | 0.00059457 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_261-663_0_6_load_116 | 132 | 0.0022895 | 0.0005738 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_261-663_0_6_load_117 | 133 | 0.001833 | 0.0004594 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_261-663_0_6_load_119 | 134 | 0.0011328 | 0.00028391 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_261-663_0_6_load_121 | 135 | 0.0063281 | 0.001586 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_261-663_0_6_load_127 | 136 | 0.0032214 | 0.00080736 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_261-663_0_6_load_128 | 137 | 0.0033762 | 0.00084615 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_261-663_0_6_load_129 | 138 | 0.003449 | 0.0008644 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_261-663_0_6_load_130 | 139 | 0.0056773 | 0.0014229 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_261-663_0_6_load_131 | 140 | 0.001904 | 0.0004772 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 110 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-663_0_6_line_0 |  | 0 | 1 | 0.018998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
1 | LV_261-663_0_6_line_1 |  | 0 | 2 | 0.010855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
2 | LV_261-663_0_6_line_2 |  | 1 | 3 | 0.020215 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
3 | LV_261-663_0_6_line_3 |  | 1 | 4 | 0.015501 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-663_0_6_line_4 |  | 2 | 5 | 0.0037178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
5 | LV_261-663_0_6_line_5 |  | 3 | 6 | 0.0072884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
6 | LV_261-663_0_6_line_6 |  | 4 | 7 | 0.013908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_261-663_0_6_line_7 |  | 5 | 8 | 0.01285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
8 | LV_261-663_0_6_line_8 |  | 6 | 9 | 0.021435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
9 | LV_261-663_0_6_line_9 |  | 8 | 10 | 0.016562 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
10 | LV_261-663_0_6_line_10 |  | 9 | 74 | 0.013389 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
11 | LV_261-663_0_6_line_11 |  | 9 | 76 | 0.011847 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_261-663_0_6_line_12 |  | 10 | 11 | 0.018513 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-663_0_6_line_13 |  | 11 | 12 | 0.010465 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_261-663_0_6_line_14 |  | 12 | 30 | 0.016082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_261-663_0_6_line_15 |  | 13 | 14 | 0.015205 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_261-663_0_6_line_16 |  | 14 | 15 | 0.013465 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_261-663_0_6_line_17 |  | 15 | 16 | 0.01459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_261-663_0_6_line_18 |  | 16 | 19 | 0.0078362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_261-663_0_6_line_19 |  | 16 | 20 | 0.018363 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_261-663_0_6_line_20 |  | 17 | 18 | 1.4722e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_261-663_0_6_line_21 |  | 18 | 21 | 0.0012142 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_261-663_0_6_line_22 |  | 19 | 52 | 0.027799 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_261-663_0_6_line_23 |  | 20 | 53 | 0.00095105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_261-663_0_6_line_24 |  | 21 | 26 | 0.021256 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_261-663_0_6_line_25 |  | 22 | 23 | 0.020872 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_261-663_0_6_line_26 |  | 23 | 24 | 0.022992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_261-663_0_6_line_27 |  | 23 | 25 | 0.01564 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_261-663_0_6_line_28 |  | 24 | 26 | 0.032232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_261-663_0_6_line_29 |  | 24 | 27 | 0.021615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_261-663_0_6_line_30 |  | 26 | 28 | 0.003661 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_261-663_0_6_line_31 |  | 27 | 29 | 0.00015178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_261-663_0_6_line_32 |  | 28 | 60 | 0.026652 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_261-663_0_6_line_33 |  | 28 | 46 | 0.036392 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_261-663_0_6_line_34 |  | 30 | 31 | 0.010906 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_261-663_0_6_line_35 |  | 31 | 55 | 0.010261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_261-663_0_6_line_36 |  | 32 | 33 | 0.0034025 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_261-663_0_6_line_37 |  | 32 | 34 | 0.0036921 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_261-663_0_6_line_38 |  | 33 | 35 | 0.01637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_261-663_0_6_line_39 |  | 33 | 36 | 0.018647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
40 | LV_261-663_0_6_line_40 |  | 34 | 37 | 0.005405 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_261-663_0_6_line_41 |  | 35 | 38 | 0.011858 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_261-663_0_6_line_42 |  | 36 | 39 | 0.0066859 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
43 | LV_261-663_0_6_line_43 |  | 37 | 40 | 0.033779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_261-663_0_6_line_44 |  | 37 | 41 | 0.021521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_261-663_0_6_line_45 |  | 38 | 42 | 0.005769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_261-663_0_6_line_46 |  | 39 | 45 | 0.020877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
47 | LV_261-663_0_6_line_47 |  | 40 | 46 | 9.8857e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_261-663_0_6_line_48 |  | 41 | 47 | 0.030463 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_261-663_0_6_line_49 |  | 43 | 44 | 3.7915e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_261-663_0_6_line_50 |  | 44 | 96 | 0.016432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_261-663_0_6_line_51 |  | 45 | 75 | 0.024806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
52 | LV_261-663_0_6_line_52 |  | 47 | 48 | 0.021855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_261-663_0_6_line_53 |  | 47 | 49 | 0.01066 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_261-663_0_6_line_54 |  | 49 | 50 | 0.0043613 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_261-663_0_6_line_55 |  | 50 | 51 | 0.025866 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_261-663_0_6_line_56 |  | 52 | 54 | 0.011226 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_261-663_0_6_line_57 |  | 54 | 59 | 0.01336 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_261-663_0_6_line_58 |  | 55 | 56 | 0.015768 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_261-663_0_6_line_59 |  | 56 | 57 | 0.010698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_261-663_0_6_line_60 |  | 56 | 58 | 0.07102 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_261-663_0_6_line_61 |  | 57 | 59 | 0.01411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_261-663_0_6_line_62 |  | 61 | 62 | 0.025759 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_261-663_0_6_line_63 |  | 61 | 63 | 0.015933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_261-663_0_6_line_64 |  | 62 | 64 | 0.01899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_261-663_0_6_line_65 |  | 62 | 65 | 0.007032 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_261-663_0_6_line_66 |  | 63 | 66 | 0.0069448 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_261-663_0_6_line_67 |  | 64 | 129 | 0.015148 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_261-663_0_6_line_68 |  | 65 | 112 | 0.0051036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_261-663_0_6_line_69 |  | 65 | 111 | 0.054009 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_261-663_0_6_line_70 |  | 66 | 113 | 0.033938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_261-663_0_6_line_71 |  | 67 | 68 | 0.015787 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
72 | LV_261-663_0_6_line_72 |  | 67 | 69 | 0.0085033 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
73 | LV_261-663_0_6_line_73 |  | 68 | 70 | 0.019594 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
74 | LV_261-663_0_6_line_74 |  | 69 | 71 | 0.017886 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
75 | LV_261-663_0_6_line_75 |  | 70 | 72 | 0.014299 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
76 | LV_261-663_0_6_line_76 |  | 71 | 73 | 0.0078416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
77 | LV_261-663_0_6_line_77 |  | 72 | 74 | 0.019126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
78 | LV_261-663_0_6_line_78 |  | 73 | 75 | 0.015492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
79 | LV_261-663_0_6_line_79 |  | 74 | 77 | 0.015541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
80 | LV_261-663_0_6_line_80 |  | 77 | 78 | 0.032905 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
81 | LV_261-663_0_6_line_81 |  | 78 | 82 | 0.010104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
82 | LV_261-663_0_6_line_82 |  | 79 | 80 | 0.018701 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
83 | LV_261-663_0_6_line_83 |  | 79 | 81 | 0.017341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
84 | LV_261-663_0_6_line_84 |  | 80 | 82 | 0.00078606 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
85 | LV_261-663_0_6_line_85 |  | 81 | 83 | 0.012357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
86 | LV_261-663_0_6_line_86 |  | 83 | 84 | 0.05442 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_261-663_0_6_line_87 |  | 83 | 85 | 0.0122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
88 | LV_261-663_0_6_line_88 |  | 84 | 86 | 0.013482 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_261-663_0_6_line_89 |  | 85 | 87 | 0.0075251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
90 | LV_261-663_0_6_line_90 |  | 87 | 88 | 0.009646 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
91 | LV_261-663_0_6_line_91 |  | 87 | 89 | 0.017988 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
92 | LV_261-663_0_6_line_92 |  | 88 | 90 | 0.008363 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
93 | LV_261-663_0_6_line_93 |  | 88 | 91 | 0.018503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_261-663_0_6_line_94 |  | 89 | 92 | 0.015801 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
95 | LV_261-663_0_6_line_95 |  | 90 | 93 | 0.023809 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
96 | LV_261-663_0_6_line_96 |  | 91 | 94 | 0.0046552 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_261-663_0_6_line_97 |  | 92 | 95 | 0.03438 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
98 | LV_261-663_0_6_line_98 |  | 93 | 130 | 0.035352 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
99 | LV_261-663_0_6_line_99 |  | 94 | 133 | 0.001364 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_261-663_0_6_line_100 |  | 95 | 100 | 0.018149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
101 | LV_261-663_0_6_line_101 |  | 96 | 97 | 0.01147 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_261-663_0_6_line_102 |  | 97 | 98 | 0.0098728 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_261-663_0_6_line_103 |  | 97 | 99 | 0.0055432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_261-663_0_6_line_104 |  | 98 | 102 | 0.0068417 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_261-663_0_6_line_105 |  | 99 | 110 | 0.015313 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_261-663_0_6_line_106 |  | 100 | 101 | 0.026832 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
107 | LV_261-663_0_6_line_107 |  | 101 | 104 | 0.021556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
108 | LV_261-663_0_6_line_108 |  | 102 | 103 | 0.0018038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_261-663_0_6_line_109 |  | 104 | 107 | 0.016087 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
110 | LV_261-663_0_6_line_110 |  | 105 | 106 | 0.0075655 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_261-663_0_6_line_111 |  | 106 | 110 | 0.0094549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_261-663_0_6_line_112 |  | 107 | 108 | 0.019114 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
113 | LV_261-663_0_6_line_113 |  | 108 | 109 | 0.024358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
114 | LV_261-663_0_6_line_114 |  | 109 | 110 | 0.010886 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
115 | LV_261-663_0_6_line_115 |  | 112 | 124 | 0.020249 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_261-663_0_6_line_116 |  | 114 | 115 | 0.00031727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_261-663_0_6_line_117 |  | 114 | 116 | 0.010705 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_261-663_0_6_line_118 |  | 115 | 117 | 0.019231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_261-663_0_6_line_119 |  | 116 | 118 | 0.024085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_261-663_0_6_line_120 |  | 117 | 119 | 0.017353 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_261-663_0_6_line_121 |  | 119 | 125 | 0.016473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
122 | LV_261-663_0_6_line_122 |  | 119 | 126 | 0.02496 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
123 | LV_261-663_0_6_line_123 |  | 120 | 121 | 0.021413 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_261-663_0_6_line_124 |  | 120 | 122 | 0.022992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_261-663_0_6_line_125 |  | 122 | 124 | 0.019432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_261-663_0_6_line_126 |  | 123 | 124 | 0.004222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_261-663_0_6_line_127 |  | 125 | 127 | 0.010447 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
128 | LV_261-663_0_6_line_128 |  | 126 | 128 | 0.013719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
129 | LV_261-663_0_6_line_129 |  | 127 | 139 | 0.020853 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
130 | LV_261-663_0_6_line_130 |  | 128 | 132 | 0.0093327 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
131 | LV_261-663_0_6_line_131 |  | 129 | 140 | 0.003257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_261-663_0_6_line_132 |  | 130 | 131 | 0.027622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
133 | LV_261-663_0_6_line_133 |  | 131 | 132 | 0.033314 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
134 | LV_261-663_0_6_line_134 |  | 133 | 134 | 0.0063484 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_261-663_0_6_line_135 |  | 134 | 135 | 0.011385 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_261-663_0_6_line_136 |  | 136 | 137 | 0.010901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_261-663_0_6_line_137 |  | 136 | 138 | 0.010917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_261-663_0_6_line_138 |  | 137 | 139 | 0.024935 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
139 | LV_261-663_0_6_line_139 |  | 138 | 140 | 0.0066869 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-663_0_6_trafo_123 | 0.63 MVA 20/0.4 kV | 141 | 110 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2686380.1156 | 1245827.6937 | 2686390.2274 | 1245827.0293 | 2686398.8569 | 1245824.9999
1 | 2686409.049 | 1245821.3103 | 2686400.6902 | 1245824.5688 | 2686398.8569 | 1245824.9999
2 | 2686380.1156 | 1245827.6937 | 2686359.9092 | 1245828.2738
3 | 2686380.1156 | 1245827.6937 | 2686379.8955 | 1245812.1946
4 | 2686409.049 | 1245821.3103 | 2686412.0906 | 1245819.1724
5 | 2686352.6239 | 1245828.4829 | 2686359.9092 | 1245828.2738
6 | 2686379.6979 | 1245798.2881 | 2686379.8955 | 1245812.1946
7 | 2686421.9316 | 1245810.9459 | 2686415.744 | 1245816.6044 | 2686412.0906 | 1245819.1724
8 | 2686331.1866 | 1245827.5591 | 2686344.1723 | 1245828.7712 | 2686352.6239 | 1245828.4829
9 | 2686421.9316 | 1245810.9459 | 2686427.9067 | 1245804.8284 | 2686432.2634 | 1245798.1056
10 | 2686331.1866 | 1245827.5591 | 2686337.6664 | 1245815.8336
11 | 2686331.1866 | 1245827.5591 | 2686325.4998 | 1245837.9524
12 | 2686439.1222 | 1245781.0235 | 2686434.6238 | 1245794.4631 | 2686432.2634 | 1245798.1056
13 | 2686442.0979 | 1245770.9921 | 2686439.6719 | 1245779.381 | 2686439.1222 | 1245781.0235
14 | 2686442.0979 | 1245770.9921 | 2686446.5655 | 1245755.5428
15 | 2686498.5389 | 1245615.2622 | 2686502.9074 | 1245610.5224 | 2686506.5053 | 1245602.5363
16 | 2686498.5389 | 1245615.2622 | 2686493.2584 | 1245624.5032 | 2686492.0309 | 1245627.0445
17 | 2686485.6852 | 1245640.1821 | 2686492.0309 | 1245627.0445
18 | 2686485.6852 | 1245640.1821 | 2686482.6667 | 1245647.4136
19 | 2686485.6852 | 1245640.1821 | 2686502.3054 | 1245647.9903
20 | 2686467.9031 | 1245587.906 | 2686467.9137 | 1245587.9161
21 | 2686467.0233 | 1245587.0691 | 2686467.9031 | 1245587.906
22 | 2686472.0049 | 1245673.0858 | 2686472.3435 | 1245672.1446 | 2686482.6667 | 1245647.4136
23 | 2686503.1662 | 1245648.3947 | 2686502.3054 | 1245647.9903
24 | 2686451.6595 | 1245572.3805 | 2686455.355 | 1245575.9704 | 2686467.0233 | 1245587.0691
25 | 2686489.6036 | 1245532.1594 | 2686504.7311 | 1245546.5397
26 | 2686489.6036 | 1245532.1594 | 2686473.8088 | 1245548.9082
27 | 2686489.6036 | 1245532.1594 | 2686500.2251 | 1245520.6798
28 | 2686451.6595 | 1245572.3805 | 2686456.0726 | 1245567.6969 | 2686473.8088 | 1245548.9082
29 | 2686473.8088 | 1245548.9082 | 2686458.2224 | 1245533.9322
30 | 2686451.6595 | 1245572.3805 | 2686449.1795 | 1245575.0797
31 | 2686458.2224 | 1245533.9322 | 2686458.1129 | 1245533.827
32 | 2686449.1795 | 1245575.0797 | 2686444.5382 | 1245571.0647 | 2686447.41 | 1245562.7448 | 2686438.8143 | 1245554.7868
33 | 2686449.1795 | 1245575.0797 | 2686424.0695 | 1245601.4208
34 | 2686446.5655 | 1245755.5428 | 2686449.5954 | 1245745.0657
35 | 2686452.4457 | 1245735.209 | 2686449.5954 | 1245745.0657
36 | 2686406.7111 | 1245642.1772 | 2686406.6991 | 1245638.7748
37 | 2686406.686 | 1245635.0827 | 2686406.6991 | 1245638.7748
38 | 2686406.7111 | 1245642.1772 | 2686401.1665 | 1245646.2217 | 2686395.3143 | 1245653.742
39 | 2686406.7111 | 1245642.1772 | 2686406.9017 | 1245655.5343 | 2686406.5495 | 1245660.811
40 | 2686406.8857 | 1245629.6816 | 2686406.686 | 1245635.0827
41 | 2686395.3143 | 1245653.742 | 2686384.8017 | 1245648.1959
42 | 2686406.1041 | 1245667.4821 | 2686406.5495 | 1245660.811
43 | 2686406.8857 | 1245629.6816 | 2686408.1769 | 1245623.5181 | 2686409.4894 | 1245619.5232 | 2686411.8039 | 1245615.2204 | 2686415.0251 | 1245610.9086 | 2686424.0013 | 1245601.4923
44 | 2686406.8857 | 1245629.6816 | 2686393.7132 | 1245622.5846 | 2686389.0522 | 1245620.4373 | 2686387.7561 | 1245619.8405
45 | 2686379.6878 | 1245645.4972 | 2686384.8017 | 1245648.1959
46 | 2686402.1137 | 1245687.9475 | 2686404.4413 | 1245678.6711 | 2686406.0801 | 1245667.8426 | 2686406.1041 | 1245667.4821
47 | 2686424.0695 | 1245601.4208 | 2686424.0013 | 1245601.4923
48 | 2686364.5975 | 1245600.4443 | 2686367.275 | 1245602.3402 | 2686383.0177 | 1245617.6585 | 2686387.7561 | 1245619.8405
49 | 2686372.9414 | 1245682.466 | 2686372.9647 | 1245682.4361
50 | 2686363.4196 | 1245695.8198 | 2686366.0697 | 1245691.2884 | 2686372.9414 | 1245682.466
51 | 2686402.1137 | 1245687.9475 | 2686401.8422 | 1245689.0298 | 2686398.2184 | 1245699.1845 | 2686392.7092 | 1245710.6572 | 2686392.6245 | 1245710.8179
52 | 2686364.5975 | 1245600.4443 | 2686380.0041 | 1245584.9015
53 | 2686364.5975 | 1245600.4443 | 2686355.7948 | 1245594.4328
54 | 2686352.1931 | 1245591.9733 | 2686355.7948 | 1245594.4328
55 | 2686330.1887 | 1245578.5343 | 2686333.1109 | 1245580.2488 | 2686338.1275 | 1245582.3678 | 2686352.1931 | 1245591.9733
56 | 2686472.0049 | 1245673.0858 | 2686468.2041 | 1245683.6485
57 | 2686463.7175 | 1245696.2312 | 2686463.8856 | 1245695.6498 | 2686468.2041 | 1245683.6485
58 | 2686456.826 | 1245720.0621 | 2686452.4457 | 1245735.209
59 | 2686456.826 | 1245720.0621 | 2686459.7978 | 1245709.7855
60 | 2686456.826 | 1245720.0621 | 2686526.0253 | 1245736.0413
61 | 2686463.7175 | 1245696.2312 | 2686459.7978 | 1245709.7855
62 | 2686251.3936 | 1245579.1037 | 2686244.5965 | 1245586.6661 | 2686235.2265 | 1245599.1613
63 | 2686251.3936 | 1245579.1037 | 2686264.6764 | 1245587.9027
64 | 2686235.2265 | 1245599.1613 | 2686230.6818 | 1245592.6571 | 2686229.3627 | 1245585.6772 | 2686226.2459 | 1245583.2478
65 | 2686231.0189 | 1245604.8043 | 2686235.2265 | 1245599.1613
66 | 2686271.1601 | 1245587.9421 | 2686266.3764 | 1245589.0289 | 2686264.6764 | 1245587.9027
67 | 2686226.2459 | 1245583.2478 | 2686226.1501 | 1245583.1731 | 2686221.9853 | 1245584.8249 | 2686213.8237 | 1245578.1458 | 2686213.8237 | 1245578.1458
68 | 2686231.0189 | 1245604.8043 | 2686228.0156 | 1245608.9307
69 | 2686231.0189 | 1245604.8043 | 2686276.5312 | 1245633.8836
70 | 2686271.1601 | 1245587.9421 | 2686271.1601 | 1245587.9421 | 2686279.0751 | 1245593.3946 | 2686286.0477 | 1245592.9846 | 2686300.4471 | 1245602.6489
71 | 2686369.708 | 1245754.9436 | 2686363.4227 | 1245767.1726 | 2686362.4696 | 1245768.9733
72 | 2686369.708 | 1245754.9436 | 2686373.5951 | 1245747.3807
73 | 2686362.4696 | 1245768.9733 | 2686353.3032 | 1245786.2912
74 | 2686381.7711 | 1245731.4732 | 2686373.5951 | 1245747.3807
75 | 2686346.614 | 1245798.9291 | 2686353.3032 | 1245786.2912
76 | 2686381.7711 | 1245731.4732 | 2686383.2368 | 1245728.6215 | 2686385.3988 | 1245724.5212
77 | 2686337.6664 | 1245815.8336 | 2686346.614 | 1245798.9291
78 | 2686392.6245 | 1245710.8179 | 2686385.3988 | 1245724.5212
79 | 2686337.6664 | 1245815.8336 | 2686322.4631 | 1245812.6126
80 | 2686322.4631 | 1245812.6126 | 2686311.3477 | 1245810.2576 | 2686291.797 | 1245801.21
81 | 2686291.797 | 1245801.21 | 2686282.6269 | 1245796.9663
82 | 2686264.9414 | 1245788.7819 | 2686281.9136 | 1245796.6362
83 | 2686249.2044 | 1245781.4992 | 2686264.9414 | 1245788.7819
84 | 2686282.6269 | 1245796.9663 | 2686281.9136 | 1245796.6362
85 | 2686249.1266 | 1245769.1889 | 2686249.691 | 1245775.057 | 2686249.2044 | 1245781.4992
86 | 2686249.1266 | 1245769.1889 | 2686259.6954 | 1245767.7527 | 2686291.1303 | 1245768.6105 | 2686303.2435 | 1245766.4299
87 | 2686249.1266 | 1245769.1889 | 2686243.4348 | 1245762.5902 | 2686240.5621 | 1245760.6159
88 | 2686316.2796 | 1245763.1865 | 2686311.5316 | 1245764.9379 | 2686303.2435 | 1245766.4299
89 | 2686234.3603 | 1245756.3537 | 2686240.5621 | 1245760.6159
90 | 2686234.3603 | 1245756.3537 | 2686229.8598 | 1245754.6092 | 2686225.0202 | 1245754.3498
91 | 2686234.3603 | 1245756.3537 | 2686245.123 | 1245741.9411
92 | 2686225.0202 | 1245754.3498 | 2686217.2086 | 1245757.394
93 | 2686225.0202 | 1245754.3498 | 2686219.4438 | 1245736.7075
94 | 2686245.123 | 1245741.9411 | 2686254.5774 | 1245729.2805
95 | 2686217.2086 | 1245757.394 | 2686209.7696 | 1245753.5164 | 2686206.215 | 1245752.186 | 2686199.0425 | 1245749.7244 | 2686195.0187 | 1245749.3436
96 | 2686218.0408 | 1245732.2688 | 2686219.4438 | 1245736.7075
97 | 2686278.7808 | 1245705.901 | 2686276.1169 | 1245709.4262 | 2686266.825 | 1245713.9722 | 2686260.8921 | 1245720.8243 | 2686254.5774 | 1245729.2805
98 | 2686161.2016 | 1245739.5467 | 2686188.3506 | 1245748.7127 | 2686195.0187 | 1245749.3436
99 | 2686217.6297 | 1245730.9682 | 2686218.0408 | 1245732.2688
100 | 2686289.7227 | 1245691.4219 | 2686278.7808 | 1245705.901
101 | 2686363.4196 | 1245695.8198 | 2686353.7555 | 1245689.5967
102 | 2686353.7555 | 1245689.5967 | 2686348.5981 | 1245698.0153
103 | 2686353.7555 | 1245689.5967 | 2686349.096 | 1245686.5942
104 | 2686346.198 | 1245703.7083 | 2686348.158 | 1245700.9125 | 2686347.4629 | 1245699.8683 | 2686348.5981 | 1245698.0153
105 | 2686336.2241 | 1245678.2999 | 2686349.096 | 1245686.5942
106 | 2686289.7227 | 1245691.4219 | 2686295.7295 | 1245688.3181 | 2686306.6308 | 1245671.4654
107 | 2686318.6613 | 1245653.5816 | 2686311.7691 | 1245663.522 | 2686306.6308 | 1245671.4654
108 | 2686346.198 | 1245703.7083 | 2686345.176 | 1245705.1946
109 | 2686318.6613 | 1245653.5816 | 2686327.3663 | 1245640.0538 | 2686327.3663 | 1245640.0538
110 | 2686327.3665 | 1245692.8339 | 2686331.3037 | 1245686.3736
111 | 2686336.2241 | 1245678.2999 | 2686331.3037 | 1245686.3736
112 | 2686327.3663 | 1245640.0538 | 2686333.6201 | 1245644.904 | 2686336.9412 | 1245645.1414 | 2686338.9266 | 1245646.8271 | 2686339.9007 | 1245650.4995 | 2686341.0952 | 1245651.3496
113 | 2686341.0952 | 1245651.3496 | 2686342.4209 | 1245652.2931 | 2686344.1324 | 1245652.0289 | 2686345.9348 | 1245652.789 | 2686347.3238 | 1245654.9553 | 2686347.0934 | 1245657.287 | 2686346.7638 | 1245659.684 | 2686344.1443 | 1245661.5917 | 2686343.2351 | 1245666.9491 | 2686341.4996 | 1245669.4364
114 | 2686336.2241 | 1245678.2999 | 2686337.3168 | 1245676.4255 | 2686336.8376 | 1245676.1183 | 2686341.4996 | 1245669.4364
115 | 2686216.0998 | 1245625.3026 | 2686228.0156 | 1245608.9307
116 | 2686214.722 | 1245659.8371 | 2686214.9954 | 1245659.998
117 | 2686224.2207 | 1245665.428 | 2686214.9954 | 1245659.998
118 | 2686198.1491 | 1245650.0822 | 2686214.722 | 1245659.8371
119 | 2686224.2207 | 1245665.428 | 2686244.97 | 1245677.6567
120 | 2686188.0828 | 1245664.2353 | 2686198.1491 | 1245650.0822
121 | 2686188.0828 | 1245664.2353 | 2686184.3482 | 1245656.0528 | 2686180.6689 | 1245649.5423
122 | 2686188.0828 | 1245664.2353 | 2686173.6122 | 1245684.5723
123 | 2686244.7548 | 1245643.2991 | 2686249.6617 | 1245646.2059 | 2686248.4483 | 1245648.0674 | 2686259.9113 | 1245655.1748
124 | 2686244.7548 | 1245643.2991 | 2686240.5373 | 1245640.7915 | 2686238.0427 | 1245644.5024 | 2686230.5152 | 1245639.9451 | 2686232.7313 | 1245636.1635 | 2686232.37 | 1245635.9276
125 | 2686216.0998 | 1245625.3026 | 2686232.37 | 1245635.9276
126 | 2686216.0998 | 1245625.3026 | 2686213.6148 | 1245628.7158
127 | 2686177.6529 | 1245639.9881 | 2686177.328 | 1245643.6305 | 2686180.6689 | 1245649.5423
128 | 2686165.5473 | 1245695.6664 | 2686166.9708 | 1245693.9061 | 2686173.6122 | 1245684.5723
129 | 2686177.6529 | 1245639.9881 | 2686177.6529 | 1245639.9881 | 2686186.4014 | 1245626.572 | 2686183.9001 | 1245622.4326 | 2686183.9001 | 1245622.4326
130 | 2686159.6789 | 1245702.9232 | 2686165.5473 | 1245695.6664
131 | 2686210.697 | 1245579.0579 | 2686213.8237 | 1245578.1458
132 | 2686136.8982 | 1245727.1939 | 2686141.3165 | 1245730.9609 | 2686147.1542 | 1245734.804 | 2686161.2016 | 1245739.5467
133 | 2686136.8982 | 1245727.1939 | 2686154.9371 | 1245708.7868 | 2686159.6789 | 1245702.9232
134 | 2686217.6297 | 1245730.9682 | 2686215.7164 | 1245724.915
135 | 2686219.5136 | 1245714.7627 | 2686215.7913 | 1245719.7679 | 2686215.7164 | 1245724.915
136 | 2686198.5037 | 1245590.6688 | 2686192.1049 | 1245599.4945
137 | 2686198.5037 | 1245590.6688 | 2686204.9116 | 1245581.8306
138 | 2686192.1049 | 1245599.4945 | 2686191.6212 | 1245600.1617 | 2686191.1135 | 1245609.0942 | 2686183.9001 | 1245622.4326
139 | 2686204.9116 | 1245581.8306 | 2686205.9091 | 1245580.4547 | 2686210.697 | 1245579.0579

## bus_geodata
| x | y | coords
0 | 2686398.8569 | 1245824.9999
1 | 2686380.1156 | 1245827.6937
2 | 2686409.049 | 1245821.3103
3 | 2686359.9092 | 1245828.2738
4 | 2686379.8955 | 1245812.1946
5 | 2686412.0906 | 1245819.1724
6 | 2686352.6239 | 1245828.4829
7 | 2686379.6979 | 1245798.2881
8 | 2686421.9316 | 1245810.9459
9 | 2686331.1866 | 1245827.5591
10 | 2686432.2634 | 1245798.1056
11 | 2686439.1222 | 1245781.0235
12 | 2686442.0979 | 1245770.9921
13 | 2686506.5053 | 1245602.5363
14 | 2686498.5389 | 1245615.2622
15 | 2686492.0309 | 1245627.0445
16 | 2686485.6852 | 1245640.1821
17 | 2686467.9137 | 1245587.9161
18 | 2686467.9031 | 1245587.906
19 | 2686482.6667 | 1245647.4136
20 | 2686502.3054 | 1245647.9903
21 | 2686467.0233 | 1245587.0691
22 | 2686504.7311 | 1245546.5397
23 | 2686489.6036 | 1245532.1594
24 | 2686473.8088 | 1245548.9082
25 | 2686500.2251 | 1245520.6798
26 | 2686451.6595 | 1245572.3805
27 | 2686458.2224 | 1245533.9322
28 | 2686449.1795 | 1245575.0797
29 | 2686458.1129 | 1245533.827
30 | 2686446.5655 | 1245755.5428
31 | 2686449.5954 | 1245745.0657
32 | 2686406.6991 | 1245638.7748
33 | 2686406.7111 | 1245642.1772
34 | 2686406.686 | 1245635.0827
35 | 2686395.3143 | 1245653.742
36 | 2686406.5495 | 1245660.811
37 | 2686406.8857 | 1245629.6816
38 | 2686384.8017 | 1245648.1959
39 | 2686406.1041 | 1245667.4821
40 | 2686424.0013 | 1245601.4923
41 | 2686387.7561 | 1245619.8405
42 | 2686379.6878 | 1245645.4972
43 | 2686372.9647 | 1245682.4361
44 | 2686372.9414 | 1245682.466
45 | 2686402.1137 | 1245687.9475
46 | 2686424.0695 | 1245601.4208
47 | 2686364.5975 | 1245600.4443
48 | 2686380.0041 | 1245584.9015
49 | 2686355.7948 | 1245594.4328
50 | 2686352.1931 | 1245591.9733
51 | 2686330.1887 | 1245578.5343
52 | 2686472.0049 | 1245673.0858
53 | 2686503.1662 | 1245648.3947
54 | 2686468.2041 | 1245683.6485
55 | 2686452.4457 | 1245735.209
56 | 2686456.826 | 1245720.0621
57 | 2686459.7978 | 1245709.7855
58 | 2686526.0253 | 1245736.0413
59 | 2686463.7175 | 1245696.2312
60 | 2686438.8143 | 1245554.7868
61 | 2686251.3936 | 1245579.1037
62 | 2686235.2265 | 1245599.1613
63 | 2686264.6764 | 1245587.9027
64 | 2686226.2459 | 1245583.2478
65 | 2686231.0189 | 1245604.8043
66 | 2686271.1601 | 1245587.9421
67 | 2686369.708 | 1245754.9436
68 | 2686362.4696 | 1245768.9733
69 | 2686373.5951 | 1245747.3807
70 | 2686353.3032 | 1245786.2912
71 | 2686381.7711 | 1245731.4732
72 | 2686346.614 | 1245798.9291
73 | 2686385.3988 | 1245724.5212
74 | 2686337.6664 | 1245815.8336
75 | 2686392.6245 | 1245710.8179
76 | 2686325.4998 | 1245837.9524
77 | 2686322.4631 | 1245812.6126
78 | 2686291.797 | 1245801.21
79 | 2686264.9414 | 1245788.7819
80 | 2686281.9136 | 1245796.6362
81 | 2686249.2044 | 1245781.4992
82 | 2686282.6269 | 1245796.9663
83 | 2686249.1266 | 1245769.1889
84 | 2686303.2435 | 1245766.4299
85 | 2686240.5621 | 1245760.6159
86 | 2686316.2796 | 1245763.1865
87 | 2686234.3603 | 1245756.3537
88 | 2686225.0202 | 1245754.3498
89 | 2686245.123 | 1245741.9411
90 | 2686217.2086 | 1245757.394
91 | 2686219.4438 | 1245736.7075
92 | 2686254.5774 | 1245729.2805
93 | 2686195.0187 | 1245749.3436
94 | 2686218.0408 | 1245732.2688
95 | 2686278.7808 | 1245705.901
96 | 2686363.4196 | 1245695.8198
97 | 2686353.7555 | 1245689.5967
98 | 2686348.5981 | 1245698.0153
99 | 2686349.096 | 1245686.5942
100 | 2686289.7227 | 1245691.4219
101 | 2686306.6308 | 1245671.4654
102 | 2686346.198 | 1245703.7083
103 | 2686345.176 | 1245705.1946
104 | 2686318.6613 | 1245653.5816
105 | 2686327.3665 | 1245692.8339
106 | 2686331.3037 | 1245686.3736
107 | 2686327.3663 | 1245640.0538
108 | 2686341.0952 | 1245651.3496
109 | 2686341.4996 | 1245669.4364
110 | 2686336.2241 | 1245678.2999
111 | 2686276.5312 | 1245633.8836
112 | 2686228.0156 | 1245608.9307
113 | 2686300.4471 | 1245602.6489
114 | 2686214.9954 | 1245659.998
115 | 2686214.722 | 1245659.8371
116 | 2686224.2207 | 1245665.428
117 | 2686198.1491 | 1245650.0822
118 | 2686244.97 | 1245677.6567
119 | 2686188.0828 | 1245664.2353
120 | 2686244.7548 | 1245643.2991
121 | 2686259.9113 | 1245655.1748
122 | 2686232.37 | 1245635.9276
123 | 2686213.6148 | 1245628.7158
124 | 2686216.0998 | 1245625.3026
125 | 2686180.6689 | 1245649.5423
126 | 2686173.6122 | 1245684.5723
127 | 2686177.6529 | 1245639.9881
128 | 2686165.5473 | 1245695.6664
129 | 2686213.8237 | 1245578.1458
130 | 2686161.2016 | 1245739.5467
131 | 2686136.8982 | 1245727.1939
132 | 2686159.6789 | 1245702.9232
133 | 2686217.6297 | 1245730.9682
134 | 2686215.7164 | 1245724.915
135 | 2686219.5136 | 1245714.7627
136 | 2686198.5037 | 1245590.6688
137 | 2686192.1049 | 1245599.4945
138 | 2686204.9116 | 1245581.8306
139 | 2686183.9001 | 1245622.4326
140 | 2686210.697 | 1245579.0579
141 | 2686353.7555 | 1245689.5967

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97635 | -0.45335 | 0.0024475 | 0.00061341
1 | 0.97661 | -0.44831 | 0 | 0
2 | 0.97621 | -0.45611 | 0 | 0
3 | 0.97691 | -0.44237 | 0.0028822 | 0.00072235
4 | 0.97652 | -0.45006 | 0.0027876 | 0.00069863
5 | 0.97616 | -0.45706 | 0.0013398 | 0.00033578
6 | 0.97702 | -0.44014 | 0 | 0
7 | 0.97647 | -0.45092 | 0.0034008 | 0.00085232
8 | 0.976 | -0.46025 | 0 | 0
9 | 0.97736 | -0.43357 | 0 | 0
10 | 0.97558 | -0.46848 | 0.0026224 | 0.00065723
11 | 0.97469 | -0.48602 | 0.0025475 | 0.00063845
12 | 0.97421 | -0.49545 | 0.0042492 | 0.0010649
13 | 0.97075 | -0.56375 | 0.0012531 | 0.00031407
14 | 0.97077 | -0.5634 | 0 | 0
15 | 0.97078 | -0.56309 | 0.0029151 | 0.0007306
16 | 0.97084 | -0.56196 | 0 | 0
17 | 0.97158 | -0.5473 | 0.00075923 | 0.00019028
18 | 0.97158 | -0.5473 | 0.00075783 | 0.00018993
19 | 0.97091 | -0.56045 | 0.003996 | 0.0010015
20 | 0.97073 | -0.56409 | 0.0019482 | 0.00048825
21 | 0.97158 | -0.54726 | 0.0011982 | 0.00030031
22 | 0.97129 | -0.55312 | 0.0014914 | 0.00037377
23 | 0.97131 | -0.55254 | 0 | 0
24 | 0.97138 | -0.55116 | 0 | 0
25 | 0.97129 | -0.55305 | 0.0017584 | 0.0004407
26 | 0.97164 | -0.5462 | 0 | 0
27 | 0.97128 | -0.55319 | 0.0025833 | 0.00064745
28 | 0.97167 | -0.54545 | 0 | 0
29 | 0.97128 | -0.5532 | 0.0024997 | 0.00062649
30 | 0.97353 | -0.50872 | 0.0059411 | 0.001489
31 | 0.97314 | -0.51653 | 0.0026125 | 0.00065475
32 | 0.97326 | -0.51413 | 0.0038343 | 0.00096097
33 | 0.97343 | -0.51073 | 0 | 0
34 | 0.97308 | -0.51756 | 0 | 0
35 | 0.97319 | -0.51542 | 0 | 0
36 | 0.97404 | -0.49875 | 0.0014509 | 0.00036363
37 | 0.97283 | -0.52258 | 0 | 0
38 | 0.97302 | -0.51882 | 0 | 0
39 | 0.97419 | -0.49583 | 0.0010995 | 0.00027555
40 | 0.97218 | -0.53545 | 0.0017787 | 0.00044578
41 | 0.97223 | -0.53439 | 0.0033218 | 0.00083253
42 | 0.97294 | -0.52048 | 0.015578 | 0.0039043
43 | 0.99948 | -0.010075 | 0.0068248 | 0.0017104
44 | 0.99948 | -0.010071 | 0.0025936 | 0.00065002
45 | 0.97466 | -0.48658 | 0.0033745 | 0.00084572
46 | 0.97218 | -0.53549 | 0.0040603 | 0.0010176
47 | 0.97148 | -0.54927 | 0 | 0
48 | 0.97133 | -0.55215 | 0.0071375 | 0.0017888
49 | 0.97129 | -0.55308 | 0.0068892 | 0.0017266
50 | 0.97124 | -0.55408 | 0.0061721 | 0.0015469
51 | 0.97109 | -0.55707 | 0.0062644 | 0.00157
52 | 0.97129 | -0.55302 | 0.0028245 | 0.00070787
53 | 0.97073 | -0.56417 | 0.0043313 | 0.0010855
54 | 0.97147 | -0.54944 | 0.0028459 | 0.00071324
55 | 0.97279 | -0.52339 | 0.003244 | 0.00081302
56 | 0.9723 | -0.53301 | 0.0030096 | 0.00075426
57 | 0.97203 | -0.53836 | 0.0036273 | 0.0009091
58 | 0.97211 | -0.53684 | 0.0029303 | 0.0007344
59 | 0.97172 | -0.54448 | 0.0033933 | 0.00085044
60 | 0.97158 | -0.54731 | 0.0037845 | 0.00094848
61 | 0.97105 | -0.55758 | 0 | 0
62 | 0.97154 | -0.54795 | 0 | 0
63 | 0.97075 | -0.56354 | 0.0089357 | 0.0022395
64 | 0.97255 | -0.5281 | 0.001772 | 0.00044411
65 | 0.9713 | -0.55268 | 0 | 0
66 | 0.97068 | -0.56499 | 0.0038398 | 0.00096235
67 | 0.97607 | -0.45885 | 0.0024606 | 0.00061667
68 | 0.9764 | -0.45227 | 0.0028995 | 0.00072668
69 | 0.97589 | -0.4623 | 0.0023704 | 0.00059408
70 | 0.97683 | -0.44385 | 0.001224 | 0.00030677
71 | 0.97553 | -0.46937 | 0.0043177 | 0.0010821
72 | 0.97715 | -0.43762 | 0.0040406 | 0.0010127
73 | 0.97538 | -0.47232 | 0.0025632 | 0.00064241
74 | 0.97759 | -0.42896 | 0 | 0
75 | 0.9751 | -0.47796 | 0.0036563 | 0.00091636
76 | 0.97727 | -0.43537 | 0.0083309 | 0.0020879
77 | 0.97823 | -0.41657 | 0.001301 | 0.00032605
78 | 0.97958 | -0.39021 | 0.0016465 | 0.00041264
79 | 0.98082 | -0.36603 | 0.0020309 | 0.00050899
80 | 0.98003 | -0.38142 | 0.0018492 | 0.00046346
81 | 0.98156 | -0.35162 | 0 | 0
82 | 0.98 | -0.38206 | 0.0018494 | 0.00046351
83 | 0.98209 | -0.34137 | 0 | 0
84 | 0.98173 | -0.34839 | 0.002276 | 0.00057042
85 | 0.98263 | -0.33086 | 0.0026812 | 0.00067197
86 | 0.98167 | -0.34958 | 0.0048614 | 0.0012184
87 | 0.98297 | -0.3243 | 0 | 0
88 | 0.98263 | -0.33078 | 0 | 0
89 | 0.9844 | -0.29658 | 0.0050581 | 0.0012677
90 | 0.98237 | -0.33594 | 0 | 0
91 | 0.98243 | -0.33487 | 0.0010311 | 0.00025843
92 | 0.98568 | -0.27193 | 0.0015339 | 0.00038444
93 | 0.98161 | -0.35063 | 0.0012456 | 0.00031218
94 | 0.98238 | -0.33581 | 0.0019226 | 0.00048186
95 | 0.98847 | -0.21829 | 0.002615 | 0.00065539
96 | 0.99962 | -0.0073705 | 0 | 0
97 | 0.99971 | -0.0054863 | 0 | 0
98 | 0.99968 | -0.0061556 | 0.0024577 | 0.00061596
99 | 0.99978 | -0.0042 | 0.002426 | 0.00060801
100 | 0.98996 | -0.18989 | 0 | 0
101 | 0.99215 | -0.14805 | 0.0091767 | 0.0022999
102 | 0.99967 | -0.0063261 | 0 | 0
103 | 0.99967 | -0.0063711 | 0.0014291 | 0.00035816
104 | 0.99396 | -0.1137 | 0 | 0
105 | 0.99994 | -0.0011484 | 0.0025046 | 0.00062771
106 | 0.99996 | -0.00081805 | 0.0024589 | 0.00061626
107 | 0.99531 | -0.088142 | 0.0076249 | 0.001911
108 | 0.99695 | -0.057231 | 0.0024589 | 0.00061626
109 | 0.99905 | -0.017722 | 0.0025057 | 0.00062799
110 | 1 | 0 | -0.40395 | -0.10407
111 | 0.97092 | -0.56024 | 0.0075758 | 0.0018987
112 | 0.97116 | -0.5554 | 0.004208 | 0.0010546
113 | 0.97044 | -0.56967 | 0.0074536 | 0.001868
114 | 0.97625 | -0.45529 | 0.0091487 | 0.0022929
115 | 0.97626 | -0.45519 | 0.011982 | 0.003003
116 | 0.97618 | -0.45669 | 0 | 0
117 | 0.97677 | -0.44524 | 0 | 0
118 | 0.97602 | -0.45985 | 0.0071702 | 0.001797
119 | 0.97722 | -0.43627 | 0 | 0
120 | 0.97025 | -0.57353 | 0 | 0
121 | 0.97009 | -0.57663 | 0.0078224 | 0.0019605
122 | 0.97042 | -0.5702 | 0.0076763 | 0.0019239
123 | 0.97066 | -0.56534 | 0.0091337 | 0.0022891
124 | 0.9707 | -0.56462 | 0 | 0
125 | 0.97687 | -0.44313 | 0.0068626 | 0.0017199
126 | 0.97792 | -0.42267 | 0.008703 | 0.0021812
127 | 0.97667 | -0.44716 | 0.0063717 | 0.0015969
128 | 0.97833 | -0.41465 | 0.0024468 | 0.00061323
129 | 0.97337 | -0.51181 | 0.0019473 | 0.00048804
130 | 0.9805 | -0.3723 | 0.0023724 | 0.00059457
131 | 0.97964 | -0.38897 | 0 | 0
132 | 0.97861 | -0.4091 | 0.0022895 | 0.0005738
133 | 0.98237 | -0.33604 | 0.001833 | 0.0004594
134 | 0.98232 | -0.3369 | 0.0011328 | 0.00028391
135 | 0.98226 | -0.3382 | 0.0063281 | 0.001586
136 | 0.97462 | -0.48736 | 0.0032214 | 0.00080736
137 | 0.97532 | -0.47358 | 0.0033762 | 0.00084615
138 | 0.97395 | -0.50054 | 0.003449 | 0.0008644
139 | 0.97616 | -0.45707 | 0.0056773 | 0.0014229
140 | 0.97356 | -0.50819 | 0.001904 | 0.0004772
141 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.058283 | -0.014681 | 0.058297 | 0.014689 | 1.4062e-05 | 8.0488e-06 | 0.088853 | 0.088853 | 0.088853 | 0.97635 | -0.45335 | 0.97661 | -0.44831 | 6.1026
1 | 0.055835 | 0.014068 | -0.055828 | -0.014063 | 7.3737e-06 | 4.1763e-06 | 0.085123 | 0.085123 | 0.085123 | 0.97635 | -0.45335 | 0.97621 | -0.45611 | 5.8464
2 | -0.064486 | -0.01624 | 0.064504 | 0.016251 | 1.8306e-05 | 1.0704e-05 | 0.098283 | 0.098283 | 0.098283 | 0.97661 | -0.44831 | 0.97691 | -0.44237 | 6.7502
3 | 0.006189 | 0.001551 | -0.0061885 | -0.0015509 | 5.1689e-07 | 1.3688e-07 | 0.00943 | 0.00943 | 0.00943 | 0.97661 | -0.44831 | 0.97652 | -0.45006 | 2.5907
4 | 0.055828 | 0.014063 | -0.055825 | -0.014062 | 2.5256e-06 | 1.4304e-06 | 0.085123 | 0.085123 | 0.085123 | 0.97621 | -0.45611 | 0.97616 | -0.45706 | 5.8464
5 | -0.067386 | -0.016973 | 0.067394 | 0.016977 | 7.2029e-06 | 4.2448e-06 | 0.10267 | 0.10267 | 0.10267 | 0.97691 | -0.44237 | 0.97702 | -0.44014 | 7.0517
6 | 0.0034009 | 0.00085224 | -0.0034008 | -0.00085232 | 1.4007e-07 | -8.4341e-08 | 0.0051823 | 0.0051824 | 0.0051824 | 0.97652 | -0.45006 | 0.97647 | -0.45092 | 1.4237
7 | 0.054486 | 0.013726 | -0.054477 | -0.013722 | 8.3156e-06 | 4.6795e-06 | 0.083081 | 0.083081 | 0.083081 | 0.97616 | -0.45706 | 0.976 | -0.46025 | 5.7061
8 | -0.067394 | -0.016977 | 0.067415 | 0.01699 | 2.1184e-05 | 1.2483e-05 | 0.10267 | 0.10267 | 0.10267 | 0.97702 | -0.44014 | 0.97736 | -0.43357 | 7.0517
9 | 0.054477 | 0.013722 | -0.054456 | -0.013708 | 2.1435e-05 | 1.3305e-05 | 0.083081 | 0.083081 | 0.083081 | 0.976 | -0.46025 | 0.97558 | -0.46848 | 11.4123
10 | -0.075746 | -0.019078 | 0.075763 | 0.019088 | 1.6703e-05 | 1.0019e-05 | 0.11536 | 0.11536 | 0.11536 | 0.97736 | -0.43357 | 0.97759 | -0.42896 | 7.9229
11 | 0.0083317 | 0.0020882 | -0.0083309 | -0.0020879 | 7.1488e-07 | 3.0906e-07 | 0.012685 | 0.012685 | 0.012685 | 0.97736 | -0.43357 | 0.97727 | -0.43537 | 3.4849
12 | 0.051833 | 0.013051 | -0.05179 | -0.013023 | 4.3416e-05 | 2.7556e-05 | 0.079082 | 0.079082 | 0.079082 | 0.97558 | -0.46848 | 0.97469 | -0.48602 | 21.7257
13 | 0.049243 | 0.012385 | -0.04922 | -0.012371 | 2.2187e-05 | 1.407e-05 | 0.075193 | 0.075193 | 0.075193 | 0.97469 | -0.48602 | 0.97421 | -0.49545 | 20.6573
14 | 0.044971 | 0.011306 | -0.044943 | -0.011288 | 2.8466e-05 | 1.8018e-05 | 0.068702 | 0.068702 | 0.068702 | 0.97421 | -0.49545 | 0.97353 | -0.50872 | 18.8743
15 | -0.0012531 | -0.00031407 | 0.0012532 | 0.00031389 | 2.1038e-08 | -1.7452e-07 | 0.0019209 | 0.0019208 | 0.0019209 | 0.97075 | -0.56375 | 0.97077 | -0.5634 | 0.52771
16 | -0.0012532 | -0.00031389 | 0.0012532 | 0.00031374 | 1.863e-08 | -1.5456e-07 | 0.0019208 | 0.0019208 | 0.0019208 | 0.97077 | -0.5634 | 0.97078 | -0.56309 | 0.5277
17 | -0.0041683 | -0.0010443 | 0.0041685 | 0.0010443 | 2.2334e-07 | -3.7463e-08 | 0.0063891 | 0.006389 | 0.0063891 | 0.97078 | -0.56309 | 0.97084 | -0.56196 | 1.7552
18 | -0.010449 | -0.0026183 | 0.010449 | 0.0026187 | 7.5365e-07 | 3.8543e-07 | 0.016015 | 0.016015 | 0.016015 | 0.97084 | -0.56196 | 0.97091 | -0.56045 | 4.3996
19 | 0.0062802 | 0.001574 | -0.0062795 | -0.0015738 | 6.3803e-07 | 1.813e-07 | 0.0096257 | 0.0096258 | 0.0096258 | 0.97084 | -0.56196 | 0.97073 | -0.56409 | 2.6444
20 | -0.00075923 | -0.00019028 | 0.00075923 | 0.00019028 | 5.7765e-12 | -1.7194e-10 | 0.0011628 | 0.0011628 | 0.0011628 | 0.97158 | -0.5473 | 0.97158 | -0.5473 | 0.31945
21 | -0.0015171 | -0.00038021 | 0.0015171 | 0.0003802 | 2.458e-09 | -1.3464e-08 | 0.0023234 | 0.0023234 | 0.0023234 | 0.97158 | -0.5473 | 0.97158 | -0.54726 | 0.63831
22 | -0.014445 | -0.0036202 | 0.014451 | 0.0036231 | 5.1095e-06 | 2.9261e-06 | 0.022139 | 0.022139 | 0.022139 | 0.97091 | -0.56045 | 0.97129 | -0.55302 | 6.0821
23 | 0.0043314 | 0.0010855 | -0.0043313 | -0.0010855 | 1.5722e-08 | -1.6954e-09 | 0.0066395 | 0.0066395 | 0.0066395 | 0.97073 | -0.56409 | 0.97073 | -0.56417 | 1.824
24 | -0.0027153 | -0.00068051 | 0.0027154 | 0.00068033 | 1.3785e-07 | -1.7503e-07 | 0.0041586 | 0.0041585 | 0.0041586 | 0.97158 | -0.54726 | 0.97164 | -0.5462 | 1.1425
25 | -0.0014914 | -0.00037377 | 0.0014914 | 0.00037354 | 4.0856e-08 | -2.3218e-07 | 0.0022848 | 0.0022847 | 0.0022848 | 0.97129 | -0.55312 | 0.97131 | -0.55254 | 0.62769
26 | -0.0032499 | -0.00081408 | 0.0032501 | 0.00081393 | 2.137e-07 | -1.4784e-07 | 0.0049785 | 0.0049784 | 0.0049785 | 0.97131 | -0.55254 | 0.97138 | -0.55116 | 1.3677
27 | 0.0017585 | 0.00044054 | -0.0017584 | -0.0004407 | 4.2561e-08 | -1.6633e-07 | 0.0026938 | 0.0026939 | 0.0026939 | 0.97131 | -0.55254 | 0.97129 | -0.55305 | 0.74009
28 | -0.0083337 | -0.0020879 | 0.0083356 | 0.0020888 | 1.9697e-06 | 8.615e-07 | 0.012766 | 0.012766 | 0.012766 | 0.97138 | -0.55116 | 0.97164 | -0.5462 | 3.5071
29 | 0.0050836 | 0.001274 | -0.0050831 | -0.0012739 | 4.9155e-07 | 4.7038e-08 | 0.0077872 | 0.0077873 | 0.0077873 | 0.97138 | -0.55116 | 0.97128 | -0.55319 | 2.1394
30 | -0.011051 | -0.0027691 | 0.011051 | 0.0027693 | 3.9322e-07 | 2.0632e-07 | 0.016924 | 0.016924 | 0.016924 | 0.97164 | -0.5462 | 0.97167 | -0.54545 | 4.6495
31 | 0.0024997 | 0.00062649 | -0.0024997 | -0.00062649 | 8.3429e-10 | -1.3439e-09 | 0.0038296 | 0.0038296 | 0.0038296 | 0.97128 | -0.55319 | 0.97128 | -0.5532 | 1.0521
32 | 0.0037848 | 0.00094836 | -0.0037845 | -0.00094848 | 3.3576e-07 | -1.1521e-07 | 0.005796 | 0.0057961 | 0.0057961 | 0.97167 | -0.54545 | 0.97158 | -0.54731 | 1.5923
33 | -0.014836 | -0.0037177 | 0.014843 | 0.0037217 | 7.0445e-06 | 4.0574e-06 | 0.02272 | 0.02272 | 0.02272 | 0.97167 | -0.54545 | 0.97218 | -0.53549 | 6.2418
34 | 0.039002 | 0.009799 | -0.038987 | -0.0097898 | 1.4539e-05 | 9.1691e-06 | 0.059622 | 0.059622 | 0.059622 | 0.97353 | -0.50872 | 0.97314 | -0.51653 | 16.3796
35 | 0.036375 | 0.0091351 | -0.036363 | -0.0091276 | 1.1906e-05 | 7.4925e-06 | 0.055627 | 0.055627 | 0.055627 | 0.97314 | -0.51653 | 0.97279 | -0.52339 | 15.2821
36 | -0.054376 | -0.013657 | 0.054385 | 0.013662 | 8.8209e-06 | 5.6031e-06 | 0.083146 | 0.083146 | 0.083146 | 0.97326 | -0.51413 | 0.97343 | -0.51073 | 22.8424
37 | 0.050542 | 0.012696 | -0.050534 | -0.012691 | 8.2695e-06 | 5.2466e-06 | 0.077284 | 0.077284 | 0.077284 | 0.97326 | -0.51413 | 0.97308 | -0.51756 | 21.2319
38 | 0.015586 | 0.0039085 | -0.015582 | -0.0039065 | 3.4847e-06 | 2.0268e-06 | 0.023826 | 0.023826 | 0.023826 | 0.97343 | -0.51073 | 0.97319 | -0.51542 | 6.5455
39 | -0.069971 | -0.017571 | 0.070011 | 0.017596 | 4.0008e-05 | 2.5141e-05 | 0.10697 | 0.10697 | 0.10697 | 0.97343 | -0.51073 | 0.97404 | -0.49875 | 14.6939
40 | 0.050534 | 0.012691 | -0.050522 | -0.012683 | 1.2106e-05 | 7.6808e-06 | 0.077284 | 0.077284 | 0.077284 | 0.97308 | -0.51756 | 0.97283 | -0.52258 | 21.2319
41 | 0.015582 | 0.0039065 | -0.01558 | -0.003905 | 2.5242e-06 | 1.4682e-06 | 0.023826 | 0.023826 | 0.023826 | 0.97319 | -0.51542 | 0.97302 | -0.51882 | 6.5455
42 | -0.071462 | -0.01796 | 0.071472 | 0.017966 | 9.9638e-06 | 6.1271e-06 | 0.10919 | 0.10919 | 0.10919 | 0.97404 | -0.49875 | 0.97419 | -0.49583 | 9.9989
43 | 0.020695 | 0.0051928 | -0.020682 | -0.0051851 | 1.2695e-05 | 7.7055e-06 | 0.031657 | 0.031657 | 0.031657 | 0.97283 | -0.52258 | 0.97218 | -0.53545 | 8.697
44 | 0.029827 | 0.00749 | -0.02981 | -0.0074795 | 1.6802e-05 | 1.0486e-05 | 0.045627 | 0.045627 | 0.045627 | 0.97283 | -0.52258 | 0.97223 | -0.53439 | 12.535
45 | 0.01558 | 0.003905 | -0.015578 | -0.0039043 | 1.2281e-06 | 7.1431e-07 | 0.023826 | 0.023826 | 0.023826 | 0.97302 | -0.51882 | 0.97294 | -0.52048 | 6.5455
46 | -0.072571 | -0.018241 | 0.072603 | 0.018261 | 3.2077e-05 | 1.9749e-05 | 0.11087 | 0.11087 | 0.11087 | 0.97419 | -0.49583 | 0.97466 | -0.48658 | 10.1527
47 | 0.018904 | 0.0047394 | -0.018904 | -0.0047393 | 3.1037e-08 | 1.8638e-08 | 0.028935 | 0.028935 | 0.028935 | 0.97218 | -0.53545 | 0.97218 | -0.53549 | 7.9491
48 | 0.026488 | 0.006647 | -0.026469 | -0.0066353 | 1.8778e-05 | 1.164e-05 | 0.040543 | 0.040543 | 0.040543 | 0.97223 | -0.53439 | 0.97148 | -0.54927 | 11.1383
49 | -0.0068248 | -0.0017104 | 0.0068248 | 0.0017105 | 1.4678e-09 | 4.4131e-10 | 0.010161 | 0.010161 | 0.010161 | 0.99948 | -0.010075 | 0.99948 | -0.010071 | 2.7914
50 | -0.0094184 | -0.0023605 | 0.0094196 | 0.002361 | 1.2116e-06 | 5.6002e-07 | 0.014022 | 0.014022 | 0.014022 | 0.99948 | -0.010071 | 0.99962 | -0.0073705 | 3.8522
51 | -0.075978 | -0.019107 | 0.076009 | 0.019126 | 3.1303e-05 | 1.8797e-05 | 0.11602 | 0.11602 | 0.11602 | 0.97466 | -0.48658 | 0.9751 | -0.47796 | 7.9683
52 | 0.0071384 | 0.0017892 | -0.0071375 | -0.0017888 | 9.7982e-07 | 3.5652e-07 | 0.010934 | 0.010934 | 0.010934 | 0.97148 | -0.54927 | 0.97133 | -0.55215 | 3.0039
53 | 0.019331 | 0.0048462 | -0.019327 | -0.0048441 | 3.5045e-06 | 2.1109e-06 | 0.029609 | 0.029609 | 0.029609 | 0.97148 | -0.54927 | 0.97129 | -0.55308 | 8.1345
54 | 0.012438 | 0.0031175 | -0.012437 | -0.0031171 | 5.9385e-07 | 3.2609e-07 | 0.019055 | 0.019055 | 0.019055 | 0.97129 | -0.55308 | 0.97124 | -0.55408 | 5.2349
55 | 0.0062653 | 0.0015703 | -0.0062644 | -0.00157 | 8.9376e-07 | 2.5195e-07 | 0.009599 | 0.0095991 | 0.0095991 | 0.97124 | -0.55408 | 0.97109 | -0.55707 | 2.6371
56 | -0.017275 | -0.004331 | 0.017278 | 0.0043327 | 2.9486e-06 | 1.7481e-06 | 0.026466 | 0.026466 | 0.026466 | 0.97129 | -0.55302 | 0.97147 | -0.54944 | 7.2708
57 | -0.020124 | -0.0050459 | 0.020129 | 0.0050488 | 4.7603e-06 | 2.8811e-06 | 0.030825 | 0.030825 | 0.030825 | 0.97147 | -0.54944 | 0.97172 | -0.54448 | 8.4684
58 | 0.033119 | 0.0083145 | -0.033103 | -0.008305 | 1.5178e-05 | 9.5181e-06 | 0.050665 | 0.050665 | 0.050665 | 0.97279 | -0.52339 | 0.9723 | -0.53301 | 13.9189
59 | 0.027163 | 0.0068169 | -0.027156 | -0.0068126 | 6.9336e-06 | 4.3049e-06 | 0.041574 | 0.041574 | 0.041574 | 0.9723 | -0.53301 | 0.97203 | -0.53836 | 11.4214
60 | 0.0029308 | 0.00073387 | -0.0029303 | -0.0007344 | 5.3579e-07 | -5.3776e-07 | 0.0044851 | 0.0044854 | 0.0044854 | 0.9723 | -0.53301 | 0.97211 | -0.53684 | 1.2323
61 | 0.023529 | 0.0059035 | -0.023522 | -0.0058993 | 6.8653e-06 | 4.219e-06 | 0.036021 | 0.036021 | 0.036021 | 0.97203 | -0.53836 | 0.97172 | -0.54448 | 9.8959
62 | -0.020237 | -0.0050744 | 0.020247 | 0.0050801 | 9.29e-06 | 5.6268e-06 | 0.031012 | 0.031012 | 0.031012 | 0.97105 | -0.55758 | 0.97154 | -0.54795 | 8.5198
63 | 0.020237 | 0.0050744 | -0.020232 | -0.0050709 | 5.7462e-06 | 3.4805e-06 | 0.031012 | 0.031012 | 0.031012 | 0.97105 | -0.55758 | 0.97075 | -0.56354 | 8.5198
64 | -0.056695 | -0.014226 | 0.056749 | 0.01426 | 5.3703e-05 | 3.4134e-05 | 0.08684 | 0.08684 | 0.08684 | 0.97154 | -0.54795 | 0.97255 | -0.5281 | 23.8572
65 | 0.036448 | 0.0091455 | -0.03644 | -0.0091404 | 8.2191e-06 | 5.1731e-06 | 0.055828 | 0.055828 | 0.055828 | 0.97154 | -0.54795 | 0.9713 | -0.55268 | 15.3375
66 | 0.011296 | 0.0028315 | -0.011295 | -0.002831 | 7.8079e-07 | 4.1385e-07 | 0.017315 | 0.017315 | 0.017315 | 0.97075 | -0.56354 | 0.97068 | -0.56499 | 4.7569
67 | -0.058521 | -0.014704 | 0.058566 | 0.014733 | 4.5555e-05 | 2.8967e-05 | 0.089551 | 0.089551 | 0.089551 | 0.97255 | -0.5281 | 0.97337 | -0.51181 | 24.602
68 | 0.028862 | 0.0072406 | -0.028858 | -0.0072383 | 3.7421e-06 | 2.3318e-06 | 0.044218 | 0.044218 | 0.044218 | 0.9713 | -0.55268 | 0.97116 | -0.5554 | 12.1479
69 | 0.0075785 | 0.0018998 | -0.0075758 | -0.0018987 | 2.7302e-06 | 1.0791e-06 | 0.01161 | 0.011611 | 0.011611 | 0.9713 | -0.55268 | 0.97092 | -0.56024 | 3.1897
70 | 0.0074552 | 0.0018687 | -0.0074536 | -0.001868 | 1.6623e-06 | 6.4447e-07 | 0.011429 | 0.011429 | 0.011429 | 0.97068 | -0.56499 | 0.97044 | -0.56967 | 3.1398
71 | -0.091454 | -0.023024 | 0.091483 | 0.023042 | 2.8785e-05 | 1.7633e-05 | 0.13946 | 0.13946 | 0.13946 | 0.97607 | -0.45885 | 0.9764 | -0.45227 | 9.5782
72 | 0.088994 | 0.022407 | -0.088979 | -0.022398 | 1.4681e-05 | 8.9711e-06 | 0.13571 | 0.13571 | 0.13571 | 0.97607 | -0.45885 | 0.97589 | -0.4623 | 9.3206
73 | -0.094382 | -0.023768 | 0.09442 | 0.023792 | 3.8026e-05 | 2.3356e-05 | 0.14388 | 0.14388 | 0.14388 | 0.9764 | -0.45227 | 0.97683 | -0.44385 | 9.8817
74 | 0.086609 | 0.021804 | -0.086579 | -0.021786 | 2.9258e-05 | 1.7832e-05 | 0.13209 | 0.13209 | 0.13209 | 0.97589 | -0.4623 | 0.97553 | -0.46937 | 9.0724
75 | -0.095644 | -0.024098 | 0.095673 | 0.024116 | 2.8474e-05 | 1.7507e-05 | 0.14574 | 0.14574 | 0.14574 | 0.97683 | -0.44385 | 0.97715 | -0.43762 | 10.0097
76 | 0.082262 | 0.020704 | -0.08225 | -0.020697 | 1.158e-05 | 7.0199e-06 | 0.12551 | 0.12551 | 0.12551 | 0.97553 | -0.46937 | 0.97538 | -0.47232 | 8.6201
77 | -0.099714 | -0.025129 | 0.099755 | 0.025154 | 4.137e-05 | 2.5518e-05 | 0.15189 | 0.15189 | 0.15189 | 0.97715 | -0.43762 | 0.97759 | -0.42896 | 10.4323
78 | 0.079687 | 0.020055 | -0.079665 | -0.020042 | 2.1475e-05 | 1.2971e-05 | 0.1216 | 0.1216 | 0.1216 | 0.97538 | -0.47232 | 0.9751 | -0.47796 | 8.3515
79 | -0.17552 | -0.044242 | 0.17562 | 0.044308 | 0.00010406 | 6.5818e-05 | 0.26725 | 0.26725 | 0.26725 | 0.97759 | -0.42896 | 0.97823 | -0.41657 | 18.3552
80 | -0.17692 | -0.044634 | 0.17715 | 0.044776 | 0.0002236 | 0.00014145 | 0.26923 | 0.26923 | 0.26923 | 0.97823 | -0.41657 | 0.97958 | -0.39021 | 18.4911
81 | -0.17879 | -0.045188 | 0.17886 | 0.045233 | 6.9945e-05 | 4.4256e-05 | 0.27173 | 0.27173 | 0.27173 | 0.97958 | -0.39021 | 0.98 | -0.38206 | 18.6628
82 | 0.1827 | 0.046248 | -0.18257 | -0.046163 | 0.00013486 | 8.5368e-05 | 0.27735 | 0.27735 | 0.27735 | 0.98082 | -0.36603 | 0.98003 | -0.38142 | 19.0485
83 | -0.18473 | -0.046757 | 0.18486 | 0.046838 | 0.00012784 | 8.0942e-05 | 0.28043 | 0.28043 | 0.28043 | 0.98082 | -0.36603 | 0.98156 | -0.35162 | 19.2601
84 | 0.18072 | 0.0457 | -0.18071 | -0.045696 | 5.5544e-06 | 3.5152e-06 | 0.27454 | 0.27454 | 0.27454 | 0.98003 | -0.38142 | 0.98 | -0.38206 | 18.8556
85 | -0.18486 | -0.046838 | 0.18495 | 0.046896 | 9.1101e-05 | 5.7679e-05 | 0.28043 | 0.28043 | 0.28043 | 0.98156 | -0.35162 | 0.98209 | -0.34137 | 19.26
86 | 0.00714 | 0.0017896 | -0.0071376 | -0.0017888 | 2.3885e-06 | 8.4027e-07 | 0.010818 | 0.010819 | 0.010819 | 0.98209 | -0.34137 | 0.98173 | -0.34839 | 2.9721
87 | -0.19209 | -0.048686 | 0.19219 | 0.048747 | 9.7018e-05 | 6.1473e-05 | 0.29124 | 0.29124 | 0.29124 | 0.98209 | -0.34137 | 0.98263 | -0.33086 | 20.003
88 | 0.0048616 | 0.0012184 | -0.0048614 | -0.0012184 | 2.7453e-07 | 5.2368e-09 | 0.0073688 | 0.0073689 | 0.0073689 | 0.98173 | -0.34839 | 0.98167 | -0.34958 | 2.0244
89 | -0.19487 | -0.049419 | 0.19493 | 0.049458 | 6.1521e-05 | 3.8992e-05 | 0.2953 | 0.2953 | 0.2953 | 0.98263 | -0.33086 | 0.98297 | -0.3243 | 20.2819
90 | 0.14999 | 0.038026 | -0.14995 | -0.037996 | 4.6686e-05 | 2.939e-05 | 0.22721 | 0.22721 | 0.22721 | 0.98297 | -0.3243 | 0.98263 | -0.33078 | 15.6053
91 | -0.34492 | -0.087484 | 0.34538 | 0.087777 | 0.00046041 | 0.00029375 | 0.52252 | 0.52252 | 0.52252 | 0.98297 | -0.3243 | 0.9844 | -0.29658 | 35.8872
92 | 0.13769 | 0.034925 | -0.13766 | -0.034903 | 3.4136e-05 | 2.1424e-05 | 0.20866 | 0.20866 | 0.20866 | 0.98263 | -0.33078 | 0.98237 | -0.33594 | 14.3311
93 | 0.012251 | 0.0030714 | -0.012249 | -0.0030701 | 2.3883e-06 | 1.2942e-06 | 0.018553 | 0.018553 | 0.018553 | 0.98263 | -0.33078 | 0.98243 | -0.33487 | 5.0969
94 | -0.35044 | -0.089045 | 0.35086 | 0.089311 | 0.00041637 | 0.00026567 | 0.53016 | 0.53016 | 0.53016 | 0.9844 | -0.29658 | 0.98568 | -0.27193 | 36.4123
95 | 0.13766 | 0.034903 | -0.13756 | -0.034842 | 9.7186e-05 | 6.0994e-05 | 0.20866 | 0.20866 | 0.20866 | 0.98237 | -0.33594 | 0.98161 | -0.35063 | 14.3312
96 | 0.011218 | 0.0028117 | -0.011217 | -0.0028114 | 5.0398e-07 | 2.636e-07 | 0.016991 | 0.016991 | 0.016991 | 0.98243 | -0.33487 | 0.98238 | -0.33581 | 4.6679
97 | -0.35239 | -0.089695 | 0.35331 | 0.090278 | 0.00091387 | 0.00058312 | 0.53248 | 0.53248 | 0.53248 | 0.98568 | -0.27193 | 0.98847 | -0.21829 | 36.5713
98 | 0.13632 | 0.03453 | -0.13618 | -0.034441 | 0.0001417 | 8.8905e-05 | 0.20677 | 0.20677 | 0.20677 | 0.98161 | -0.35063 | 0.9805 | -0.3723 | 14.2015
99 | 0.0092947 | 0.0023295 | -0.0092946 | -0.0023295 | 1.0139e-07 | 4.7617e-08 | 0.014079 | 0.014079 | 0.014079 | 0.98238 | -0.33581 | 0.98237 | -0.33604 | 3.8678
100 | -0.35592 | -0.090934 | 0.35641 | 0.091246 | 0.00048957 | 0.00031239 | 0.53641 | 0.53641 | 0.53641 | 0.98847 | -0.21829 | 0.98996 | -0.18989 | 36.8416
101 | -0.0094196 | -0.002361 | 0.0094204 | 0.0023614 | 8.4569e-07 | 3.9086e-07 | 0.014022 | 0.014022 | 0.014022 | 0.99962 | -0.0073705 | 0.99971 | -0.0054863 | 3.8522
102 | 0.0038869 | 0.00097397 | -0.0038868 | -0.00097402 | 1.2392e-07 | -5.0136e-08 | 0.0057854 | 0.0057855 | 0.0057855 | 0.99971 | -0.0054863 | 0.99968 | -0.0061556 | 1.5894
103 | -0.013307 | -0.0033354 | 0.013308 | 0.0033358 | 8.1553e-07 | 4.4925e-07 | 0.019807 | 0.019807 | 0.019807 | 0.99971 | -0.0054863 | 0.99978 | -0.0042 | 5.4416
104 | 0.0014291 | 0.00035806 | -0.0014291 | -0.00035814 | 1.1609e-08 | -8.227e-08 | 0.0021272 | 0.0021272 | 0.0021272 | 0.99968 | -0.0061556 | 0.99967 | -0.0063261 | 0.5844
105 | -0.015734 | -0.0039438 | 0.015737 | 0.0039457 | 3.1491e-06 | 1.8146e-06 | 0.023418 | 0.023418 | 0.023418 | 0.99978 | -0.0042 | 1 | 0 | 6.4335
106 | -0.35641 | -0.091246 | 0.35713 | 0.091708 | 0.00072382 | 0.00046186 | 0.53641 | 0.53641 | 0.53641 | 0.98996 | -0.18989 | 0.99215 | -0.14805 | 36.8416
107 | -0.36631 | -0.094008 | 0.36692 | 0.094398 | 0.00061172 | 0.00039038 | 0.55018 | 0.55018 | 0.55018 | 0.99215 | -0.14805 | 0.99396 | -0.1137 | 37.7868
108 | 0.0014291 | 0.00035814 | -0.0014291 | -0.00035816 | 3.0609e-09 | -2.169e-08 | 0.0021272 | 0.0021272 | 0.0021272 | 0.99967 | -0.0063261 | 0.99967 | -0.0063711 | 0.5844
109 | -0.36692 | -0.094398 | 0.36738 | 0.09469 | 0.0004565 | 0.00029132 | 0.55018 | 0.55018 | 0.55018 | 0.99396 | -0.1137 | 0.99531 | -0.088142 | 37.7868
110 | -0.0025046 | -0.00062771 | 0.0025046 | 0.00062764 | 3.941e-08 | -7.4021e-08 | 0.0037271 | 0.0037271 | 0.0037271 | 0.99994 | -0.0011484 | 0.99996 | -0.00081805 | 1.0239
111 | -0.0049635 | -0.0012439 | 0.0049637 | 0.0012439 | 1.9343e-07 | -2.4312e-10 | 0.0073861 | 0.0073861 | 0.0073861 | 0.99996 | -0.00081805 | 1 | 0 | 2.0292
112 | -0.375 | -0.096601 | 0.37557 | 0.096961 | 0.00056511 | 0.00036067 | 0.56157 | 0.56157 | 0.56157 | 0.99531 | -0.088142 | 0.99695 | -0.057231 | 38.5697
113 | -0.37803 | -0.097578 | 0.37876 | 0.098043 | 0.00072961 | 0.00046568 | 0.56524 | 0.56524 | 0.56524 | 0.99695 | -0.057231 | 0.99905 | -0.017722 | 38.8217
114 | -0.38126 | -0.098671 | 0.38159 | 0.098882 | 0.0003304 | 0.00021088 | 0.56898 | 0.56898 | 0.56898 | 0.99905 | -0.017722 | 1 | 0 | 39.078
115 | 0.02465 | 0.0061837 | -0.024639 | -0.006177 | 1.0833e-05 | 6.6827e-06 | 0.037771 | 0.037771 | 0.037771 | 0.97116 | -0.5554 | 0.9707 | -0.56462 | 10.3766
116 | -0.01632 | -0.0040905 | 0.01632 | 0.0040905 | 7.3622e-08 | 4.3151e-08 | 0.024876 | 0.024876 | 0.024876 | 0.97625 | -0.45529 | 0.97626 | -0.45519 | 6.834
117 | 0.0071717 | 0.0017976 | -0.0071713 | -0.0017974 | 4.7968e-07 | 1.7316e-07 | 0.010931 | 0.010931 | 0.010931 | 0.97625 | -0.45529 | 0.97618 | -0.45669 | 3.0031
118 | -0.028303 | -0.0070935 | 0.028316 | 0.0071019 | 1.342e-05 | 8.3485e-06 | 0.043139 | 0.043139 | 0.043139 | 0.97626 | -0.45519 | 0.97677 | -0.44524 | 11.8514
119 | 0.0071713 | 0.0017974 | -0.0071702 | -0.001797 | 1.0793e-06 | 3.8967e-07 | 0.010931 | 0.010931 | 0.010931 | 0.97618 | -0.45669 | 0.97602 | -0.45985 | 3.0031
120 | -0.028316 | -0.0071019 | 0.028328 | 0.0071094 | 1.211e-05 | 7.5331e-06 | 0.043139 | 0.043139 | 0.043139 | 0.97677 | -0.44524 | 0.97722 | -0.43627 | 11.8514
121 | 0.091637 | 0.02312 | -0.091607 | -0.023101 | 3.0092e-05 | 1.8434e-05 | 0.13959 | 0.13959 | 0.13959 | 0.97722 | -0.43627 | 0.97687 | -0.44313 | 9.5873
122 | -0.11997 | -0.030229 | 0.12004 | 0.030278 | 7.8133e-05 | 4.8753e-05 | 0.18273 | 0.18273 | 0.18273 | 0.97722 | -0.43627 | 0.97792 | -0.42267 | 12.5502
123 | 0.0078235 | 0.0019609 | -0.0078224 | -0.0019605 | 1.156e-06 | 4.7545e-07 | 0.011999 | 0.011999 | 0.011999 | 0.97025 | -0.57353 | 0.97009 | -0.57663 | 3.2963
124 | -0.0078235 | -0.0019609 | 0.0078248 | 0.0019615 | 1.2413e-06 | 5.1041e-07 | 0.011999 | 0.011998 | 0.011999 | 0.97025 | -0.57353 | 0.97042 | -0.5702 | 3.2963
125 | -0.015501 | -0.0038853 | 0.015505 | 0.0038877 | 4.117e-06 | 2.3947e-06 | 0.023769 | 0.023769 | 0.023769 | 0.97042 | -0.5702 | 0.9707 | -0.56462 | 6.53
126 | -0.0091337 | -0.0022891 | 0.009134 | 0.0022893 | 3.104e-07 | 1.4647e-07 | 0.014002 | 0.014002 | 0.014002 | 0.97066 | -0.56534 | 0.9707 | -0.56462 | 3.8467
127 | 0.084745 | 0.021381 | -0.084728 | -0.021371 | 1.6334e-05 | 9.9306e-06 | 0.12914 | 0.12914 | 0.12914 | 0.97687 | -0.44313 | 0.97667 | -0.44716 | 8.8694
128 | -0.12875 | -0.032459 | 0.1288 | 0.03249 | 4.9396e-05 | 3.0925e-05 | 0.19597 | 0.19597 | 0.19597 | 0.97792 | -0.42267 | 0.97833 | -0.41465 | 13.4596
129 | 0.078356 | 0.019775 | -0.078319 | -0.019752 | 3.718e-05 | 2.3013e-05 | 0.11943 | 0.11943 | 0.11943 | 0.97667 | -0.44716 | 0.97616 | -0.45707 | 10.9369
130 | -0.13124 | -0.033103 | 0.13128 | 0.033125 | 3.489e-05 | 2.1861e-05 | 0.19969 | 0.19969 | 0.19969 | 0.97833 | -0.41465 | 0.97861 | -0.4091 | 13.7152
131 | -0.060514 | -0.015221 | 0.060524 | 0.015227 | 1.0457e-05 | 6.6518e-06 | 0.092528 | 0.092528 | 0.092528 | 0.97337 | -0.51181 | 0.97356 | -0.50819 | 25.4198
132 | 0.1338 | 0.033847 | -0.1337 | -0.03378 | 0.0001069 | 6.7021e-05 | 0.20317 | 0.20317 | 0.20317 | 0.9805 | -0.3723 | 0.97964 | -0.38897 | 13.9543
133 | 0.1337 | 0.03378 | -0.13357 | -0.033699 | 0.00012892 | 8.0835e-05 | 0.20317 | 0.20317 | 0.20317 | 0.97964 | -0.38897 | 0.97861 | -0.4091 | 13.9543
134 | 0.0074616 | 0.0018701 | -0.0074613 | -0.00187 | 3.0411e-07 | 1.1426e-07 | 0.011302 | 0.011302 | 0.011302 | 0.98237 | -0.33604 | 0.98232 | -0.3369 | 3.105
135 | 0.0063285 | 0.0015861 | -0.0063281 | -0.001586 | 3.9236e-07 | 1.0699e-07 | 0.0095863 | 0.0095864 | 0.0095864 | 0.98232 | -0.3369 | 0.98226 | -0.3382 | 2.6336
136 | -0.069163 | -0.017417 | 0.069208 | 0.017446 | 4.5609e-05 | 2.9054e-05 | 0.10563 | 0.10563 | 0.10563 | 0.97462 | -0.48736 | 0.97532 | -0.47358 | 29.0182
137 | 0.065941 | 0.01661 | -0.0659 | -0.016584 | 4.1519e-05 | 2.6436e-05 | 0.10071 | 0.10071 | 0.10071 | 0.97462 | -0.48736 | 0.97395 | -0.50054 | 27.667
138 | -0.072585 | -0.018293 | 0.072642 | 0.018329 | 5.7373e-05 | 3.6096e-05 | 0.11078 | 0.11078 | 0.11078 | 0.97532 | -0.47358 | 0.97616 | -0.45707 | 15.2166
139 | 0.062451 | 0.015719 | -0.062428 | -0.015705 | 2.284e-05 | 1.4535e-05 | 0.095438 | 0.095438 | 0.095438 | 0.97395 | -0.50054 | 0.97356 | -0.50819 | 26.2193

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.40395 | 0.10407

## res_load
| p_mw | q_mvar
0 | 0.0024475 | 0.00061341
1 | 0.0028822 | 0.00072235
2 | 0.0027876 | 0.00069863
3 | 0.0013398 | 0.00033578
4 | 0.0034008 | 0.00085232
5 | 0.0026224 | 0.00065723
6 | 0.0025475 | 0.00063845
7 | 0.0042492 | 0.0010649
8 | 0.0012531 | 0.00031407
9 | 0.0029151 | 0.0007306
10 | 0.00075923 | 0.00019028
11 | 0.00075783 | 0.00018993
12 | 0.003996 | 0.0010015
13 | 0.0019482 | 0.00048825
14 | 0.0011982 | 0.00030031
15 | 0.0014914 | 0.00037377
16 | 0.0017584 | 0.0004407
17 | 0.0025833 | 0.00064745
18 | 0.0024997 | 0.00062649
19 | 0.0059411 | 0.001489
20 | 0.0026125 | 0.00065475
21 | 0.0038343 | 0.00096097
22 | 0.0014509 | 0.00036363
23 | 0.0010995 | 0.00027555
24 | 0.0017787 | 0.00044578
25 | 0.0033218 | 0.00083253
26 | 0.015578 | 0.0039043
27 | 0.0068248 | 0.0017104
28 | 0.0025936 | 0.00065002
29 | 0.0033745 | 0.00084572
30 | 0.0040603 | 0.0010176
31 | 0.0071375 | 0.0017888
32 | 0.0068892 | 0.0017266
33 | 0.0061721 | 0.0015469
34 | 0.0062644 | 0.00157
35 | 0.0028245 | 0.00070787
36 | 0.0043313 | 0.0010855
37 | 0.0028459 | 0.00071324
38 | 0.003244 | 0.00081302
39 | 0.0030096 | 0.00075426
40 | 0.0036273 | 0.0009091
41 | 0.0029303 | 0.0007344
42 | 0.0033933 | 0.00085044
43 | 0.0037845 | 0.00094848
44 | 0.0089357 | 0.0022395
45 | 0.001772 | 0.00044411
46 | 0.0038398 | 0.00096235
47 | 0.0024606 | 0.00061667
48 | 0.0028995 | 0.00072668
49 | 0.0023704 | 0.00059408
50 | 0.001224 | 0.00030677
51 | 0.0043177 | 0.0010821
52 | 0.0040406 | 0.0010127
53 | 0.0025632 | 0.00064241
54 | 0.0036563 | 0.00091636
55 | 0.0083309 | 0.0020879
56 | 0.001301 | 0.00032605
57 | 0.0016465 | 0.00041264
58 | 0.0020309 | 0.00050899
59 | 0.0018492 | 0.00046346
60 | 0.0018494 | 0.00046351
61 | 0.002276 | 0.00057042
62 | 0.0026812 | 0.00067197
63 | 0.0048614 | 0.0012184
64 | 0.0050581 | 0.0012677
65 | 0.0010311 | 0.00025843
66 | 0.0015339 | 0.00038444
67 | 0.0012456 | 0.00031218
68 | 0.0019226 | 0.00048186
69 | 0.002615 | 0.00065539
70 | 0.0024577 | 0.00061596
71 | 0.002426 | 0.00060801
72 | 0.0091767 | 0.0022999
73 | 0.0014291 | 0.00035816
74 | 0.0025046 | 0.00062771
75 | 0.0024589 | 0.00061626
76 | 0.0076249 | 0.001911
77 | 0.0024589 | 0.00061626
78 | 0.0025057 | 0.00062799
79 | 0.0075758 | 0.0018987
80 | 0.004208 | 0.0010546
81 | 0.0074536 | 0.001868
82 | 0.0091487 | 0.0022929
83 | 0.011982 | 0.003003
84 | 0.0071702 | 0.001797
85 | 0.0078224 | 0.0019605
86 | 0.0076763 | 0.0019239
87 | 0.0091337 | 0.0022891
88 | 0.0068626 | 0.0017199
89 | 0.008703 | 0.0021812
90 | 0.0063717 | 0.0015969
91 | 0.0024468 | 0.00061323
92 | 0.0019473 | 0.00048804
93 | 0.0023724 | 0.00059457
94 | 0.0022895 | 0.0005738
95 | 0.001833 | 0.0004594
96 | 0.0011328 | 0.00028391
97 | 0.0063281 | 0.001586
98 | 0.0032214 | 0.00080736
99 | 0.0033762 | 0.00084615
100 | 0.003449 | 0.0008644
101 | 0.0056773 | 0.0014229
102 | 0.001904 | 0.0004772

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1