## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-664_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-664_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-664_0_4_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_261-664_0_4_node_5 | 0.4 | n |  | TRUE
4 | bus_LV_261-664_0_4_node_2 | 0.4 | n |  | TRUE
5 | bus_LV_261-664_0_4_node_25 | 0.4 | n |  | TRUE
6 | bus_LV_261-664_0_4_node_23 | 0.4 | n |  | TRUE
7 | bus_LV_261-664_0_4_node_28 | 0.4 | n |  | TRUE
8 | bus_LV_261-664_0_4_node_4 | 0.4 | n |  | TRUE
9 | bus_LV_261-664_0_4_node_26 | 0.4 | n |  | TRUE
10 | bus_LV_261-664_0_4_node_24 | 0.4 | n |  | TRUE
11 | bus_LV_261-664_0_4_node_57 | 0.4 | n |  | TRUE
12 | bus_LV_261-664_0_4_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_261-664_0_4_node_15 | 0.4 | n |  | TRUE
14 | bus_LV_261-664_0_4_node_33 | 0.4 | n |  | TRUE
15 | bus_LV_261-664_0_4_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_261-664_0_4_node_27 | 0.4 | n |  | TRUE
17 | bus_LV_261-664_0_4_node_16 | 0.4 | n |  | TRUE
18 | bus_LV_261-664_0_4_node_31 | 0.4 | n |  | TRUE
19 | bus_LV_261-664_0_4_node_11 | 0.4 | n |  | TRUE
20 | bus_LV_261-664_0_4_node_20 | 0.4 | n |  | TRUE
21 | bus_LV_261-664_0_4_node_51 | 0.4 | n |  | TRUE
22 | bus_LV_261-664_0_4_node_12 | 0.4 | n |  | TRUE
23 | bus_LV_261-664_0_4_node_50 | 0.4 | n |  | TRUE
24 | bus_LV_261-664_0_4_node_13 | 0.4 | n |  | TRUE
25 | bus_LV_261-664_0_4_node_14 | 0.4 | n |  | TRUE
26 | bus_LV_261-664_0_4_node_39 | 0.4 | n |  | TRUE
27 | bus_LV_261-664_0_4_node_43 | 0.4 | n |  | TRUE
28 | bus_LV_261-664_0_4_node_52 | 0.4 | n |  | TRUE
29 | bus_LV_261-664_0_4_node_30 | 0.4 | n |  | TRUE
30 | bus_LV_261-664_0_4_node_55 | 0.4 | n |  | TRUE
31 | bus_LV_261-664_0_4_node_18 | 0.4 | n |  | TRUE
32 | bus_LV_261-664_0_4_node_56 | 0.4 | n |  | TRUE
33 | bus_LV_261-664_0_4_node_19 | 0.4 | n |  | TRUE
34 | bus_LV_261-664_0_4_node_47 | 0.4 | n |  | TRUE
35 | bus_LV_261-664_0_4_node_48 | 0.4 | n |  | TRUE
36 | bus_LV_261-664_0_4_node_49 | 0.4 | n |  | TRUE
37 | bus_LV_261-664_0_4_node_21 | 0.4 | n |  | TRUE
38 | bus_LV_261-664_0_4_node_46 | 0.4 | n |  | TRUE
39 | bus_LV_261-664_0_4_node_45 | 0.4 | n |  | TRUE
40 | bus_LV_261-664_0_4_node_44 | 0.4 | n |  | TRUE
41 | bus_LV_261-664_0_4_node_32 | 0.4 | n |  | TRUE
42 | bus_LV_261-664_0_4_node_53 | 0.4 | n |  | TRUE
43 | bus_LV_261-664_0_4_node_37 | 0.4 | n |  | TRUE
44 | bus_LV_261-664_0_4_node_41 | 0.4 | n |  | TRUE
45 | bus_LV_261-664_0_4_node_29 | 0.4 | n |  | TRUE
46 | bus_LV_261-664_0_4_node_34 | 0.4 | n |  | TRUE
47 | bus_LV_261-664_0_4_node_35 | 0.4 | n |  | TRUE
48 | bus_LV_261-664_0_4_node_54 | 0.4 | n |  | TRUE
49 | bus_LV_261-664_0_4_node_40 | 0.4 | n |  | TRUE
50 | bus_LV_261-664_0_4_node_36 | 0.4 | n |  | TRUE
51 | bus_LV_261-664_0_4_node_38 | 0.4 | n |  | TRUE
52 | bus_LV_261-664_0_4_node_42 | 0.4 | n |  | TRUE
53 | bus_MV_545_0_node_115 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-664_0_4_load_0 | 0 | 0.011859 | 0.0029723 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-664_0_4_load_23 | 6 | 0.01056 | 0.0026465 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-664_0_4_load_28 | 7 | 0.036561 | 0.0091631 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-664_0_4_load_24 | 10 | 0.010817 | 0.002711 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-664_0_4_load_57 | 11 | 0.00022128 | 5.5457e-05 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-664_0_4_load_33 | 14 | 0.0016371 | 0.00041031 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-664_0_4_load_31 | 18 | 0.0064423 | 0.0016146 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-664_0_4_load_51 | 21 | 0.063814 | 0.015993 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-664_0_4_load_50 | 23 | 0.074773 | 0.01874 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-664_0_4_load_39 | 26 | 0.0024869 | 0.00062329 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-664_0_4_load_43 | 27 | 0.0020963 | 0.00052537 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-664_0_4_load_52 | 28 | 0.0040298 | 0.00101 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-664_0_4_load_30 | 29 | 0.0043225 | 0.0010833 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-664_0_4_load_55 | 30 | 0.0085497 | 0.0021428 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-664_0_4_load_56 | 32 | 0.0081073 | 0.0020319 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-664_0_4_load_48 | 35 | 0.047179 | 0.011824 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-664_0_4_load_49 | 36 | 0.046872 | 0.011747 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_261-664_0_4_load_46 | 38 | 0.023507 | 0.0058915 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_261-664_0_4_load_45 | 39 | 0.0022668 | 0.00056811 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_261-664_0_4_load_44 | 40 | 0.0074477 | 0.0018666 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_261-664_0_4_load_32 | 41 | 0.0015522 | 0.00038902 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_261-664_0_4_load_53 | 42 | 0.0039411 | 0.00098773 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_261-664_0_4_load_37 | 43 | 0.0016375 | 0.00041041 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_261-664_0_4_load_41 | 44 | 0.0015788 | 0.00039568 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_261-664_0_4_load_29 | 45 | 0.044969 | 0.01127 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_261-664_0_4_load_34 | 46 | 0.0015635 | 0.00039184 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_261-664_0_4_load_35 | 47 | 0.0016219 | 0.00040649 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_261-664_0_4_load_54 | 48 | 0.0017445 | 0.00043721 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_261-664_0_4_load_40 | 49 | 0.0017099 | 0.00042855 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_261-664_0_4_load_36 | 50 | 0.001556 | 0.00038997 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_261-664_0_4_load_38 | 51 | 0.0016458 | 0.00041247 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_261-664_0_4_load_42 | 52 | 0.0016961 | 0.00042509 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 22 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-664_0_4_line_0 |  | 0 | 1 | 0.018639 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-664_0_4_line_1 |  | 1 | 2 | 0.047732 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-664_0_4_line_2 |  | 1 | 3 | 0.32723 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-664_0_4_line_3 |  | 2 | 7 | 0.080633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-664_0_4_line_4 |  | 2 | 4 | 0.021738 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_261-664_0_4_line_5 |  | 3 | 11 | 0.0098654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_261-664_0_4_line_6 |  | 4 | 5 | 0.015767 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_261-664_0_4_line_7 |  | 4 | 6 | 0.014451 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
8 | LV_261-664_0_4_line_8 |  | 5 | 38 | 0.022592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_261-664_0_4_line_9 |  | 5 | 37 | 0.01623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_261-664_0_4_line_10 |  | 6 | 10 | 0.025617 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
11 | LV_261-664_0_4_line_11 |  | 8 | 9 | 0.04326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
12 | LV_261-664_0_4_line_12 |  | 8 | 10 | 0.030345 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
13 | LV_261-664_0_4_line_13 |  | 9 | 16 | 0.013114 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_261-664_0_4_line_14 |  | 9 | 36 | 0.028186 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
15 | LV_261-664_0_4_line_15 |  | 12 | 13 | 0.059369 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_261-664_0_4_line_16 |  | 12 | 14 | 0.024818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_261-664_0_4_line_17 |  | 13 | 29 | 0.035411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_261-664_0_4_line_18 |  | 14 | 41 | 0.0056333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_261-664_0_4_line_19 |  | 15 | 16 | 0.029344 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_261-664_0_4_line_20 |  | 15 | 17 | 0.064668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_261-664_0_4_line_21 |  | 15 | 18 | 0.023388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_261-664_0_4_line_22 |  | 17 | 30 | 0.070928 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_261-664_0_4_line_23 |  | 18 | 29 | 0.026245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_261-664_0_4_line_24 |  | 19 | 20 | 0.012528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_261-664_0_4_line_25 |  | 19 | 21 | 0.0085631 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_261-664_0_4_line_26 |  | 20 | 36 | 0.026291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
27 | LV_261-664_0_4_line_27 |  | 20 | 22 | 0.03626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
28 | LV_261-664_0_4_line_28 |  | 22 | 23 | 0.0077529 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_261-664_0_4_line_29 |  | 24 | 25 | 0.0076383 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_261-664_0_4_line_30 |  | 24 | 26 | 0.0046648 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_261-664_0_4_line_31 |  | 24 | 27 | 0.0033796 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_261-664_0_4_line_32 |  | 25 | 28 | 0.011399 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_261-664_0_4_line_33 |  | 26 | 43 | 0.01571 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_261-664_0_4_line_34 |  | 27 | 44 | 0.016317 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_261-664_0_4_line_35 |  | 28 | 42 | 0.014328 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_261-664_0_4_line_36 |  | 30 | 31 | 0.047542 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_261-664_0_4_line_37 |  | 31 | 32 | 0.040673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_261-664_0_4_line_38 |  | 33 | 34 | 0.013729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_261-664_0_4_line_39 |  | 33 | 35 | 0.0338 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_261-664_0_4_line_40 |  | 34 | 45 | 0.038285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_261-664_0_4_line_41 |  | 35 | 37 | 0.031085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_261-664_0_4_line_42 |  | 39 | 40 | 0.023349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_261-664_0_4_line_43 |  | 40 | 52 | 0.019214 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_261-664_0_4_line_44 |  | 41 | 46 | 0.0055057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_261-664_0_4_line_45 |  | 43 | 50 | 0.005634 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_261-664_0_4_line_46 |  | 44 | 52 | 0.0065568 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_261-664_0_4_line_47 |  | 46 | 47 | 0.0056306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_261-664_0_4_line_48 |  | 47 | 48 | 0.0046888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_261-664_0_4_line_49 |  | 48 | 49 | 0.0038513 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_261-664_0_4_line_50 |  | 49 | 51 | 0.0047168 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_261-664_0_4_line_51 |  | 50 | 51 | 0.0056518 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-664_0_4_trafo_12 | 0.63 MVA 20/0.4 kV | 53 | 22 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13
0 | 2681151.8259 | 1246578.2693 | 2681150.5785 | 1246567.2998 | 2681149.7224 | 1246559.7492
1 | 2681151.8259 | 1246578.2693 | 2681163.5256 | 1246591.6836 | 2681169.8916 | 1246592.9716 | 2681175.3974 | 1246600.2523 | 2681180.5539 | 1246607.6616 | 2681183.0207 | 1246612.3321
2 | 2681151.8259 | 1246578.2693 | 2681139.7101 | 1246564.3378 | 2681117.707 | 1246539.7968 | 2681088.6196 | 1246510.1219 | 2681063.2406 | 1246485.4681 | 2681060.2105 | 1246482.2021 | 2681056.3871 | 1246478.9364 | 2681241.5828 | 1246439.33
3 | 2681183.0207 | 1246612.3321 | 2681192.9562 | 1246601.7604 | 2681213.1229 | 1246572.2816 | 2681230.2788 | 1246547.1754
4 | 2681183.0207 | 1246612.3321 | 2681184.4421 | 1246615.0091 | 2681189.359 | 1246625.017 | 2681192.6883 | 1246631.8008
5 | 2681241.5828 | 1246439.33 | 2681239.4228 | 1246430.4606 | 2681239.4325 | 1246429.7239
6 | 2681206.0691 | 1246623.4001 | 2681192.6883 | 1246631.8008
7 | 2681192.6883 | 1246631.8008 | 2681198.8302 | 1246644.8822
8 | 2681206.0691 | 1246623.4001 | 2681219.6487 | 1246605.3452
9 | 2681219.065 | 1246633.1741 | 2681206.0691 | 1246623.4001
10 | 2681198.8302 | 1246644.8822 | 2681209.7175 | 1246668.0705
11 | 2681222.782 | 1246695.4593 | 2681228.0869 | 1246706.3621 | 2681236.002 | 1246720.2807 | 2681244.8801 | 1246708.0378
12 | 2681222.782 | 1246695.4593 | 2681212.0667 | 1246673.074 | 2681209.7175 | 1246668.0705
13 | 2681244.8801 | 1246708.0378 | 2681255.9871 | 1246715.0617
14 | 2681244.8801 | 1246708.0378 | 2681254.2124 | 1246695.1784 | 2681261.2195 | 1246685.0727
15 | 2681331.1193 | 1246778.6823 | 2681317.3721 | 1246812.1405 | 2681313.9164 | 1246810.7365 | 2681312.7111 | 1246811.5873 | 2681311.3073 | 1246812.0461 | 2681309.834 | 1246812.0593 | 2681308.2845 | 1246811.571 | 2681306.9834 | 1246810.5969 | 2681301.0216 | 1246804.6442 | 2681298.5651 | 1246806.9455
16 | 2681331.1193 | 1246778.6823 | 2681340.6838 | 1246755.7812
17 | 2681298.5651 | 1246806.9455 | 2681295.5202 | 1246803.6792 | 2681277.8705 | 1246784.6012 | 2681274.6427 | 1246780.8406
18 | 2681340.6838 | 1246755.7812 | 2681342.8548 | 1246750.5831
19 | 2681248.197 | 1246738.8612 | 2681243.563 | 1246731.3812 | 2681246.921 | 1246727.7912 | 2681252.8652 | 1246719.6111 | 2681255.9871 | 1246715.0617
20 | 2681192.3351 | 1246727.6214 | 2681201.1724 | 1246728.2762 | 2681209.0874 | 1246726.2164 | 2681215.0914 | 1246726.3432 | 2681222.3179 | 1246728.2213 | 2681227.4619 | 1246729.9152 | 2681230.45 | 1246734.0258 | 2681233.7346 | 1246738.5518 | 2681234.8549 | 1246738.3893 | 2681237.2062 | 1246738.7995 | 2681239.2211 | 1246740.0614 | 2681241.7127 | 1246743.4647 | 2681244.7947 | 1246741.272 | 2681248.197 | 1246738.8612
21 | 2681248.197 | 1246738.8612 | 2681260.49 | 1246758.7585
22 | 2681192.3351 | 1246727.6214 | 2681192.5329 | 1246724.2106 | 2681192.5618 | 1246719.8967 | 2681179.2576 | 1246658.1151
23 | 2681274.6427 | 1246780.8406 | 2681273.6694 | 1246779.7067 | 2681269.5848 | 1246773.4795 | 2681260.49 | 1246758.7585
24 | 2681286.5583 | 1246670.5592 | 2681276.2001 | 1246663.4677
25 | 2681286.5583 | 1246670.5592 | 2681281.7097 | 1246677.6174
26 | 2681276.2001 | 1246663.4677 | 2681261.2195 | 1246685.0727
27 | 2681276.2001 | 1246663.4677 | 2681297.0201 | 1246633.7424
28 | 2681297.0201 | 1246633.7424 | 2681301.4677 | 1246627.3921
29 | 2681364.4571 | 1246698.859 | 2681368.0335 | 1246700.2758 | 2681366.5878 | 1246703.7808
30 | 2681364.4571 | 1246698.859 | 2681362.6593 | 1246703.1635
31 | 2681364.4571 | 1246698.859 | 2681365.8731 | 1246695.7904
32 | 2681366.5878 | 1246703.7808 | 2681362.2237 | 1246714.3113
33 | 2681362.6593 | 1246703.1635 | 2681356.6049 | 1246717.6601
34 | 2681365.8731 | 1246695.7904 | 2681372.7099 | 1246680.9753
35 | 2681362.2237 | 1246714.3113 | 2681356.7383 | 1246727.5472
36 | 2681145.834 | 1246647.3265 | 2681175.6502 | 1246641.3635 | 2681179.2576 | 1246658.1151
37 | 2681145.834 | 1246647.3265 | 2681138.4389 | 1246612.5 | 2681133.471 | 1246613.5123
38 | 2681256.0052 | 1246579.83 | 2681244.4199 | 1246572.4103
39 | 2681256.0052 | 1246579.83 | 2681236.7623 | 1246607.6181
40 | 2681244.4199 | 1246572.4103 | 2681266.2767 | 1246540.9775
41 | 2681219.065 | 1246633.1741 | 2681236.7623 | 1246607.6181
42 | 2681395.6733 | 1246637.5572 | 2681384.7187 | 1246658.1765
43 | 2681375.7042 | 1246675.1443 | 2681384.7187 | 1246658.1765
44 | 2681344.9766 | 1246745.5027 | 2681342.8548 | 1246750.5831
45 | 2681356.6049 | 1246717.6601 | 2681354.4336 | 1246722.8589
46 | 2681375.7042 | 1246675.1443 | 2681373.3955 | 1246679.4898 | 2681372.7099 | 1246680.9753
47 | 2681347.1465 | 1246740.307 | 2681344.9766 | 1246745.5027
48 | 2681348.9535 | 1246735.9804 | 2681347.1465 | 1246740.307
49 | 2681350.4378 | 1246732.4265 | 2681348.9535 | 1246735.9804
50 | 2681352.2555 | 1246728.0741 | 2681350.4378 | 1246732.4265
51 | 2681352.2555 | 1246728.0741 | 2681354.4336 | 1246722.8589

## bus_geodata
| x | y | coords
0 | 2681149.7224 | 1246559.7492
1 | 2681151.8259 | 1246578.2693
2 | 2681183.0207 | 1246612.3321
3 | 2681241.5828 | 1246439.33
4 | 2681192.6883 | 1246631.8008
5 | 2681206.0691 | 1246623.4001
6 | 2681198.8302 | 1246644.8822
7 | 2681230.2788 | 1246547.1754
8 | 2681222.782 | 1246695.4593
9 | 2681244.8801 | 1246708.0378
10 | 2681209.7175 | 1246668.0705
11 | 2681239.4325 | 1246429.7239
12 | 2681331.1193 | 1246778.6823
13 | 2681298.5651 | 1246806.9455
14 | 2681340.6838 | 1246755.7812
15 | 2681248.197 | 1246738.8612
16 | 2681255.9871 | 1246715.0617
17 | 2681192.3351 | 1246727.6214
18 | 2681260.49 | 1246758.7585
19 | 2681286.5583 | 1246670.5592
20 | 2681276.2001 | 1246663.4677
21 | 2681281.7097 | 1246677.6174
22 | 2681297.0201 | 1246633.7424
23 | 2681301.4677 | 1246627.3921
24 | 2681364.4571 | 1246698.859
25 | 2681366.5878 | 1246703.7808
26 | 2681362.6593 | 1246703.1635
27 | 2681365.8731 | 1246695.7904
28 | 2681362.2237 | 1246714.3113
29 | 2681274.6427 | 1246780.8406
30 | 2681179.2576 | 1246658.1151
31 | 2681145.834 | 1246647.3265
32 | 2681133.471 | 1246613.5123
33 | 2681256.0052 | 1246579.83
34 | 2681244.4199 | 1246572.4103
35 | 2681236.7623 | 1246607.6181
36 | 2681261.2195 | 1246685.0727
37 | 2681219.065 | 1246633.1741
38 | 2681219.6487 | 1246605.3452
39 | 2681395.6733 | 1246637.5572
40 | 2681384.7187 | 1246658.1765
41 | 2681342.8548 | 1246750.5831
42 | 2681356.7383 | 1246727.5472
43 | 2681356.6049 | 1246717.6601
44 | 2681372.7099 | 1246680.9753
45 | 2681266.2767 | 1246540.9775
46 | 2681344.9766 | 1246745.5027
47 | 2681347.1465 | 1246740.307
48 | 2681348.9535 | 1246735.9804
49 | 2681350.4378 | 1246732.4265
50 | 2681354.4336 | 1246722.8589
51 | 2681352.2555 | 1246728.0741
52 | 2681375.7042 | 1246675.1443
53 | 2681307.7917 | 1246642.085

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9829 | -0.32813 | 0.011859 | 0.0029723
1 | 0.9831 | -0.32414 | 0 | 0
2 | 0.98363 | -0.31374 | 0 | 0
3 | 0.98304 | -0.32548 | 0 | 0
4 | 0.98461 | -0.29471 | 0 | 0
5 | 0.98292 | -0.32755 | 0 | 0
6 | 0.98571 | -0.27338 | 0.01056 | 0.0026465
7 | 0.98091 | -0.367 | 0.036561 | 0.0091631
8 | 0.98883 | -0.21309 | 0 | 0
9 | 0.99131 | -0.16548 | 0 | 0
10 | 0.98709 | -0.24663 | 0.010817 | 0.002711
11 | 0.98303 | -0.32552 | 0.00022128 | 5.5457e-05
12 | 0.98295 | -0.32728 | 0 | 0
13 | 0.98516 | -0.28431 | 0 | 0
14 | 0.98203 | -0.34531 | 0.0016371 | 0.00041031
15 | 0.98866 | -0.21656 | 0 | 0
16 | 0.99049 | -0.18123 | 0 | 0
17 | 0.98767 | -0.23579 | 0 | 0
18 | 0.98756 | -0.23785 | 0.0064423 | 0.0016146
19 | 0.99522 | -0.091063 | 0 | 0
20 | 0.99594 | -0.077005 | 0 | 0
21 | 0.99472 | -0.10068 | 0.063814 | 0.015993
22 | 1 | 0 | -0.44559 | -0.11325
23 | 0.99947 | -0.010109 | 0.074773 | 0.01874
24 | 0.9803 | -0.37918 | 0 | 0
25 | 0.98024 | -0.38028 | 0 | 0
26 | 0.9804 | -0.37723 | 0.0024869 | 0.00062329
27 | 0.98025 | -0.38011 | 0.0020963 | 0.00052537
28 | 0.98016 | -0.38193 | 0.0040298 | 0.00101
29 | 0.98648 | -0.25876 | 0.0043225 | 0.0010833
30 | 0.98659 | -0.25693 | 0.0085497 | 0.0021428
31 | 0.98623 | -0.26384 | 0 | 0
32 | 0.98593 | -0.26975 | 0.0081073 | 0.0020319
33 | 0.97746 | -0.43422 | 0 | 0
34 | 0.97689 | -0.44549 | 0 | 0
35 | 0.97887 | -0.40653 | 0.047179 | 0.011824
36 | 0.99351 | -0.12335 | 0.046872 | 0.011747
37 | 0.98153 | -0.35457 | 0 | 0
38 | 0.98243 | -0.33713 | 0.023507 | 0.0058915
39 | 0.97977 | -0.38966 | 0.0022668 | 0.00056811
40 | 0.97982 | -0.3887 | 0.0074477 | 0.0018666
41 | 0.98183 | -0.34923 | 0.0015522 | 0.00038902
42 | 0.98011 | -0.38296 | 0.0039411 | 0.00098773
43 | 0.98077 | -0.36995 | 0.0016375 | 0.00041041
44 | 0.98006 | -0.38395 | 0.0015788 | 0.00039568
45 | 0.97528 | -0.47699 | 0.044969 | 0.01127
46 | 0.98164 | -0.35292 | 0.0015635 | 0.00039184
47 | 0.98146 | -0.35653 | 0.0016219 | 0.00040649
48 | 0.98131 | -0.3594 | 0.0017445 | 0.00043721
49 | 0.9812 | -0.36164 | 0.0017099 | 0.00042855
50 | 0.98091 | -0.36718 | 0.001556 | 0.00038997
51 | 0.98106 | -0.36424 | 0.0016458 | 0.00041247
52 | 0.97999 | -0.38531 | 0.0016961 | 0.00042509
53 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.011859 | -0.0029723 | 0.011862 | 0.0029735 | 2.2531e-06 | 1.2057e-06 | 0.017954 | 0.017954 | 0.017954 | 0.9829 | -0.32813 | 0.9831 | -0.32414 | 4.9324
1 | -0.012083 | -0.0030246 | 0.012089 | 0.0030279 | 5.986e-06 | 3.2255e-06 | 0.018287 | 0.018287 | 0.018287 | 0.9831 | -0.32414 | 0.98363 | -0.31374 | 5.024
2 | 0.00022129 | 5.1192e-05 | -0.00022128 | -5.5332e-05 | 1.3703e-08 | -4.1401e-06 | 0.00033348 | 0.0003349 | 0.0003349 | 0.9831 | -0.32414 | 0.98304 | -0.32548 | 0.092006
3 | 0.036654 | 0.0092216 | -0.036561 | -0.0091631 | 9.3011e-05 | 5.8507e-05 | 0.055462 | 0.055462 | 0.055462 | 0.98363 | -0.31374 | 0.98091 | -0.367 | 15.2369
4 | -0.048743 | -0.012249 | 0.048787 | 0.012278 | 4.4337e-05 | 2.81e-05 | 0.073749 | 0.073749 | 0.073749 | 0.98363 | -0.31374 | 0.98461 | -0.29471 | 20.2608
5 | 0.00022128 | 5.5332e-05 | -0.00022128 | -5.5457e-05 | 4.1499e-10 | -1.2481e-07 | 0.0003349 | 0.00033495 | 0.00033495 | 0.98304 | -0.32548 | 0.98303 | -0.32552 | 0.092018
6 | 0.11635 | 0.029428 | -0.11617 | -0.029311 | 0.00018301 | 0.00011693 | 0.17593 | 0.17593 | 0.17593 | 0.98461 | -0.29471 | 0.98292 | -0.32755 | 48.3331
7 | -0.16514 | -0.041706 | 0.16531 | 0.041814 | 0.00016892 | 0.00010774 | 0.24968 | 0.24968 | 0.24968 | 0.98461 | -0.29471 | 0.98571 | -0.27338 | 34.2969
8 | 0.023518 | 0.0058981 | -0.023507 | -0.0058915 | 1.074e-05 | 6.5874e-06 | 0.035605 | 0.035605 | 0.035605 | 0.98292 | -0.32755 | 0.98243 | -0.33713 | 9.7816
9 | 0.092649 | 0.023413 | -0.092529 | -0.023337 | 0.00011985 | 7.6498e-05 | 0.14033 | 0.14033 | 0.14033 | 0.98292 | -0.32755 | 0.98153 | -0.35457 | 38.5515
10 | -0.17587 | -0.04446 | 0.17609 | 0.044604 | 0.00022593 | 0.00014361 | 0.26562 | 0.26562 | 0.26562 | 0.98571 | -0.27338 | 0.98709 | -0.24663 | 24.3244
11 | -0.18721 | -0.047506 | 0.18764 | 0.04778 | 0.0004298 | 0.0002734 | 0.28193 | 0.28193 | 0.28193 | 0.98883 | -0.21309 | 0.99131 | -0.16548 | 25.8175
12 | 0.18721 | 0.047506 | -0.18691 | -0.047315 | 0.00030149 | 0.00019179 | 0.28193 | 0.28193 | 0.28193 | 0.98883 | -0.21309 | 0.98709 | -0.24663 | 25.8176
13 | 0.068159 | 0.017279 | -0.068107 | -0.017246 | 5.1547e-05 | 3.2821e-05 | 0.10238 | 0.10238 | 0.10238 | 0.99131 | -0.16548 | 0.99049 | -0.18123 | 28.1266
14 | -0.2558 | -0.065059 | 0.25632 | 0.065391 | 0.00052036 | 0.00033194 | 0.38431 | 0.38431 | 0.38431 | 0.99131 | -0.16548 | 0.99351 | -0.12335 | 35.193
15 | -0.040304 | -0.010134 | 0.040386 | 0.010187 | 8.2907e-05 | 5.2306e-05 | 0.061024 | 0.061024 | 0.061024 | 0.98295 | -0.32728 | 0.98516 | -0.28431 | 16.7649
16 | 0.040304 | 0.010134 | -0.040269 | -0.010112 | 3.4658e-05 | 2.1867e-05 | 0.061024 | 0.061024 | 0.061024 | 0.98295 | -0.32728 | 0.98203 | -0.34531 | 16.765
17 | -0.040386 | -0.010187 | 0.040436 | 0.010218 | 4.9451e-05 | 3.1197e-05 | 0.061024 | 0.061024 | 0.061024 | 0.98516 | -0.28431 | 0.98648 | -0.25876 | 16.7649
18 | 0.038632 | 0.0097022 | -0.038625 | -0.0096976 | 7.2403e-06 | 4.5625e-06 | 0.058544 | 0.058544 | 0.058544 | 0.98203 | -0.34531 | 0.98183 | -0.34923 | 16.0835
19 | -0.067992 | -0.017173 | 0.068107 | 0.017246 | 0.00011534 | 7.3442e-05 | 0.10238 | 0.10238 | 0.10238 | 0.98866 | -0.21656 | 0.99049 | -0.18123 | 28.1266
20 | 0.016694 | 0.0041955 | -0.016679 | -0.0041865 | 1.5315e-05 | 8.9732e-06 | 0.02513 | 0.02513 | 0.02513 | 0.98866 | -0.21656 | 0.98767 | -0.23579 | 6.904
21 | 0.051298 | 0.012977 | -0.051246 | -0.012944 | 5.2341e-05 | 3.3198e-05 | 0.077251 | 0.077251 | 0.077251 | 0.98866 | -0.21656 | 0.98756 | -0.23785 | 21.2228
22 | 0.016679 | 0.0041865 | -0.016662 | -0.0041767 | 1.6798e-05 | 9.844e-06 | 0.02513 | 0.025131 | 0.025131 | 0.98767 | -0.23579 | 0.98659 | -0.25693 | 6.9041
23 | 0.044803 | 0.01133 | -0.044758 | -0.011301 | 4.4901e-05 | 2.8401e-05 | 0.067544 | 0.067544 | 0.067544 | 0.98756 | -0.23785 | 0.98648 | -0.25876 | 18.5561
24 | -0.063843 | -0.016012 | 0.063886 | 0.016039 | 4.2811e-05 | 2.7236e-05 | 0.09546 | 0.09546 | 0.09546 | 0.99522 | -0.091063 | 0.99594 | -0.077005 | 26.2253
25 | 0.063843 | 0.016012 | -0.063814 | -0.015993 | 2.9262e-05 | 1.8617e-05 | 0.09546 | 0.09546 | 0.09546 | 0.99522 | -0.091063 | 0.99472 | -0.10068 | 26.2253
26 | 0.30387 | 0.077572 | -0.30319 | -0.077138 | 0.00067888 | 0.00043346 | 0.45451 | 0.45451 | 0.45451 | 0.99594 | -0.077005 | 0.99351 | -0.12335 | 41.6217
27 | -0.36776 | -0.093611 | 0.36913 | 0.094487 | 0.0013709 | 0.00087597 | 0.54997 | 0.54997 | 0.54997 | 0.99594 | -0.077005 | 1 | 0 | 50.3633
28 | 0.074809 | 0.018763 | -0.074773 | -0.01874 | 3.6029e-05 | 2.2957e-05 | 0.11132 | 0.11132 | 0.11132 | 1 | 0 | 0.99947 | -0.010109 | 30.583
29 | 0.0079721 | 0.0019981 | -0.0079717 | -0.0019979 | 4.1944e-07 | 1.7215e-07 | 0.012101 | 0.012101 | 0.012101 | 0.9803 | -0.37918 | 0.98024 | -0.38028 | 3.3245
30 | -0.023063 | -0.0057815 | 0.023065 | 0.0057828 | 2.1439e-06 | 1.3133e-06 | 0.035009 | 0.035008 | 0.035009 | 0.9803 | -0.37918 | 0.9804 | -0.37723 | 9.6177
31 | 0.015091 | 0.0037834 | -0.01509 | -0.0037831 | 6.6504e-07 | 3.8302e-07 | 0.022907 | 0.022907 | 0.022907 | 0.9803 | -0.37918 | 0.98025 | -0.38011 | 6.2933
32 | 0.0079717 | 0.0019979 | -0.0079711 | -0.0019976 | 6.2597e-07 | 2.5693e-07 | 0.012101 | 0.012101 | 0.012101 | 0.98024 | -0.38028 | 0.98016 | -0.38193 | 3.3245
33 | -0.025552 | -0.0064061 | 0.025561 | 0.0064116 | 8.8612e-06 | 5.473e-06 | 0.038783 | 0.038783 | 0.038783 | 0.9804 | -0.37723 | 0.98077 | -0.36995 | 10.6547
34 | 0.012994 | 0.0032577 | -0.012992 | -0.0032564 | 2.3807e-06 | 1.318e-06 | 0.019725 | 0.019725 | 0.019725 | 0.98025 | -0.38011 | 0.98006 | -0.38395 | 5.4191
35 | 0.0039413 | 0.00098768 | -0.0039411 | -0.00098773 | 1.9235e-07 | -5.7466e-08 | 0.0059834 | 0.0059834 | 0.0059834 | 0.98016 | -0.38193 | 0.98011 | -0.38296 | 1.6438
36 | 0.0081123 | 0.0020339 | -0.0081096 | -0.0020328 | 2.6691e-06 | 1.1014e-06 | 0.012236 | 0.012236 | 0.012236 | 0.98659 | -0.25693 | 0.98623 | -0.26384 | 3.3615
37 | 0.0081096 | 0.0020328 | -0.0081073 | -0.0020319 | 2.2836e-06 | 9.4263e-07 | 0.012236 | 0.012236 | 0.012236 | 0.98623 | -0.26384 | 0.98593 | -0.26975 | 3.3616
38 | 0.045061 | 0.011328 | -0.045036 | -0.011313 | 2.4235e-05 | 1.5338e-05 | 0.06861 | 0.06861 | 0.06861 | 0.97746 | -0.43422 | 0.97689 | -0.44549 | 18.8489
39 | -0.045061 | -0.011328 | 0.04512 | 0.011366 | 5.9666e-05 | 3.7762e-05 | 0.06861 | 0.06861 | 0.06861 | 0.97746 | -0.43422 | 0.97887 | -0.40653 | 18.8489
40 | 0.045036 | 0.011313 | -0.044969 | -0.01127 | 6.7583e-05 | 4.2774e-05 | 0.06861 | 0.06861 | 0.06861 | 0.97689 | -0.44549 | 0.97528 | -0.47699 | 18.8489
41 | -0.092299 | -0.02319 | 0.092529 | 0.023337 | 0.00022955 | 0.00014652 | 0.14033 | 0.14033 | 0.14033 | 0.97887 | -0.40653 | 0.98153 | -0.35457 | 38.5516
42 | -0.0022668 | -0.00056811 | 0.0022669 | 0.00056788 | 1.0377e-07 | -2.2765e-07 | 0.0034427 | 0.0034426 | 0.0034427 | 0.97977 | -0.38966 | 0.97982 | -0.3887 | 0.94579
43 | -0.0097146 | -0.0024344 | 0.0097161 | 0.0024352 | 1.5682e-06 | 7.6162e-07 | 0.014753 | 0.014753 | 0.014753 | 0.97982 | -0.3887 | 0.97999 | -0.38531 | 4.0531
44 | 0.037072 | 0.0093086 | -0.037066 | -0.0093045 | 6.519e-06 | 4.1026e-06 | 0.056191 | 0.056191 | 0.056191 | 0.98183 | -0.34923 | 0.98164 | -0.35292 | 15.4372
45 | -0.027199 | -0.006822 | 0.027202 | 0.0068242 | 3.598e-06 | 2.2316e-06 | 0.041267 | 0.041267 | 0.041267 | 0.98077 | -0.36995 | 0.98091 | -0.36718 | 11.3372
46 | 0.011413 | 0.0028607 | -0.011412 | -0.0028603 | 7.3831e-07 | 3.899e-07 | 0.017328 | 0.017328 | 0.017328 | 0.98006 | -0.38395 | 0.97999 | -0.38531 | 4.7606
47 | 0.035502 | 0.0089127 | -0.035496 | -0.0089088 | 6.1164e-06 | 3.8433e-06 | 0.053821 | 0.053821 | 0.053821 | 0.98164 | -0.35292 | 0.98146 | -0.35653 | 14.7861
48 | 0.033874 | 0.0085023 | -0.03387 | -0.0084994 | 4.6386e-06 | 2.9094e-06 | 0.051362 | 0.051362 | 0.051362 | 0.98146 | -0.35653 | 0.98131 | -0.3594 | 14.1106
49 | 0.032125 | 0.0080622 | -0.032122 | -0.0080601 | 3.4277e-06 | 2.1451e-06 | 0.048717 | 0.048717 | 0.048717 | 0.98131 | -0.3594 | 0.9812 | -0.36164 | 13.3838
50 | 0.030412 | 0.0076315 | -0.030408 | -0.0076292 | 3.763e-06 | 2.3487e-06 | 0.046124 | 0.046124 | 0.046124 | 0.9812 | -0.36164 | 0.98106 | -0.36424 | 12.6714
51 | -0.028758 | -0.0072142 | 0.028762 | 0.0072167 | 4.0341e-06 | 2.5104e-06 | 0.043628 | 0.043628 | 0.043628 | 0.98091 | -0.36718 | 0.98106 | -0.36424 | 11.9857

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.44559 | 0.11325

## res_load
| p_mw | q_mvar
0 | 0.011859 | 0.0029723
1 | 0.01056 | 0.0026465
2 | 0.036561 | 0.0091631
3 | 0.010817 | 0.002711
4 | 0.00022128 | 5.5457e-05
5 | 0.0016371 | 0.00041031
6 | 0.0064423 | 0.0016146
7 | 0.063814 | 0.015993
8 | 0.074773 | 0.01874
9 | 0.0024869 | 0.00062329
10 | 0.0020963 | 0.00052537
11 | 0.0040298 | 0.00101
12 | 0.0043225 | 0.0010833
13 | 0.0085497 | 0.0021428
14 | 0.0081073 | 0.0020319
15 | 0.047179 | 0.011824
16 | 0.046872 | 0.011747
17 | 0.023507 | 0.0058915
18 | 0.0022668 | 0.00056811
19 | 0.0074477 | 0.0018666
20 | 0.0015522 | 0.00038902
21 | 0.0039411 | 0.00098773
22 | 0.0016375 | 0.00041041
23 | 0.0015788 | 0.00039568
24 | 0.044969 | 0.01127
25 | 0.0015635 | 0.00039184
26 | 0.0016219 | 0.00040649
27 | 0.0017445 | 0.00043721
28 | 0.0017099 | 0.00042855
29 | 0.001556 | 0.00038997
30 | 0.0016458 | 0.00041247
31 | 0.0016961 | 0.00042509

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1