## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-666_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-666_0_2_node_2 | 0.4 | n |  | TRUE
2 | bus_LV_261-666_0_2_node_19 | 0.4 | n |  | TRUE
3 | bus_LV_261-666_0_2_node_9 | 0.4 | n |  | TRUE
4 | bus_LV_261-666_0_2_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_261-666_0_2_node_16 | 0.4 | n |  | TRUE
6 | bus_LV_261-666_0_2_node_28 | 0.4 | n |  | TRUE
7 | bus_LV_261-666_0_2_node_6 | 0.4 | n |  | TRUE
8 | bus_LV_261-666_0_2_node_30 | 0.4 | n |  | TRUE
9 | bus_LV_261-666_0_2_node_8 | 0.4 | n |  | TRUE
10 | bus_LV_261-666_0_2_node_12 | 0.4 | n |  | TRUE
11 | bus_LV_261-666_0_2_node_29 | 0.4 | n |  | TRUE
12 | bus_LV_261-666_0_2_node_20 | 0.4 | n |  | TRUE
13 | bus_LV_261-666_0_2_node_10 | 0.4 | n |  | TRUE
14 | bus_LV_261-666_0_2_node_14 | 0.4 | n |  | TRUE
15 | bus_LV_261-666_0_2_node_23 | 0.4 | n |  | TRUE
16 | bus_LV_261-666_0_2_node_11 | 0.4 | n |  | TRUE
17 | bus_LV_261-666_0_2_node_17 | 0.4 | n |  | TRUE
18 | bus_LV_261-666_0_2_node_24 | 0.4 | n |  | TRUE
19 | bus_LV_261-666_0_2_node_18 | 0.4 | n |  | TRUE
20 | bus_LV_261-666_0_2_node_27 | 0.4 | n |  | TRUE
21 | bus_LV_261-666_0_2_node_13 | 0.4 | n |  | TRUE
22 | bus_LV_261-666_0_2_node_22 | 0.4 | n |  | TRUE
23 | bus_LV_261-666_0_2_node_21 | 0.4 | n |  | TRUE
24 | bus_LV_261-666_0_2_node_26 | 0.4 | n |  | TRUE
25 | bus_LV_261-666_0_2_node_15 | 0.4 | n |  | TRUE
26 | bus_LV_261-666_0_2_node_25 | 0.4 | n |  | TRUE
27 | bus_MV_359_0_node_174 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-666_0_2_load_0 | 0 | 0.0087108 | 0.0021831 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-666_0_2_load_19 | 2 | 0.0084964 | 0.0021294 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-666_0_2_load_28 | 6 | 0.0041111 | 0.0010303 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-666_0_2_load_30 | 8 | 0.080664 | 0.020216 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-666_0_2_load_29 | 11 | 0.043566 | 0.010919 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-666_0_2_load_20 | 12 | 0.0146 | 0.0036591 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-666_0_2_load_23 | 15 | 0.046225 | 0.011585 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-666_0_2_load_24 | 18 | 0.025815 | 0.0064699 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-666_0_2_load_27 | 20 | 0.0012867 | 0.00032247 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-666_0_2_load_22 | 22 | 0.047786 | 0.011976 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-666_0_2_load_21 | 23 | 0.035894 | 0.0089959 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-666_0_2_load_26 | 24 | 0.0071422 | 0.00179 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-666_0_2_load_25 | 26 | 0.0056795 | 0.0014234 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 8 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-666_0_2_line_0 |  | 0 | 1 | 0.0021681 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-666_0_2_line_1 |  | 1 | 2 | 0.024091 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-666_0_2_line_2 |  | 1 | 3 | 0.069887 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-666_0_2_line_3 |  | 3 | 12 | 0.02036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-666_0_2_line_4 |  | 3 | 4 | 0.066727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_261-666_0_2_line_5 |  | 3 | 7 | 0.048548 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_261-666_0_2_line_6 |  | 4 | 5 | 0.048858 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_261-666_0_2_line_7 |  | 4 | 6 | 0.026008 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_261-666_0_2_line_8 |  | 5 | 22 | 0.031583 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_261-666_0_2_line_9 |  | 7 | 8 | 0.025772 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
10 | LV_261-666_0_2_line_10 |  | 7 | 9 | 0.077208 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_261-666_0_2_line_11 |  | 7 | 10 | 0.080247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_261-666_0_2_line_12 |  | 9 | 11 | 0.010854 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-666_0_2_line_13 |  | 10 | 19 | 0.070409 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_261-666_0_2_line_14 |  | 10 | 20 | 0.092081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_261-666_0_2_line_15 |  | 13 | 14 | 0.048084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_261-666_0_2_line_16 |  | 13 | 15 | 0.010652 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_261-666_0_2_line_17 |  | 14 | 24 | 0.016482 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_261-666_0_2_line_18 |  | 15 | 19 | 0.0085351 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_261-666_0_2_line_19 |  | 16 | 17 | 0.021218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_261-666_0_2_line_20 |  | 16 | 18 | 0.015368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_261-666_0_2_line_21 |  | 17 | 24 | 0.02792 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_261-666_0_2_line_22 |  | 17 | 25 | 0.035669 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_261-666_0_2_line_23 |  | 21 | 22 | 0.019439 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_261-666_0_2_line_24 |  | 21 | 23 | 0.034618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_261-666_0_2_line_25 |  | 25 | 26 | 0.022746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-666_0_2_trafo_30 | 0.63 MVA 20/0.4 kV | 27 | 8 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15
0 | 2681222.9754 | 1242227.5185 | 2681223.6197 | 1242225.4484
1 | 2681222.9754 | 1242227.5185 | 2681215.8083 | 1242250.5189
2 | 2681222.9754 | 1242227.5185 | 2681238.8626 | 1242228.9369 | 2681237.9207 | 1242237.5413 | 2681236.1301 | 1242250.1481 | 2681232.2025 | 1242270.3088 | 2681229.5774 | 1242282.0257
3 | 2681229.5774 | 1242282.0257 | 2681223.3125 | 1242287.3772 | 2681219.186 | 1242293.9032 | 2681218.1844 | 1242298.1866
4 | 2681229.5774 | 1242282.0257 | 2681235.9311 | 1242277.376 | 2681238.0358 | 1242266.119 | 2681243.4963 | 1242237.8178 | 2681248.6248 | 1242238.166 | 2681258.4286 | 1242238.8452 | 2681262.0315 | 1242239.0836
5 | 2681229.5774 | 1242282.0257 | 2681235.9311 | 1242277.376 | 2681232.1382 | 1242297.6386 | 2681231.7115 | 1242312.2322 | 2681237.1659 | 1242311.9733
6 | 2681262.0315 | 1242239.0836 | 2681264.9242 | 1242239.29 | 2681285.4911 | 1242240.7059 | 2681310.786 | 1242239.1513
7 | 2681262.0315 | 1242239.0836 | 2681264.7015 | 1242213.2134
8 | 2681310.786 | 1242239.1513 | 2681329.743 | 1242231.1608 | 2681331.1803 | 1242220.2439
9 | 2681262.9803 | 1242313.3054 | 2681237.1659 | 1242311.9733
10 | 2681209.2502 | 1242373.0018 | 2681212.3444 | 1242368.4297 | 2681216.8313 | 1242362.0754 | 2681220.9154 | 1242356.9832 | 2681225.5177 | 1242351.5868 | 2681229.9097 | 1242347.1993 | 2681231.535 | 1242344.9977 | 2681232.1469 | 1242342.2708 | 2681232.3663 | 1242340.05 | 2681231.7886 | 1242337.518 | 2681238.6049 | 1242333.3083 | 2681243.3568 | 1242330.7937 | 2681241.6968 | 1242329.459 | 2681239.8769 | 1242325.4423 | 2681238.082 | 1242319.6024 | 2681237.1659 | 1242311.9733
11 | 2681237.1659 | 1242311.9733 | 2681238.082 | 1242319.6024 | 2681239.8769 | 1242325.4423 | 2681241.6968 | 1242329.459 | 2681243.3568 | 1242330.7937 | 2681238.6049 | 1242333.3083 | 2681243.4411 | 1242343.404 | 2681273.7772 | 1242324.8059 | 2681280.4437 | 1242328.7778
12 | 2681209.2502 | 1242373.0018 | 2681199.93 | 1242367.3925
13 | 2681280.4437 | 1242328.7778 | 2681327.1659 | 1242304.9785 | 2681333.1565 | 1242302.0029 | 2681339.3016 | 1242299.8855 | 2681343.7024 | 1242297.622
14 | 2681280.4437 | 1242328.7778 | 2681255.8049 | 1242342.0722 | 2681242.1712 | 1242353.327 | 2681225.8905 | 1242370.7389 | 2681216.3611 | 1242384.8187 | 2681213.9766 | 1242389.8481
15 | 2681360.5936 | 1242292.5165 | 2681371.9395 | 1242281.6198 | 2681378.4486 | 1242273.3697 | 2681380.4439 | 1242270.1059 | 2681376.6822 | 1242269.8652 | 2681379.3341 | 1242263.9307 | 2681382.5005 | 1242256.8579
16 | 2681360.5936 | 1242292.5165 | 2681352.1283 | 1242298.9829
17 | 2681382.5005 | 1242256.8579 | 2681384.1968 | 1242259.4052 | 2681391.8808 | 1242263.6024 | 2681396.3572 | 1242264.9202
18 | 2681343.7024 | 1242297.622 | 2681352.1283 | 1242298.9829
19 | 2681410.0163 | 1242276.3603 | 2681410.5295 | 1242272.0198 | 2681423.0626 | 1242273.237 | 2681423.9136 | 1242269.0679
20 | 2681410.0163 | 1242276.3603 | 2681408.217 | 1242291.6228
21 | 2681423.9136 | 1242269.0679 | 2681412.3706 | 1242267.8754 | 2681400.5174 | 1242266.1449 | 2681396.3572 | 1242264.9202
22 | 2681431.0387 | 1242234.1183 | 2681423.9136 | 1242269.0679
23 | 2681333.7178 | 1242200.9714 | 2681331.1803 | 1242220.2439
24 | 2681333.7178 | 1242200.9714 | 2681317.4286 | 1242199.6472 | 2681316.7495 | 1242203.9633 | 2681309.4553 | 1242203.3073 | 2681308.0286 | 1242204.2551 | 2681303.1747 | 1242203.8702
25 | 2681431.0387 | 1242234.1183 | 2681425.7439 | 1242227.7078 | 2681411.4551 | 1242225.6863

## bus_geodata
| x | y | coords
0 | 2681223.6197 | 1242225.4484
1 | 2681222.9754 | 1242227.5185
2 | 2681215.8083 | 1242250.5189
3 | 2681229.5774 | 1242282.0257
4 | 2681262.0315 | 1242239.0836
5 | 2681310.786 | 1242239.1513
6 | 2681264.7015 | 1242213.2134
7 | 2681237.1659 | 1242311.9733
8 | 2681262.9803 | 1242313.3054
9 | 2681209.2502 | 1242373.0018
10 | 2681280.4437 | 1242328.7778
11 | 2681199.93 | 1242367.3925
12 | 2681218.1844 | 1242298.1866
13 | 2681360.5936 | 1242292.5165
14 | 2681382.5005 | 1242256.8579
15 | 2681352.1283 | 1242298.9829
16 | 2681410.0163 | 1242276.3603
17 | 2681423.9136 | 1242269.0679
18 | 2681408.217 | 1242291.6228
19 | 2681343.7024 | 1242297.622
20 | 2681213.9766 | 1242389.8481
21 | 2681333.7178 | 1242200.9714
22 | 2681331.1803 | 1242220.2439
23 | 2681303.1747 | 1242203.8702
24 | 2681396.3572 | 1242264.9202
25 | 2681431.0388 | 1242234.1183
26 | 2681411.4551 | 1242225.6863
27 | 2681237.1659 | 1242311.9733

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99055 | -0.18021 | 0.0087108 | 0.0021831
1 | 0.99057 | -0.17987 | 0 | 0
2 | 0.99038 | -0.18351 | 0.0084964 | 0.0021294
3 | 0.99167 | -0.15853 | 0 | 0
4 | 0.98625 | -0.26293 | 0 | 0
5 | 0.98246 | -0.33648 | 0 | 0
6 | 0.98615 | -0.26485 | 0.0041111 | 0.0010303
7 | 0.99704 | -0.056168 | 0 | 0
8 | 1 | 0 | -0.25455 | -0.064766
9 | 0.99397 | -0.11533 | 0 | 0
10 | 0.99065 | -0.17818 | 0 | 0
11 | 0.99354 | -0.12367 | 0.043566 | 0.010919
12 | 0.9914 | -0.1638 | 0.0146 | 0.0036591
13 | 0.98409 | -0.30532 | 0 | 0
14 | 0.98237 | -0.33882 | 0 | 0
15 | 0.98447 | -0.29791 | 0.046225 | 0.011585
16 | 0.98046 | -0.37617 | 0 | 0
17 | 0.98097 | -0.36624 | 0 | 0
18 | 0.98009 | -0.38337 | 0.025815 | 0.0064699
19 | 0.98514 | -0.2849 | 0 | 0
20 | 0.99054 | -0.18028 | 0.0012867 | 0.00032247
21 | 0.97936 | -0.397 | 0 | 0
22 | 0.98001 | -0.38433 | 0.047786 | 0.011976
23 | 0.97821 | -0.4196 | 0.035894 | 0.0089959
24 | 0.98178 | -0.35033 | 0.0071422 | 0.00179
25 | 0.98078 | -0.36992 | 0 | 0
26 | 0.98066 | -0.37226 | 0.0056795 | 0.0014234
27 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0087108 | -0.0021831 | 0.0087109 | 0.0021832 | 1.3921e-07 | 6.1186e-08 | 0.013085 | 0.013085 | 0.013085 | 0.99055 | -0.18021 | 0.99057 | -0.17987 | 3.5949
1 | 0.0084979 | 0.00213 | -0.0084964 | -0.0021294 | 1.4722e-06 | 6.3214e-07 | 0.012765 | 0.012766 | 0.012766 | 0.99057 | -0.17987 | 0.99038 | -0.18351 | 3.507
2 | -0.017209 | -0.0043132 | 0.017226 | 0.0043235 | 1.7513e-05 | 1.0308e-05 | 0.025851 | 0.02585 | 0.025851 | 0.99057 | -0.17987 | 0.99167 | -0.15853 | 7.1019
3 | 0.014604 | 0.0036612 | -0.0146 | -0.0036591 | 3.6663e-06 | 2.0838e-06 | 0.021913 | 0.021914 | 0.021914 | 0.99167 | -0.15853 | 0.9914 | -0.1638 | 6.0202
4 | 0.088785 | 0.022636 | -0.08834 | -0.022352 | 0.00044503 | 0.00028396 | 0.13336 | 0.13336 | 0.13336 | 0.99167 | -0.15853 | 0.98625 | -0.26293 | 36.6374
5 | -0.12062 | -0.03062 | 0.12121 | 0.031002 | 0.00059725 | 0.00038161 | 0.18112 | 0.18112 | 0.18112 | 0.99167 | -0.15853 | 0.99704 | -0.056168 | 49.7592
6 | 0.084229 | 0.021321 | -0.083932 | -0.021132 | 0.00029625 | 0.00018898 | 0.12716 | 0.12716 | 0.12716 | 0.98625 | -0.26293 | 0.98246 | -0.33648 | 34.9333
7 | 0.0041115 | 0.0010302 | -0.0041111 | -0.0010303 | 3.7529e-07 | -9.1658e-08 | 0.0062032 | 0.0062033 | 0.0062033 | 0.98625 | -0.26293 | 0.98615 | -0.26485 | 1.7042
8 | 0.083932 | 0.021132 | -0.083741 | -0.02101 | 0.0001915 | 0.00012216 | 0.12716 | 0.12716 | 0.12716 | 0.98246 | -0.33648 | 0.98001 | -0.38433 | 34.9334
9 | -0.25221 | -0.064327 | 0.2529 | 0.064765 | 0.0006861 | 0.00043843 | 0.37681 | 0.37681 | 0.37681 | 0.99704 | -0.056168 | 1 | 0 | 51.7592
10 | 0.043707 | 0.011007 | -0.043583 | -0.01093 | 0.00012326 | 7.7885e-05 | 0.065248 | 0.065249 | 0.065249 | 0.99704 | -0.056168 | 0.99397 | -0.11533 | 17.9254
11 | 0.087293 | 0.022318 | -0.086781 | -0.021991 | 0.00051198 | 0.00032663 | 0.13044 | 0.13044 | 0.13044 | 0.99704 | -0.056168 | 0.99065 | -0.17818 | 35.834
12 | 0.043583 | 0.01093 | -0.043566 | -0.010919 | 1.7329e-05 | 1.095e-05 | 0.065249 | 0.065249 | 0.065249 | 0.99397 | -0.11533 | 0.99354 | -0.12367 | 17.9254
13 | 0.085494 | 0.02167 | -0.085058 | -0.021391 | 0.000436 | 0.00027814 | 0.1285 | 0.1285 | 0.1285 | 0.99065 | -0.17818 | 0.98514 | -0.2849 | 35.3032
14 | 0.0012868 | 0.00032137 | -0.0012867 | -0.00032247 | 1.2898e-07 | -1.1029e-06 | 0.0019325 | 0.0019329 | 0.0019329 | 0.99065 | -0.17818 | 0.99054 | -0.18028 | 0.53101
15 | 0.038767 | 0.009764 | -0.038705 | -0.009725 | 6.1994e-05 | 3.9067e-05 | 0.058635 | 0.058636 | 0.058636 | 0.98409 | -0.30532 | 0.98237 | -0.33882 | 16.1087
16 | -0.038767 | -0.009764 | 0.03878 | 0.0097727 | 1.3734e-05 | 8.6544e-06 | 0.058635 | 0.058635 | 0.058635 | 0.98409 | -0.30532 | 0.98447 | -0.29791 | 16.1086
17 | 0.038705 | 0.009725 | -0.038683 | -0.0097116 | 2.1251e-05 | 1.3392e-05 | 0.058636 | 0.058636 | 0.058636 | 0.98237 | -0.33882 | 0.98178 | -0.35033 | 16.1087
18 | -0.085005 | -0.021358 | 0.085058 | 0.021391 | 5.2853e-05 | 3.3718e-05 | 0.1285 | 0.1285 | 0.1285 | 0.98447 | -0.29791 | 0.98514 | -0.2849 | 35.3032
19 | -0.025824 | -0.0064754 | 0.025836 | 0.0064829 | 1.2222e-05 | 7.5547e-06 | 0.039193 | 0.039193 | 0.039193 | 0.98046 | -0.37617 | 0.98097 | -0.36624 | 10.7674
20 | 0.025824 | 0.0064754 | -0.025815 | -0.0064699 | 8.8528e-06 | 5.4721e-06 | 0.039193 | 0.039194 | 0.039194 | 0.98046 | -0.37617 | 0.98009 | -0.38337 | 10.7675
21 | -0.031517 | -0.0079066 | 0.031541 | 0.0079216 | 2.3933e-05 | 1.4964e-05 | 0.047811 | 0.047811 | 0.047811 | 0.98097 | -0.36624 | 0.98178 | -0.35033 | 13.1349
22 | 0.0056811 | 0.0014237 | -0.0056801 | -0.0014235 | 9.9334e-07 | 1.8551e-07 | 0.0086175 | 0.0086177 | 0.0086177 | 0.98097 | -0.36624 | 0.98078 | -0.36992 | 2.3675
23 | -0.035933 | -0.0090203 | 0.035955 | 0.0090339 | 2.1732e-05 | 1.3664e-05 | 0.054601 | 0.0546 | 0.054601 | 0.97936 | -0.397 | 0.98001 | -0.38433 | 15.0001
24 | 0.035933 | 0.0090203 | -0.035894 | -0.0089959 | 3.8701e-05 | 2.4334e-05 | 0.054601 | 0.054601 | 0.054601 | 0.97936 | -0.397 | 0.97821 | -0.4196 | 15.0002
25 | 0.0056801 | 0.0014235 | -0.0056795 | -0.0014234 | 6.3345e-07 | 1.184e-07 | 0.0086177 | 0.0086178 | 0.0086178 | 0.98078 | -0.36992 | 0.98066 | -0.37226 | 2.3675

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.33521 | 0.084982

## res_load
| p_mw | q_mvar
0 | 0.0087108 | 0.0021831
1 | 0.0084964 | 0.0021294
2 | 0.0041111 | 0.0010303
3 | 0.080664 | 0.020216
4 | 0.043566 | 0.010919
5 | 0.0146 | 0.0036591
6 | 0.046225 | 0.011585
7 | 0.025815 | 0.0064699
8 | 0.0012867 | 0.00032247
9 | 0.047786 | 0.011976
10 | 0.035894 | 0.0089959
11 | 0.0071422 | 0.00179
12 | 0.0056795 | 0.0014234

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1