## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-669_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-669_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-669_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_261-669_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_261-669_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_261-669_0_4_node_37 | 0.4 | n |  | TRUE
6 | bus_LV_261-669_0_4_node_23 | 0.4 | n |  | TRUE
7 | bus_LV_261-669_0_4_node_17 | 0.4 | n |  | TRUE
8 | bus_LV_261-669_0_4_node_11 | 0.4 | n |  | TRUE
9 | bus_LV_261-669_0_4_node_5 | 0.4 | n |  | TRUE
10 | bus_LV_261-669_0_4_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_261-669_0_4_node_8 | 0.4 | n |  | TRUE
12 | bus_LV_261-669_0_4_node_9 | 0.4 | n |  | TRUE
13 | bus_LV_261-669_0_4_node_13 | 0.4 | n |  | TRUE
14 | bus_LV_261-669_0_4_node_10 | 0.4 | n |  | TRUE
15 | bus_LV_261-669_0_4_node_12 | 0.4 | n |  | TRUE
16 | bus_LV_261-669_0_4_node_26 | 0.4 | n |  | TRUE
17 | bus_LV_261-669_0_4_node_36 | 0.4 | n |  | TRUE
18 | bus_LV_261-669_0_4_node_40 | 0.4 | n |  | TRUE
19 | bus_LV_261-669_0_4_node_27 | 0.4 | n |  | TRUE
20 | bus_LV_261-669_0_4_node_16 | 0.4 | n |  | TRUE
21 | bus_LV_261-669_0_4_node_31 | 0.4 | n |  | TRUE
22 | bus_LV_261-669_0_4_node_18 | 0.4 | n |  | TRUE
23 | bus_LV_261-669_0_4_node_35 | 0.4 | n |  | TRUE
24 | bus_LV_261-669_0_4_node_32 | 0.4 | n |  | TRUE
25 | bus_LV_261-669_0_4_node_19 | 0.4 | n |  | TRUE
26 | bus_LV_261-669_0_4_node_25 | 0.4 | n |  | TRUE
27 | bus_LV_261-669_0_4_node_34 | 0.4 | n |  | TRUE
28 | bus_LV_261-669_0_4_node_20 | 0.4 | n |  | TRUE
29 | bus_LV_261-669_0_4_node_21 | 0.4 | n |  | TRUE
30 | bus_LV_261-669_0_4_node_30 | 0.4 | n |  | TRUE
31 | bus_LV_261-669_0_4_node_39 | 0.4 | n |  | TRUE
32 | bus_LV_261-669_0_4_node_38 | 0.4 | n |  | TRUE
33 | bus_LV_261-669_0_4_node_29 | 0.4 | n |  | TRUE
34 | bus_LV_261-669_0_4_node_28 | 0.4 | n |  | TRUE
35 | bus_LV_261-669_0_4_node_33 | 0.4 | n |  | TRUE
36 | bus_LV_261-669_0_4_node_24 | 0.4 | n |  | TRUE
37 | bus_MV_533_0_node_80 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-669_0_4_load_0 | 0 | 0.015424 | 0.0038657 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-669_0_4_load_1 | 1 | 0.010513 | 0.0026349 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-669_0_4_load_2 | 2 | 0.0077471 | 0.0019416 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-669_0_4_load_3 | 3 | 0.016401 | 0.0041105 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-669_0_4_load_4 | 4 | 0.010449 | 0.0026187 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-669_0_4_load_37 | 5 | 0.037791 | 0.0094713 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-669_0_4_load_23 | 6 | 0.022154 | 0.0055523 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-669_0_4_load_5 | 9 | 0.010617 | 0.0026608 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-669_0_4_load_6 | 10 | 0.032696 | 0.0081943 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-669_0_4_load_8 | 11 | 0.034365 | 0.0086126 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-669_0_4_load_26 | 16 | 0.081305 | 0.020377 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-669_0_4_load_36 | 17 | 0.017852 | 0.0044742 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-669_0_4_load_40 | 18 | 0.0078769 | 0.0019741 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-669_0_4_load_27 | 19 | 0.022982 | 0.0057598 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-669_0_4_load_31 | 21 | 0.02597 | 0.0065087 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-669_0_4_load_35 | 23 | 0.013604 | 0.0034094 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-669_0_4_load_32 | 24 | 0.0099645 | 0.0024973 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_261-669_0_4_load_25 | 26 | 0.017151 | 0.0042984 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_261-669_0_4_load_34 | 27 | 0.010033 | 0.0025145 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_261-669_0_4_load_30 | 30 | 0.014987 | 0.0037562 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_261-669_0_4_load_39 | 31 | 0.01215 | 0.0030451 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_261-669_0_4_load_38 | 32 | 0.012212 | 0.0030607 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_261-669_0_4_load_29 | 33 | 0.012943 | 0.0032437 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_261-669_0_4_load_28 | 34 | 0.012621 | 0.0031632 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_261-669_0_4_load_33 | 35 | 0.0099473 | 0.002493 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_261-669_0_4_load_24 | 36 | 0.027671 | 0.0069349 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 4 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-669_0_4_line_0 |  | 0 | 1 | 0.0034741 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-669_0_4_line_1 |  | 0 | 2 | 0.0085475 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-669_0_4_line_2 |  | 1 | 3 | 0.022423 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-669_0_4_line_3 |  | 2 | 4 | 0.011913 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-669_0_4_line_4 |  | 3 | 5 | 0.022222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_261-669_0_4_line_5 |  | 4 | 6 | 0.021611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
6 | LV_261-669_0_4_line_6 |  | 5 | 7 | 0.0088597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_261-669_0_4_line_7 |  | 6 | 8 | 0.0018394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
8 | LV_261-669_0_4_line_8 |  | 7 | 20 | 0.008834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_261-669_0_4_line_9 |  | 8 | 17 | 0.030647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_261-669_0_4_line_10 |  | 8 | 12 | 0.0105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
11 | LV_261-669_0_4_line_11 |  | 9 | 10 | 0.027581 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_261-669_0_4_line_12 |  | 10 | 11 | 0.027137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-669_0_4_line_13 |  | 11 | 12 | 0.0099418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_261-669_0_4_line_14 |  | 12 | 13 | 0.024027 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
15 | LV_261-669_0_4_line_15 |  | 13 | 19 | 0.0022482 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
16 | LV_261-669_0_4_line_16 |  | 14 | 15 | 0.0091345 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_261-669_0_4_line_17 |  | 14 | 16 | 0.029279 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_261-669_0_4_line_18 |  | 15 | 18 | 0.024906 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_261-669_0_4_line_19 |  | 17 | 32 | 0.015832 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_261-669_0_4_line_20 |  | 18 | 31 | 0.011499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_261-669_0_4_line_21 |  | 19 | 29 | 0.0089934 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
22 | LV_261-669_0_4_line_22 |  | 20 | 21 | 0.015289 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_261-669_0_4_line_23 |  | 22 | 23 | 0.012145 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_261-669_0_4_line_24 |  | 22 | 24 | 0.020233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_261-669_0_4_line_25 |  | 23 | 32 | 0.017756 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_261-669_0_4_line_26 |  | 24 | 35 | 0.013021 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_261-669_0_4_line_27 |  | 25 | 26 | 0.0027524 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_261-669_0_4_line_28 |  | 25 | 27 | 0.010375 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_261-669_0_4_line_29 |  | 26 | 36 | 0.032559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_261-669_0_4_line_30 |  | 27 | 35 | 0.012972 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_261-669_0_4_line_31 |  | 28 | 29 | 0.0088526 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
32 | LV_261-669_0_4_line_32 |  | 28 | 30 | 0.010073 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_261-669_0_4_line_33 |  | 28 | 31 | 0.021914 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_261-669_0_4_line_34 |  | 30 | 34 | 0.016381 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_261-669_0_4_line_35 |  | 33 | 34 | 0.015648 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-669_0_4_trafo_4 | 0.63 MVA 20/0.4 kV | 37 | 4 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11
0 | 2681534.9539 | 1247242.978 | 2681532.3909 | 1247240.6328
1 | 2681534.9539 | 1247242.978 | 2681541.2599 | 1247248.7481
2 | 2681532.3909 | 1247240.6328 | 2681515.8484 | 1247225.4962
3 | 2681550.0491 | 1247256.7904 | 2681541.2599 | 1247248.7481
4 | 2681515.8484 | 1247225.4962 | 2681499.4542 | 1247210.4952
5 | 2681565.5617 | 1247271.7558 | 2681564.0926 | 1247269.6404 | 2681550.0491 | 1247256.7904
6 | 2681492.9179 | 1247204.5144 | 2681499.4542 | 1247210.4952
7 | 2681566.611 | 1247273.2666 | 2681565.5617 | 1247271.7558
8 | 2681492.9179 | 1247204.5144 | 2681484.6774 | 1247207.7591
9 | 2681566.611 | 1247273.2666 | 2681568.0038 | 1247277.4444 | 2681568.042 | 1247281.8036 | 2681567.4269 | 1247285.3311 | 2681565.5785 | 1247289.0084 | 2681557.1369 | 1247300.4106
10 | 2681566.611 | 1247273.2666 | 2681570.1994 | 1247269.3909 | 2681573.742 | 1247265.559
11 | 2681525.9595 | 1247221.9959 | 2681546.3415 | 1247240.5781
12 | 2681566.3952 | 1247258.861 | 2681546.3415 | 1247240.5781
13 | 2681573.742 | 1247265.559 | 2681566.3952 | 1247258.861
14 | 2681573.742 | 1247265.559 | 2681576.1138 | 1247266.1143 | 2681578.547 | 1247266.0477 | 2681580.6323 | 1247265.4648 | 2681582.5276 | 1247264.4235 | 2681584.1263 | 1247262.9666 | 2681585.773 | 1247264.0679 | 2681588.8868 | 1247266.1456 | 2681589.6801 | 1247266.6791 | 2681590.5633 | 1247267.2694 | 2681593.7592 | 1247269.415 | 2681594.6499 | 1247270.0166
15 | 2681594.6499 | 1247270.0166 | 2681593.5893 | 1247271.9989
16 | 2681629.5121 | 1247325.2812 | 2681631.7727 | 1247322.388 | 2681635.1405 | 1247318.0867
17 | 2681635.1405 | 1247318.0867 | 2681634.5489 | 1247317.7116 | 2681612.6213 | 1247299.3831
18 | 2681629.5121 | 1247325.2812 | 2681628.6709 | 1247324.3801 | 2681610.5555 | 1247309.1397
19 | 2681557.1369 | 1247300.4106 | 2681547.7165 | 1247313.135
20 | 2681601.7566 | 1247301.7373 | 2681610.5555 | 1247309.1397
21 | 2681589.3466 | 1247279.9286 | 2681593.5893 | 1247271.9989
22 | 2681484.6774 | 1247207.7591 | 2681470.4549 | 1247213.3684
23 | 2681530.0544 | 1247337.2552 | 2681531.1895 | 1247335.4584 | 2681537.1512 | 1247327.4058
24 | 2681530.0544 | 1247337.2552 | 2681514.534 | 1247324.2748
25 | 2681547.7165 | 1247313.135 | 2681537.1512 | 1247327.4058
26 | 2681514.534 | 1247324.2748 | 2681504.5459 | 1247315.9214
27 | 2681486.6367 | 1247300.9431 | 2681484.5259 | 1247299.1766
28 | 2681486.6367 | 1247300.9431 | 2681494.5956 | 1247307.5994
29 | 2681484.5259 | 1247299.1766 | 2681477.653 | 1247293.4252 | 2681470.5862 | 1247287.1236 | 2681466.1723 | 1247282.9154 | 2681462.883 | 1247278.7672 | 2681461.3745 | 1247276.4848
30 | 2681494.5956 | 1247307.5994 | 2681504.5459 | 1247315.9214
31 | 2681584.9879 | 1247287.6299 | 2681586.9508 | 1247284.4101 | 2681589.3466 | 1247279.9286
32 | 2681584.9879 | 1247287.6299 | 2681579.1073 | 1247295.8076
33 | 2681584.9879 | 1247287.6299 | 2681601.7566 | 1247301.7373
34 | 2681579.1073 | 1247295.8076 | 2681569.5439 | 1247309.1068
35 | 2681560.4085 | 1247321.8108 | 2681569.5439 | 1247309.1068

## bus_geodata
| x | y | coords
0 | 2681534.9539 | 1247242.978
1 | 2681532.3909 | 1247240.6328
2 | 2681541.2599 | 1247248.7481
3 | 2681515.8484 | 1247225.4962
4 | 2681550.0491 | 1247256.7904
5 | 2681499.4542 | 1247210.4952
6 | 2681565.5617 | 1247271.7558
7 | 2681492.9179 | 1247204.5144
8 | 2681566.611 | 1247273.2666
9 | 2681525.9595 | 1247221.9959
10 | 2681546.3415 | 1247240.5781
11 | 2681566.3952 | 1247258.861
12 | 2681573.742 | 1247265.559
13 | 2681594.6498 | 1247270.0166
14 | 2681635.1405 | 1247318.0867
15 | 2681629.5121 | 1247325.2812
16 | 2681612.6213 | 1247299.3831
17 | 2681557.1369 | 1247300.4106
18 | 2681610.5555 | 1247309.1397
19 | 2681593.5893 | 1247271.9989
20 | 2681484.6774 | 1247207.7591
21 | 2681470.4549 | 1247213.3684
22 | 2681530.0544 | 1247337.2552
23 | 2681537.1512 | 1247327.4058
24 | 2681514.534 | 1247324.2748
25 | 2681486.6367 | 1247300.9431
26 | 2681484.5259 | 1247299.1766
27 | 2681494.5956 | 1247307.5994
28 | 2681584.9879 | 1247287.6299
29 | 2681589.3466 | 1247279.9286
30 | 2681579.1073 | 1247295.8076
31 | 2681601.7566 | 1247301.7373
32 | 2681547.7165 | 1247313.135
33 | 2681560.4085 | 1247321.8108
34 | 2681569.5439 | 1247309.1068
35 | 2681504.5459 | 1247315.9214
36 | 2681461.3745 | 1247276.4848
37 | 2681566.611 | 1247273.2666

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99794 | -0.039528 | 0.015424 | 0.0038657
1 | 0.99765 | -0.045043 | 0.010513 | 0.0026349
2 | 0.99876 | -0.023669 | 0.0077471 | 0.0019416
3 | 0.99601 | -0.076572 | 0.016401 | 0.0041105
4 | 1 | 0 | -0.50218 | -0.12682
5 | 0.99472 | -0.1015 | 0.037791 | 0.0094713
6 | 0.99747 | -0.048228 | 0.022154 | 0.0055523
7 | 0.99451 | -0.10555 | 0 | 0
8 | 0.99727 | -0.052106 | 0 | 0
9 | 0.99445 | -0.1064 | 0.010617 | 0.0026608
10 | 0.99472 | -0.10124 | 0.032696 | 0.0081943
11 | 0.99579 | -0.08056 | 0.034365 | 0.0086126
12 | 0.99649 | -0.066996 | 0 | 0
13 | 0.99528 | -0.090201 | 0 | 0
14 | 0.98868 | -0.21757 | 0 | 0
15 | 0.98936 | -0.20433 | 0 | 0
16 | 0.98649 | -0.26011 | 0.081305 | 0.020377
17 | 0.99394 | -0.11593 | 0.017852 | 0.0044742
18 | 0.99122 | -0.16834 | 0.0078769 | 0.0019741
19 | 0.99517 | -0.092376 | 0.022982 | 0.0057598
20 | 0.9943 | -0.1096 | 0 | 0
21 | 0.99394 | -0.1166 | 0.02597 | 0.0065087
22 | 0.9902 | -0.188 | 0 | 0
23 | 0.99104 | -0.17187 | 0.013604 | 0.0034094
24 | 0.98882 | -0.21493 | 0.0099645 | 0.0024973
25 | 0.98696 | -0.25101 | 0 | 0
26 | 0.98685 | -0.25322 | 0.017151 | 0.0042984
27 | 0.98739 | -0.2427 | 0.010033 | 0.0025145
28 | 0.99421 | -0.11093 | 0 | 0
29 | 0.99478 | -0.099864 | 0 | 0
30 | 0.99383 | -0.11814 | 0.014987 | 0.0037562
31 | 0.99217 | -0.15017 | 0.01215 | 0.0030451
32 | 0.99248 | -0.14407 | 0.012212 | 0.0030607
33 | 0.99327 | -0.12911 | 0.012943 | 0.0032437
34 | 0.99345 | -0.12553 | 0.012621 | 0.0031632
35 | 0.98804 | -0.22998 | 0.0099473 | 0.002493
36 | 0.98602 | -0.26936 | 0.027671 | 0.0069349
37 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.090915 | 0.022878 | -0.090891 | -0.022862 | 2.3953e-05 | 1.5284e-05 | 0.13559 | 0.13559 | 0.13559 | 0.99794 | -0.039528 | 0.99765 | -0.045043 | 37.2512
1 | -0.10634 | -0.026743 | 0.10642 | 0.026795 | 8.062e-05 | 5.1485e-05 | 0.15859 | 0.15859 | 0.15859 | 0.99794 | -0.039528 | 0.99876 | -0.023669 | 43.5697
2 | 0.080377 | 0.020227 | -0.080256 | -0.02015 | 0.00012091 | 7.7088e-05 | 0.11991 | 0.11991 | 0.11991 | 0.99765 | -0.045043 | 0.99601 | -0.076572 | 32.9433
3 | -0.11417 | -0.028736 | 0.1143 | 0.028819 | 0.00012932 | 8.2607e-05 | 0.17014 | 0.17014 | 0.17014 | 0.99876 | -0.023669 | 1 | 0 | 46.7406
4 | 0.063855 | 0.01604 | -0.06378 | -0.015992 | 7.5858e-05 | 4.8261e-05 | 0.095411 | 0.095411 | 0.095411 | 0.99601 | -0.076572 | 0.99472 | -0.1015 | 26.2119
5 | 0.38624 | 0.098003 | -0.38534 | -0.097432 | 0.00089361 | 0.00057106 | 0.57515 | 0.57515 | 0.57515 | 1 | 0 | 0.99747 | -0.048228 | 52.6697
6 | 0.025989 | 0.0065202 | -0.025984 | -0.0065171 | 5.022e-06 | 3.0991e-06 | 0.038879 | 0.038879 | 0.038879 | 0.99472 | -0.1015 | 0.99451 | -0.10555 | 10.6811
7 | 0.36319 | 0.091879 | -0.36312 | -0.091836 | 6.7571e-05 | 4.3173e-05 | 0.5421 | 0.5421 | 0.5421 | 0.99747 | -0.048228 | 0.99727 | -0.052106 | 49.6432
8 | 0.025984 | 0.0065171 | -0.025978 | -0.006514 | 5.0075e-06 | 3.0902e-06 | 0.038879 | 0.038879 | 0.038879 | 0.99451 | -0.10555 | 0.9943 | -0.1096 | 10.6811
9 | 0.11933 | 0.030254 | -0.11897 | -0.030021 | 0.00036485 | 0.0002331 | 0.17817 | 0.17818 | 0.17818 | 0.99727 | -0.052106 | 0.99394 | -0.11593 | 48.9492
10 | 0.24379 | 0.061582 | -0.24362 | -0.061471 | 0.00017384 | 0.00011085 | 0.36393 | 0.36393 | 0.36393 | 0.99727 | -0.052106 | 0.99649 | -0.066996 | 33.3269
11 | -0.010617 | -0.0026608 | 0.010619 | 0.0026621 | 2.6101e-06 | 1.3125e-06 | 0.015886 | 0.015886 | 0.015886 | 0.99445 | -0.1064 | 0.99472 | -0.10124 | 4.3642
12 | -0.043315 | -0.010856 | 0.043358 | 0.010883 | 4.2725e-05 | 2.6991e-05 | 0.064796 | 0.064796 | 0.064796 | 0.99472 | -0.10124 | 0.99579 | -0.08056 | 17.801
13 | -0.077723 | -0.019496 | 0.077773 | 0.019528 | 5.0294e-05 | 3.2059e-05 | 0.11615 | 0.11615 | 0.11615 | 0.99579 | -0.08056 | 0.99649 | -0.066996 | 31.9086
14 | 0.16585 | 0.041943 | -0.16566 | -0.041826 | 0.0001844 | 0.00011708 | 0.24778 | 0.24778 | 0.24778 | 0.99649 | -0.066996 | 0.99528 | -0.090201 | 22.6907
15 | 0.16566 | 0.041826 | -0.16564 | -0.041815 | 1.7254e-05 | 1.0955e-05 | 0.24778 | 0.24778 | 0.24778 | 0.99528 | -0.090201 | 0.99517 | -0.092376 | 22.6907
16 | -0.08147 | -0.020482 | 0.081522 | 0.020515 | 5.152e-05 | 3.2856e-05 | 0.12264 | 0.12264 | 0.12264 | 0.98868 | -0.21757 | 0.98936 | -0.20433 | 33.6922
17 | 0.08147 | 0.020482 | -0.081305 | -0.020377 | 0.00016514 | 0.00010532 | 0.12264 | 0.12264 | 0.12264 | 0.98868 | -0.21757 | 0.98649 | -0.26011 | 33.6923
18 | -0.081522 | -0.020515 | 0.081662 | 0.020605 | 0.00014048 | 8.9584e-05 | 0.12264 | 0.12264 | 0.12264 | 0.98936 | -0.20433 | 0.99122 | -0.16834 | 33.6922
19 | 0.10111 | 0.025547 | -0.10098 | -0.02546 | 0.00013618 | 8.6948e-05 | 0.15145 | 0.15145 | 0.15145 | 0.99394 | -0.11593 | 0.99248 | -0.14407 | 41.6069
20 | -0.089539 | -0.022579 | 0.089617 | 0.022629 | 7.7963e-05 | 4.9748e-05 | 0.13446 | 0.13446 | 0.13446 | 0.99122 | -0.16834 | 0.99217 | -0.15017 | 36.9407
21 | 0.14266 | 0.036055 | -0.14261 | -0.036023 | 5.1204e-05 | 3.242e-05 | 0.21342 | 0.21342 | 0.21342 | 0.99517 | -0.092376 | 0.99478 | -0.099864 | 19.5439
22 | 0.025978 | 0.006514 | -0.02597 | -0.0065087 | 8.6663e-06 | 5.3482e-06 | 0.038879 | 0.038879 | 0.038879 | 0.9943 | -0.1096 | 0.99394 | -0.1166 | 10.6811
23 | -0.074986 | -0.018878 | 0.075044 | 0.018915 | 5.7859e-05 | 3.6874e-05 | 0.11271 | 0.11271 | 0.11271 | 0.9902 | -0.188 | 0.99104 | -0.17187 | 30.9655
24 | 0.074986 | 0.018878 | -0.07489 | -0.018816 | 9.6394e-05 | 6.1432e-05 | 0.11271 | 0.11271 | 0.11271 | 0.9902 | -0.188 | 0.98882 | -0.21493 | 30.9655
25 | -0.088648 | -0.022324 | 0.088766 | 0.022399 | 0.00011803 | 7.5311e-05 | 0.13314 | 0.13314 | 0.13314 | 0.99104 | -0.17187 | 0.99248 | -0.14407 | 36.5768
26 | 0.064925 | 0.016319 | -0.064879 | -0.016289 | 4.6626e-05 | 2.9674e-05 | 0.097719 | 0.097719 | 0.097719 | 0.98882 | -0.21493 | 0.98804 | -0.22998 | 26.846
27 | 0.044847 | 0.011249 | -0.044843 | -0.011246 | 4.7194e-06 | 2.9852e-06 | 0.067619 | 0.067619 | 0.067619 | 0.98696 | -0.25101 | 0.98685 | -0.25322 | 18.5766
28 | -0.044847 | -0.011249 | 0.044865 | 0.011261 | 1.779e-05 | 1.1253e-05 | 0.067619 | 0.067619 | 0.067619 | 0.98696 | -0.25101 | 0.98739 | -0.2427 | 18.5766
29 | 0.027692 | 0.0069481 | -0.027671 | -0.0069349 | 2.129e-05 | 1.321e-05 | 0.041758 | 0.041758 | 0.041758 | 0.98685 | -0.25322 | 0.98602 | -0.26936 | 11.472
30 | -0.054898 | -0.013775 | 0.054931 | 0.013796 | 3.33e-05 | 2.1146e-05 | 0.082739 | 0.082738 | 0.082739 | 0.98739 | -0.2427 | 0.98804 | -0.22998 | 22.7304
31 | -0.14253 | -0.035975 | 0.14261 | 0.036023 | 7.5603e-05 | 4.8156e-05 | 0.21342 | 0.21342 | 0.21342 | 0.99421 | -0.11093 | 0.99478 | -0.099864 | 29.3159
32 | 0.040576 | 0.010179 | -0.040562 | -0.01017 | 1.3932e-05 | 8.7861e-06 | 0.060733 | 0.060733 | 0.060733 | 0.99421 | -0.11093 | 0.99383 | -0.11814 | 16.685
33 | 0.10196 | 0.025796 | -0.10177 | -0.025674 | 0.00019158 | 0.00012233 | 0.15269 | 0.15269 | 0.15269 | 0.99421 | -0.11093 | 0.99217 | -0.15017 | 41.9468
34 | 0.025575 | 0.0064137 | -0.025566 | -0.0064081 | 9.0078e-06 | 5.5528e-06 | 0.038294 | 0.038294 | 0.038294 | 0.99383 | -0.11814 | 0.99345 | -0.12553 | 10.5202
35 | -0.012943 | -0.0032437 | 0.012945 | 0.0032449 | 2.206e-06 | 1.2093e-06 | 0.019389 | 0.019389 | 0.019389 | 0.99327 | -0.12911 | 0.99345 | -0.12553 | 5.3268

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.51263 | 0.12944

## res_load
| p_mw | q_mvar
0 | 0.015424 | 0.0038657
1 | 0.010513 | 0.0026349
2 | 0.0077471 | 0.0019416
3 | 0.016401 | 0.0041105
4 | 0.010449 | 0.0026187
5 | 0.037791 | 0.0094713
6 | 0.022154 | 0.0055523
7 | 0.010617 | 0.0026608
8 | 0.032696 | 0.0081943
9 | 0.034365 | 0.0086126
10 | 0.081305 | 0.020377
11 | 0.017852 | 0.0044742
12 | 0.0078769 | 0.0019741
13 | 0.022982 | 0.0057598
14 | 0.02597 | 0.0065087
15 | 0.013604 | 0.0034094
16 | 0.0099645 | 0.0024973
17 | 0.017151 | 0.0042984
18 | 0.010033 | 0.0025145
19 | 0.014987 | 0.0037562
20 | 0.01215 | 0.0030451
21 | 0.012212 | 0.0030607
22 | 0.012943 | 0.0032437
23 | 0.012621 | 0.0031632
24 | 0.0099473 | 0.002493
25 | 0.027671 | 0.0069349

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1