## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-670_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-670_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-670_0_6_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_261-670_0_6_node_22 | 0.4 | n |  | TRUE
4 | bus_LV_261-670_0_6_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_261-670_0_6_node_20 | 0.4 | n |  | TRUE
6 | bus_LV_261-670_0_6_node_39 | 0.4 | n |  | TRUE
7 | bus_LV_261-670_0_6_node_6 | 0.4 | n |  | TRUE
8 | bus_LV_261-670_0_6_node_7 | 0.4 | n |  | TRUE
9 | bus_LV_261-670_0_6_node_17 | 0.4 | n |  | TRUE
10 | bus_LV_261-670_0_6_node_41 | 0.4 | n |  | TRUE
11 | bus_LV_261-670_0_6_node_40 | 0.4 | n |  | TRUE
12 | bus_LV_261-670_0_6_node_11 | 0.4 | n |  | TRUE
13 | bus_LV_261-670_0_6_node_44 | 0.4 | n |  | TRUE
14 | bus_LV_261-670_0_6_node_14 | 0.4 | n |  | TRUE
15 | bus_LV_261-670_0_6_node_12 | 0.4 | n |  | TRUE
16 | bus_LV_261-670_0_6_node_42 | 0.4 | n |  | TRUE
17 | bus_LV_261-670_0_6_node_30 | 0.4 | n |  | TRUE
18 | bus_LV_261-670_0_6_node_32 | 0.4 | n |  | TRUE
19 | bus_LV_261-670_0_6_node_18 | 0.4 | n |  | TRUE
20 | bus_LV_261-670_0_6_node_36 | 0.4 | n |  | TRUE
21 | bus_LV_261-670_0_6_node_21 | 0.4 | n |  | TRUE
22 | bus_LV_261-670_0_6_node_37 | 0.4 | n |  | TRUE
23 | bus_LV_261-670_0_6_node_38 | 0.4 | n |  | TRUE
24 | bus_LV_261-670_0_6_node_33 | 0.4 | n |  | TRUE
25 | bus_LV_261-670_0_6_node_23 | 0.4 | n |  | TRUE
26 | bus_LV_261-670_0_6_node_24 | 0.4 | n |  | TRUE
27 | bus_LV_261-670_0_6_node_43 | 0.4 | n |  | TRUE
28 | bus_LV_261-670_0_6_node_46 | 0.4 | n |  | TRUE
29 | bus_LV_261-670_0_6_node_47 | 0.4 | n |  | TRUE
30 | bus_LV_261-670_0_6_node_28 | 0.4 | n |  | TRUE
31 | bus_LV_261-670_0_6_node_27 | 0.4 | n |  | TRUE
32 | bus_LV_261-670_0_6_node_31 | 0.4 | n |  | TRUE
33 | bus_LV_261-670_0_6_node_45 | 0.4 | n |  | TRUE
34 | bus_LV_261-670_0_6_node_29 | 0.4 | n |  | TRUE
35 | bus_LV_261-670_0_6_node_35 | 0.4 | n |  | TRUE
36 | bus_LV_261-670_0_6_node_34 | 0.4 | n |  | TRUE
37 | bus_MV_533_0_node_103 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-670_0_6_load_0 | 0 | 0.013977 | 0.0035028 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-670_0_6_load_1 | 1 | 0.015152 | 0.0037976 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-670_0_6_load_3 | 2 | 0.033092 | 0.0082936 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-670_0_6_load_39 | 6 | 0.048515 | 0.012159 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-670_0_6_load_41 | 10 | 0.037628 | 0.0094304 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-670_0_6_load_40 | 11 | 0.034419 | 0.0086261 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-670_0_6_load_44 | 13 | 0.0077607 | 0.001945 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-670_0_6_load_42 | 16 | 0.011164 | 0.0027979 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-670_0_6_load_30 | 17 | 0.011462 | 0.0028727 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-670_0_6_load_32 | 18 | 0.0084288 | 0.0021124 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-670_0_6_load_36 | 20 | 0.0099077 | 0.0024831 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-670_0_6_load_37 | 22 | 0.024372 | 0.0061081 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-670_0_6_load_38 | 23 | 0.040419 | 0.01013 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-670_0_6_load_33 | 24 | 0.033764 | 0.0084619 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-670_0_6_load_43 | 27 | 0.0085763 | 0.0021494 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-670_0_6_load_46 | 28 | 0.013522 | 0.003389 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-670_0_6_load_47 | 29 | 0.0089504 | 0.0022432 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_261-670_0_6_load_28 | 30 | 0.021921 | 0.0054938 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_261-670_0_6_load_27 | 31 | 0.014292 | 0.0035819 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_261-670_0_6_load_31 | 32 | 0.019483 | 0.0048829 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_261-670_0_6_load_45 | 33 | 0.0083961 | 0.0021042 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_261-670_0_6_load_29 | 34 | 0.0094345 | 0.0023645 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_261-670_0_6_load_35 | 35 | 0.010093 | 0.0025294 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_261-670_0_6_load_34 | 36 | 0.033775 | 0.0084647 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 19 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-670_0_6_line_0 |  | 0 | 1 | 0.018181 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-670_0_6_line_1 |  | 1 | 2 | 0.02398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-670_0_6_line_2 |  | 2 | 3 | 0.01575 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-670_0_6_line_3 |  | 3 | 23 | 0.02432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
4 | LV_261-670_0_6_line_4 |  | 3 | 19 | 0.014166 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
5 | LV_261-670_0_6_line_5 |  | 4 | 5 | 0.00762 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_261-670_0_6_line_6 |  | 4 | 6 | 0.016595 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_261-670_0_6_line_7 |  | 5 | 21 | 0.013398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_261-670_0_6_line_8 |  | 5 | 23 | 0.025388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
9 | LV_261-670_0_6_line_9 |  | 7 | 8 | 0.042101 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_261-670_0_6_line_10 |  | 7 | 9 | 0.010234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_261-670_0_6_line_11 |  | 7 | 10 | 0.016653 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_261-670_0_6_line_12 |  | 8 | 11 | 0.0087817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-670_0_6_line_13 |  | 9 | 21 | 0.007368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_261-670_0_6_line_14 |  | 9 | 22 | 0.032896 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_261-670_0_6_line_15 |  | 12 | 13 | 0.023485 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_261-670_0_6_line_16 |  | 12 | 14 | 0.017588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
17 | LV_261-670_0_6_line_17 |  | 12 | 15 | 0.013782 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_261-670_0_6_line_18 |  | 12 | 16 | 0.013706 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_261-670_0_6_line_19 |  | 13 | 33 | 0.0096165 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_261-670_0_6_line_20 |  | 14 | 19 | 0.021837 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
21 | LV_261-670_0_6_line_21 |  | 14 | 20 | 0.014445 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_261-670_0_6_line_22 |  | 15 | 17 | 0.016085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_261-670_0_6_line_23 |  | 15 | 18 | 0.018178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_261-670_0_6_line_24 |  | 16 | 27 | 0.011826 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_261-670_0_6_line_25 |  | 17 | 34 | 0.013781 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_261-670_0_6_line_26 |  | 18 | 32 | 0.015134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_261-670_0_6_line_27 |  | 20 | 35 | 0.00048425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_261-670_0_6_line_28 |  | 21 | 24 | 0.020269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_261-670_0_6_line_29 |  | 25 | 26 | 0.016622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_261-670_0_6_line_30 |  | 25 | 27 | 0.016066 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_261-670_0_6_line_31 |  | 25 | 28 | 0.0077629 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_261-670_0_6_line_32 |  | 26 | 29 | 0.010042 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_261-670_0_6_line_33 |  | 30 | 31 | 0.013932 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_261-670_0_6_line_34 |  | 31 | 34 | 0.01909 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_261-670_0_6_line_35 |  | 35 | 36 | 0.015482 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-670_0_6_trafo_18 | 0.63 MVA 20/0.4 kV | 37 | 19 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2681516.5582 | 1247195.1829 | 2681533.471 | 1247188.5125
1 | 2681533.471 | 1247188.5125 | 2681546.8124 | 1247183.2507 | 2681555.8315 | 1247179.85
2 | 2681571.2583 | 1247178.7391 | 2681564.6383 | 1247177.8474 | 2681558.506 | 1247178.8416 | 2681555.8315 | 1247179.85
3 | 2681571.2583 | 1247178.7391 | 2681576.9859 | 1247181.3531 | 2681591.2643 | 1247192.3525
4 | 2681571.2583 | 1247178.7391 | 2681575.3122 | 1247173.4354 | 2681579.8585 | 1247167.4825
5 | 2681611.3764 | 1247207.8456 | 2681612.0308 | 1247209.6893 | 2681612.2231 | 1247211.6379 | 2681611.9712 | 1247213.4691 | 2681611.3128 | 1247215.2057
6 | 2681611.3128 | 1247215.2057 | 2681603.1032 | 1247229.6282
7 | 2681611.3764 | 1247207.8456 | 2681615.1413 | 1247202.6826 | 2681619.2607 | 1247197.0129
8 | 2681611.3764 | 1247207.8456 | 2681591.2643 | 1247192.3525
9 | 2681634.3846 | 1247204.6044 | 2681633.6928 | 1247206.5741 | 2681633.9848 | 1247207.8568 | 2681637.2064 | 1247210.8811 | 2681650.3259 | 1247220.3131 | 2681664.8383 | 1247231.1653
10 | 2681626.0284 | 1247198.6961 | 2681629.7689 | 1247201.3384 | 2681634.3846 | 1247204.6044
11 | 2681634.3846 | 1247204.6044 | 2681643.2536 | 1247190.5092
12 | 2681664.8383 | 1247231.1653 | 2681665.8175 | 1247229.7221 | 2681670.0677 | 1247224.1128
13 | 2681626.0284 | 1247198.6961 | 2681624.02 | 1247199.18 | 2681622.1738 | 1247198.8543 | 2681619.2607 | 1247197.0129
14 | 2681626.0284 | 1247198.6961 | 2681627.3333 | 1247197.7356 | 2681629.2661 | 1247195.6162 | 2681644.2494 | 1247171.4812
15 | 2681558.0822 | 1247145.4113 | 2681553.4472 | 1247144.6359 | 2681549.8549 | 1247143.2966 | 2681544.801 | 1247139.4799 | 2681539.504 | 1247134.6591 | 2681538.4558 | 1247133.648
16 | 2681558.0822 | 1247145.4113 | 2681560.2788 | 1247145.5305 | 2681563.8264 | 1247145.7239 | 2681566.4912 | 1247145.8495 | 2681569.2163 | 1247145.9871 | 2681570.9601 | 1247146.0667 | 2681573.4437 | 1247146.1898 | 2681575.6479 | 1247146.298
17 | 2681552.9901 | 1247158.095 | 2681555.8552 | 1247152.9973 | 2681557.2489 | 1247149.425 | 2681558.0822 | 1247145.4113
18 | 2681558.0822 | 1247145.4113 | 2681558.4006 | 1247142.0354 | 2681560.2351 | 1247134.4329 | 2681561.1723 | 1247132.1213
19 | 2681538.4558 | 1247133.648 | 2681532.7796 | 1247128.173 | 2681531.6153 | 1247126.8933
20 | 2681575.6479 | 1247146.298 | 2681575.7352 | 1247154.772 | 2681577.9164 | 1247161.4959 | 2681578.9887 | 1247164.813 | 2681579.8585 | 1247167.4825
21 | 2681575.6479 | 1247146.298 | 2681575.9178 | 1247140.4085 | 2681576.6588 | 1247135.971 | 2681577.1582 | 1247133.1647 | 2681577.622 | 1247132.0577
22 | 2681552.9901 | 1247158.095 | 2681549.0922 | 1247163.5899 | 2681546.1294 | 1247165.9064 | 2681540.9334 | 1247167.9597
23 | 2681552.9901 | 1247158.095 | 2681548.4507 | 1247154.7635 | 2681540.6621 | 1247148.7631 | 2681538.7181 | 1247146.8679
24 | 2681561.1723 | 1247132.1213 | 2681562.9249 | 1247127.7984 | 2681566.4346 | 1247121.5556
25 | 2681540.9334 | 1247167.9597 | 2681528.1167 | 1247173.0244
26 | 2681538.7181 | 1247146.8679 | 2681532.6566 | 1247140.9585 | 2681528.0484 | 1247136.1376
27 | 2681577.622 | 1247132.0577 | 2681577.8091 | 1247131.6111
28 | 2681619.2607 | 1247197.0129 | 2681603.0415 | 1247184.8572
29 | 2681574.3079 | 1247107.5512 | 2681578.4353 | 1247100.2026 | 2681582.5365 | 1247093.1094
30 | 2681574.3079 | 1247107.5512 | 2681566.4346 | 1247121.5556
31 | 2681574.3079 | 1247107.5512 | 2681569.3109 | 1247101.6103
32 | 2681582.5365 | 1247093.1094 | 2681587.5577 | 1247084.4131
33 | 2681510.3622 | 1247180.0403 | 2681497.4048 | 1247185.1606
34 | 2681510.3622 | 1247180.0403 | 2681528.1167 | 1247173.0244
35 | 2681584.2419 | 1247117.5528 | 2681582.1882 | 1247121.1584 | 2681577.8091 | 1247131.6111

## bus_geodata
| x | y | coords
0 | 2681516.5582 | 1247195.1829
1 | 2681533.471 | 1247188.5125
2 | 2681555.8315 | 1247179.85
3 | 2681571.2583 | 1247178.7391
4 | 2681611.3128 | 1247215.2057
5 | 2681611.3764 | 1247207.8456
6 | 2681603.1032 | 1247229.6282
7 | 2681634.3846 | 1247204.6044
8 | 2681664.8383 | 1247231.1653
9 | 2681626.0284 | 1247198.6961
10 | 2681643.2536 | 1247190.5092
11 | 2681670.0677 | 1247224.1128
12 | 2681558.0822 | 1247145.4113
13 | 2681538.4558 | 1247133.648
14 | 2681575.6479 | 1247146.298
15 | 2681552.9901 | 1247158.095
16 | 2681561.1723 | 1247132.1213
17 | 2681540.9334 | 1247167.9597
18 | 2681538.7181 | 1247146.8679
19 | 2681579.8585 | 1247167.4825
20 | 2681577.622 | 1247132.0577
21 | 2681619.2607 | 1247197.0129
22 | 2681644.2494 | 1247171.4812
23 | 2681591.2643 | 1247192.3525
24 | 2681603.0415 | 1247184.8572
25 | 2681574.3079 | 1247107.5512
26 | 2681582.5365 | 1247093.1094
27 | 2681566.4346 | 1247121.5556
28 | 2681569.3109 | 1247101.6103
29 | 2681587.5577 | 1247084.4131
30 | 2681497.4048 | 1247185.1606
31 | 2681510.3622 | 1247180.0403
32 | 2681528.0484 | 1247136.1376
33 | 2681531.6153 | 1247126.8933
34 | 2681528.1167 | 1247173.0244
35 | 2681577.8091 | 1247131.6111
36 | 2681584.2419 | 1247117.5528
37 | 2681577.9164 | 1247161.4959

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99703 | -0.05701 | 0.013977 | 0.0035028
1 | 0.99726 | -0.052556 | 0.015152 | 0.0037976
2 | 0.9979 | -0.040322 | 0.033092 | 0.0082936
3 | 0.99879 | -0.023183 | 0 | 0
4 | 0.99476 | -0.10062 | 0 | 0
5 | 0.99509 | -0.094115 | 0 | 0
6 | 0.99402 | -0.11482 | 0.048515 | 0.012159
7 | 0.99217 | -0.15047 | 0 | 0
8 | 0.99085 | -0.17616 | 0 | 0
9 | 0.99285 | -0.13742 | 0 | 0
10 | 0.9916 | -0.16157 | 0.037628 | 0.0094304
11 | 0.99057 | -0.18152 | 0.034419 | 0.0086261
12 | 0.99755 | -0.047111 | 0 | 0
13 | 0.9972 | -0.053759 | 0.0077607 | 0.001945
14 | 0.99869 | -0.025048 | 0 | 0
15 | 0.99648 | -0.067657 | 0 | 0
16 | 0.99702 | -0.05725 | 0.011164 | 0.0027979
17 | 0.99564 | -0.083795 | 0.011462 | 0.0028727
18 | 0.99602 | -0.076567 | 0.0084288 | 0.0021124
19 | 1 | 0 | -0.48233 | -0.12131
20 | 0.99799 | -0.038632 | 0.0099077 | 0.0024831
21 | 0.9935 | -0.12487 | 0 | 0
22 | 0.99212 | -0.15161 | 0.024372 | 0.0061081
23 | 0.99717 | -0.05427 | 0.040419 | 0.01013
24 | 0.99287 | -0.13696 | 0.033764 | 0.0084619
25 | 0.99636 | -0.070029 | 0 | 0
26 | 0.99622 | -0.072641 | 0 | 0
27 | 0.99668 | -0.063691 | 0.0085763 | 0.0021494
28 | 0.99626 | -0.071872 | 0.013522 | 0.003389
29 | 0.99614 | -0.07422 | 0.0089504 | 0.0022432
30 | 0.99416 | -0.11242 | 0.021921 | 0.0054938
31 | 0.99444 | -0.10704 | 0.014292 | 0.0035819
32 | 0.99575 | -0.081749 | 0.019483 | 0.0048829
33 | 0.99713 | -0.055175 | 0.0083961 | 0.0021042
34 | 0.99507 | -0.094862 | 0.0094345 | 0.0023645
35 | 0.99797 | -0.039004 | 0.010093 | 0.0025294
36 | 0.99749 | -0.04816 | 0.033775 | 0.0084647
37 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.013977 | -0.0035028 | 0.013979 | 0.0035045 | 2.9664e-06 | 1.6614e-06 | 0.020859 | 0.020859 | 0.020859 | 0.99703 | -0.05701 | 0.99726 | -0.052556 | 5.7305
1 | -0.029132 | -0.0073021 | 0.029149 | 0.0073126 | 1.6991e-05 | 1.0561e-05 | 0.043468 | 0.043468 | 0.043468 | 0.99726 | -0.052556 | 0.9979 | -0.040322 | 11.9418
2 | -0.062241 | -0.015606 | 0.062292 | 0.015639 | 5.088e-05 | 3.2357e-05 | 0.092813 | 0.092813 | 0.092813 | 0.9979 | -0.040322 | 0.99879 | -0.023183 | 25.4981
3 | 0.22023 | 0.055627 | -0.21991 | -0.055419 | 0.00032757 | 0.00020869 | 0.32826 | 0.32826 | 0.32826 | 0.99879 | -0.023183 | 0.99717 | -0.05427 | 30.0606
4 | -0.28253 | -0.071266 | 0.28284 | 0.071466 | 0.00031396 | 0.00020038 | 0.42107 | 0.42107 | 0.42107 | 0.99879 | -0.023183 | 1 | 0 | 38.56
5 | -0.048548 | -0.01218 | 0.048563 | 0.012189 | 1.5072e-05 | 9.547e-06 | 0.072626 | 0.072626 | 0.072626 | 0.99476 | -0.10062 | 0.99509 | -0.094115 | 19.9521
6 | 0.048548 | 0.01218 | -0.048515 | -0.012159 | 3.2824e-05 | 2.0792e-05 | 0.072626 | 0.072626 | 0.072626 | 0.99476 | -0.10062 | 0.99402 | -0.11482 | 19.9521
7 | 0.13058 | 0.032881 | -0.13039 | -0.032759 | 0.00019168 | 0.0001225 | 0.19532 | 0.19532 | 0.19532 | 0.99509 | -0.094115 | 0.9935 | -0.12487 | 53.66
8 | -0.17915 | -0.045071 | 0.17949 | 0.045289 | 0.00034176 | 0.00021807 | 0.26795 | 0.26795 | 0.26795 | 0.99509 | -0.094115 | 0.99717 | -0.05427 | 36.806
9 | 0.03447 | 0.0086581 | -0.034427 | -0.0086316 | 4.2204e-05 | 2.6468e-05 | 0.051703 | 0.051703 | 0.051703 | 0.99217 | -0.15047 | 0.99085 | -0.17616 | 14.2041
10 | -0.072117 | -0.018101 | 0.072162 | 0.01813 | 4.4902e-05 | 2.8605e-05 | 0.10817 | 0.10817 | 0.10817 | 0.99217 | -0.15047 | 0.99285 | -0.13742 | 29.7164
11 | 0.037648 | 0.0094429 | -0.037628 | -0.0094304 | 1.9911e-05 | 1.2528e-05 | 0.056465 | 0.056465 | 0.056465 | 0.99217 | -0.15047 | 0.9916 | -0.16157 | 15.5124
12 | 0.034427 | 0.0086316 | -0.034419 | -0.0086261 | 8.8031e-06 | 5.5209e-06 | 0.051703 | 0.051703 | 0.051703 | 0.99085 | -0.17616 | 0.99057 | -0.18152 | 14.2041
13 | -0.09655 | -0.024248 | 0.096608 | 0.024285 | 5.7869e-05 | 3.6941e-05 | 0.14472 | 0.14472 | 0.14472 | 0.99285 | -0.13742 | 0.9935 | -0.12487 | 39.7585
14 | 0.024388 | 0.0061182 | -0.024372 | -0.0061081 | 1.6483e-05 | 1.0124e-05 | 0.036554 | 0.036554 | 0.036554 | 0.99285 | -0.13742 | 0.99212 | -0.15161 | 10.0422
15 | 0.016162 | 0.0040525 | -0.016157 | -0.0040495 | 5.1193e-06 | 2.9699e-06 | 0.02411 | 0.02411 | 0.02411 | 0.99755 | -0.047111 | 0.9972 | -0.053759 | 6.6236
16 | -0.14363 | -0.036088 | 0.14378 | 0.036185 | 0.00015143 | 9.6453e-05 | 0.21428 | 0.21428 | 0.21428 | 0.99755 | -0.047111 | 0.99869 | -0.025048 | 29.4346
17 | 0.085216 | 0.021432 | -0.085133 | -0.021378 | 8.3542e-05 | 5.3287e-05 | 0.12714 | 0.12714 | 0.12714 | 0.99755 | -0.047111 | 0.99648 | -0.067657 | 34.929
18 | 0.042253 | 0.010604 | -0.042232 | -0.010591 | 2.0421e-05 | 1.289e-05 | 0.063033 | 0.063033 | 0.063033 | 0.99755 | -0.047111 | 0.99702 | -0.05725 | 17.3166
19 | 0.0083966 | 0.0021045 | -0.0083961 | -0.0021042 | 5.6612e-07 | 2.3687e-07 | 0.012529 | 0.012529 | 0.012529 | 0.9972 | -0.053759 | 0.99713 | -0.055175 | 3.4422
20 | -0.19761 | -0.049694 | 0.19784 | 0.049844 | 0.00023672 | 0.00015064 | 0.29449 | 0.29449 | 0.29449 | 0.99869 | -0.025048 | 1 | 0 | 26.9678
21 | 0.053825 | 0.013509 | -0.05379 | -0.013487 | 3.4846e-05 | 2.2113e-05 | 0.080204 | 0.080205 | 0.080205 | 0.99869 | -0.025048 | 0.99799 | -0.038632 | 22.0342
22 | 0.057204 | 0.014373 | -0.05716 | -0.014345 | 4.4027e-05 | 2.7968e-05 | 0.085434 | 0.085434 | 0.085434 | 0.99648 | -0.067657 | 0.99564 | -0.083795 | 23.471
23 | 0.027929 | 0.0070056 | -0.027917 | -0.0069983 | 1.1857e-05 | 7.3521e-06 | 0.041707 | 0.041707 | 0.041707 | 0.99648 | -0.067657 | 0.99602 | -0.076567 | 11.458
24 | 0.031068 | 0.0077932 | -0.031059 | -0.0077872 | 9.5362e-06 | 5.949e-06 | 0.046371 | 0.046371 | 0.046371 | 0.99702 | -0.05725 | 0.99668 | -0.063691 | 12.7393
25 | 0.045698 | 0.011472 | -0.045674 | -0.011457 | 2.411e-05 | 1.5252e-05 | 0.068304 | 0.068304 | 0.068304 | 0.99564 | -0.083795 | 0.99507 | -0.094862 | 18.7648
26 | 0.019488 | 0.0048858 | -0.019483 | -0.0048829 | 4.8109e-06 | 2.8821e-06 | 0.029115 | 0.029115 | 0.029115 | 0.99602 | -0.076567 | 0.99575 | -0.081749 | 7.9986
27 | 0.043883 | 0.011004 | -0.043882 | -0.011003 | 7.7746e-07 | 4.9125e-07 | 0.065432 | 0.065432 | 0.065432 | 0.99799 | -0.038632 | 0.99797 | -0.039004 | 17.9758
28 | 0.033783 | 0.0084741 | -0.033764 | -0.0084619 | 1.9462e-05 | 1.2193e-05 | 0.050601 | 0.050601 | 0.050601 | 0.9935 | -0.12487 | 0.99287 | -0.13696 | 13.9015
29 | 0.0089522 | 0.002244 | -0.0089511 | -0.0022435 | 1.1142e-06 | 4.9664e-07 | 0.01337 | 0.01337 | 0.01337 | 0.99636 | -0.070029 | 0.99622 | -0.072641 | 3.673
30 | -0.022476 | -0.0056337 | 0.022483 | 0.0056378 | 6.7883e-06 | 4.1352e-06 | 0.033567 | 0.033567 | 0.033567 | 0.99636 | -0.070029 | 0.99668 | -0.063691 | 9.2217
31 | 0.013524 | 0.0033897 | -0.013522 | -0.003389 | 1.1875e-06 | 6.5891e-07 | 0.020197 | 0.020197 | 0.020197 | 0.99636 | -0.070029 | 0.99626 | -0.071872 | 5.5487
32 | 0.0089511 | 0.0022435 | -0.0089504 | -0.0022432 | 6.7313e-07 | 3.0007e-07 | 0.01337 | 0.01337 | 0.01337 | 0.99622 | -0.072641 | 0.99614 | -0.07422 | 3.6731
33 | -0.021921 | -0.0054938 | 0.021926 | 0.0054972 | 5.6243e-06 | 3.4188e-06 | 0.03281 | 0.03281 | 0.03281 | 0.99416 | -0.11242 | 0.99444 | -0.10704 | 9.0137
34 | -0.036218 | -0.0090792 | 0.036239 | 0.0090924 | 2.1027e-05 | 1.3209e-05 | 0.054196 | 0.054196 | 0.054196 | 0.99444 | -0.10704 | 0.99507 | -0.094862 | 14.8889
35 | 0.033789 | 0.0084739 | -0.033775 | -0.0084647 | 1.4738e-05 | 9.2302e-06 | 0.050383 | 0.050383 | 0.050383 | 0.99797 | -0.039004 | 0.99749 | -0.04816 | 13.8416

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.48233 | 0.12131

## res_load
| p_mw | q_mvar
0 | 0.013977 | 0.0035028
1 | 0.015152 | 0.0037976
2 | 0.033092 | 0.0082936
3 | 0.048515 | 0.012159
4 | 0.037628 | 0.0094304
5 | 0.034419 | 0.0086261
6 | 0.0077607 | 0.001945
7 | 0.011164 | 0.0027979
8 | 0.011462 | 0.0028727
9 | 0.0084288 | 0.0021124
10 | 0.0099077 | 0.0024831
11 | 0.024372 | 0.0061081
12 | 0.040419 | 0.01013
13 | 0.033764 | 0.0084619
14 | 0.0085763 | 0.0021494
15 | 0.013522 | 0.003389
16 | 0.0089504 | 0.0022432
17 | 0.021921 | 0.0054938
18 | 0.014292 | 0.0035819
19 | 0.019483 | 0.0048829
20 | 0.0083961 | 0.0021042
21 | 0.0094345 | 0.0023645
22 | 0.010093 | 0.0025294
23 | 0.033775 | 0.0084647

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1