## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-676_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-676_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-676_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_261-676_0_4_node_12 | 0.4 | n |  | TRUE
4 | bus_LV_261-676_0_4_node_7 | 0.4 | n |  | TRUE
5 | bus_LV_261-676_0_4_node_9 | 0.4 | n |  | TRUE
6 | bus_LV_261-676_0_4_node_13 | 0.4 | n |  | TRUE
7 | bus_LV_261-676_0_4_node_10 | 0.4 | n |  | TRUE
8 | bus_LV_261-676_0_4_node_32 | 0.4 | n |  | TRUE
9 | bus_LV_261-676_0_4_node_8 | 0.4 | n |  | TRUE
10 | bus_LV_261-676_0_4_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_261-676_0_4_node_11 | 0.4 | n |  | TRUE
12 | bus_LV_261-676_0_4_node_3 | 0.4 | n |  | TRUE
13 | bus_LV_261-676_0_4_node_4 | 0.4 | n |  | TRUE
14 | bus_LV_261-676_0_4_node_5 | 0.4 | n |  | TRUE
15 | bus_LV_261-676_0_4_node_26 | 0.4 | n |  | TRUE
16 | bus_LV_261-676_0_4_node_14 | 0.4 | n |  | TRUE
17 | bus_LV_261-676_0_4_node_15 | 0.4 | n |  | TRUE
18 | bus_LV_261-676_0_4_node_16 | 0.4 | n |  | TRUE
19 | bus_LV_261-676_0_4_node_30 | 0.4 | n |  | TRUE
20 | bus_LV_261-676_0_4_node_28 | 0.4 | n |  | TRUE
21 | bus_LV_261-676_0_4_node_17 | 0.4 | n |  | TRUE
22 | bus_LV_261-676_0_4_node_18 | 0.4 | n |  | TRUE
23 | bus_LV_261-676_0_4_node_19 | 0.4 | n |  | TRUE
24 | bus_LV_261-676_0_4_node_20 | 0.4 | n |  | TRUE
25 | bus_LV_261-676_0_4_node_21 | 0.4 | n |  | TRUE
26 | bus_LV_261-676_0_4_node_34 | 0.4 | n |  | TRUE
27 | bus_LV_261-676_0_4_node_37 | 0.4 | n |  | TRUE
28 | bus_LV_261-676_0_4_node_33 | 0.4 | n |  | TRUE
29 | bus_LV_261-676_0_4_node_36 | 0.4 | n |  | TRUE
30 | bus_LV_261-676_0_4_node_22 | 0.4 | n |  | TRUE
31 | bus_LV_261-676_0_4_node_23 | 0.4 | n |  | TRUE
32 | bus_LV_261-676_0_4_node_24 | 0.4 | n |  | TRUE
33 | bus_LV_261-676_0_4_node_25 | 0.4 | n |  | TRUE
34 | bus_LV_261-676_0_4_node_35 | 0.4 | n |  | TRUE
35 | bus_LV_261-676_0_4_node_27 | 0.4 | n |  | TRUE
36 | bus_LV_261-676_0_4_node_29 | 0.4 | n |  | TRUE
37 | bus_LV_261-676_0_4_node_31 | 0.4 | n |  | TRUE
38 | bus_MV_526_0_node_9 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-676_0_4_load_0 | 0 | 0.02971 | 0.0074461 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-676_0_4_load_1 | 1 | 0.038748 | 0.0097113 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-676_0_4_load_12 | 3 | 0.027144 | 0.0068029 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-676_0_4_load_13 | 6 | 0.031579 | 0.0079145 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-676_0_4_load_32 | 8 | 0.0091587 | 0.0022954 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-676_0_4_load_6 | 10 | 0.0063763 | 0.0015981 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-676_0_4_load_11 | 11 | 0.0073303 | 0.0018371 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-676_0_4_load_3 | 12 | 0.017129 | 0.004293 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-676_0_4_load_4 | 13 | 0.0072451 | 0.0018158 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-676_0_4_load_5 | 14 | 0.024566 | 0.0061569 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-676_0_4_load_26 | 15 | 0.0092433 | 0.0023166 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-676_0_4_load_14 | 16 | 0.0024099 | 0.00060397 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-676_0_4_load_15 | 17 | 0.0031449 | 0.00078819 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-676_0_4_load_16 | 18 | 0.0037496 | 0.00093973 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-676_0_4_load_30 | 19 | 0.0066203 | 0.0016592 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-676_0_4_load_28 | 20 | 0.0066601 | 0.0016692 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-676_0_4_load_17 | 21 | 0.0032293 | 0.00080933 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_261-676_0_4_load_18 | 22 | 0.0032237 | 0.00080793 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_261-676_0_4_load_19 | 23 | 0.0032344 | 0.00081062 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_261-676_0_4_load_20 | 24 | 0.0033391 | 0.00083687 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_261-676_0_4_load_21 | 25 | 0.04522 | 0.011333 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_261-676_0_4_load_34 | 26 | 0.0034382 | 0.0008617 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_261-676_0_4_load_37 | 27 | 0.0095726 | 0.0023991 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_261-676_0_4_load_33 | 28 | 0.0035098 | 0.00087964 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_261-676_0_4_load_36 | 29 | 0.0094582 | 0.0023705 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_261-676_0_4_load_22 | 30 | 0.0092747 | 0.0023245 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_261-676_0_4_load_23 | 31 | 0.0093144 | 0.0023344 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_261-676_0_4_load_24 | 32 | 0.0092645 | 0.0023219 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_261-676_0_4_load_25 | 33 | 0.0094925 | 0.0023791 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_261-676_0_4_load_35 | 34 | 0.0094326 | 0.002364 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_261-676_0_4_load_27 | 35 | 0.0066893 | 0.0016765 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_261-676_0_4_load_31 | 37 | 0.0035365 | 0.00088633 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 3 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-676_0_4_line_0 |  | 0 | 1 | 0.023678 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-676_0_4_line_1 |  | 1 | 2 | 0.05873 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-676_0_4_line_2 |  | 2 | 3 | 0.038936 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
3 | LV_261-676_0_4_line_3 |  | 2 | 4 | 0.19881 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-676_0_4_line_4 |  | 2 | 5 | 0.10048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
5 | LV_261-676_0_4_line_5 |  | 3 | 6 | 0.029232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_261-676_0_4_line_6 |  | 4 | 10 | 0.014955 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_261-676_0_4_line_7 |  | 5 | 11 | 0.0081784 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
8 | LV_261-676_0_4_line_8 |  | 7 | 8 | 0.012373 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
9 | LV_261-676_0_4_line_9 |  | 7 | 9 | 0.11572 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
10 | LV_261-676_0_4_line_10 |  | 8 | 15 | 0.0098214 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
11 | LV_261-676_0_4_line_11 |  | 9 | 11 | 0.028015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
12 | LV_261-676_0_4_line_12 |  | 10 | 14 | 0.022836 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-676_0_4_line_13 |  | 12 | 13 | 0.029582 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_261-676_0_4_line_14 |  | 13 | 14 | 0.00035915 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_261-676_0_4_line_15 |  | 15 | 32 | 0.010245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
16 | LV_261-676_0_4_line_16 |  | 16 | 17 | 0.030487 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_261-676_0_4_line_17 |  | 17 | 18 | 0.00075889 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_261-676_0_4_line_18 |  | 18 | 19 | 0.0013962 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_261-676_0_4_line_19 |  | 19 | 20 | 0.0016067 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_261-676_0_4_line_20 |  | 20 | 35 | 0.0019457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_261-676_0_4_line_21 |  | 21 | 22 | 0.0094921 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_261-676_0_4_line_22 |  | 21 | 23 | 0.0098906 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_261-676_0_4_line_23 |  | 22 | 24 | 0.009945 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_261-676_0_4_line_24 |  | 23 | 25 | 0.0094529 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_261-676_0_4_line_25 |  | 24 | 26 | 0.0099245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_261-676_0_4_line_26 |  | 25 | 27 | 0.034888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_261-676_0_4_line_27 |  | 26 | 28 | 0.0095684 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_261-676_0_4_line_28 |  | 27 | 29 | 0.0099862 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
29 | LV_261-676_0_4_line_29 |  | 28 | 37 | 0.019425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_261-676_0_4_line_30 |  | 29 | 34 | 0.0097767 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
31 | LV_261-676_0_4_line_31 |  | 30 | 31 | 0.010218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
32 | LV_261-676_0_4_line_32 |  | 30 | 32 | 0.0098098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
33 | LV_261-676_0_4_line_33 |  | 31 | 33 | 0.0098253 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
34 | LV_261-676_0_4_line_34 |  | 33 | 34 | 0.010244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
35 | LV_261-676_0_4_line_35 |  | 35 | 36 | 0.0054855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_261-676_0_4_line_36 |  | 36 | 37 | 0.018513 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-676_0_4_trafo_12 | 0.63 MVA 20/0.4 kV | 38 | 3 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15
0 | 2681882.8403 | 1248819.5825 | 2681875.3791 | 1248824.5053 | 2681868.9885 | 1248831.1887 | 2681863.8095 | 1248833.0155
1 | 2681821.4074 | 1248864.9123 | 2681832.9461 | 1248853.452 | 2681835.187 | 1248841.0182 | 2681853.175 | 1248835.5736 | 2681857.2184 | 1248835.3403 | 2681863.8095 | 1248833.0155
2 | 2681821.4074 | 1248864.9123 | 2681810.828 | 1248861.0412 | 2681795.2746 | 1248846.5938 | 2681792.8333 | 1248840.6323
3 | 2681704.8856 | 1248857.7113 | 2681716.334 | 1248858.2584 | 2681727.9158 | 1248861.1757 | 2681734.5983 | 1248863.9699 | 2681741.0019 | 1248868.9173 | 2681747.0221 | 1248875.9277 | 2681765.1089 | 1248903.2528 | 2681781.6178 | 1248922.8727 | 2681797.8691 | 1248909.1868 | 2681795.5632 | 1248906.0972 | 2681800.9771 | 1248902.3135 | 2681817.0736 | 1248891.094 | 2681831.5636 | 1248881.3757 | 2681834.9098 | 1248879.1313 | 2681827.2618 | 1248870.7974 | 2681821.4074 | 1248864.9123
4 | 2681821.4074 | 1248864.9123 | 2681827.2618 | 1248870.7974 | 2681834.9098 | 1248879.1313 | 2681850.7642 | 1248868.4979 | 2681855.3141 | 1248875.8773 | 2681864.5027 | 1248890.7706 | 2681883.1895 | 1248921.0844
5 | 2681774.5768 | 1248818.5765 | 2681789.3718 | 1248832.1795 | 2681792.8333 | 1248840.6323
6 | 2681704.8856 | 1248857.7113 | 2681699.5213 | 1248843.7518
7 | 2681883.1895 | 1248921.0844 | 2681887.4821 | 1248928.0456
8 | 2681884.3195 | 1248979.1984 | 2681873.253 | 1248973.6656
9 | 2681884.3195 | 1248979.1984 | 2681882.4231 | 1248982.5524 | 2681879.3422 | 1248988.0028 | 2681875.7899 | 1248986.0412 | 2681878.7951 | 1248980.6009 | 2681883.1371 | 1248982.7958 | 2681878.3044 | 1248991.5133 | 2681878.5519 | 1248991.639 | 2681890.4668 | 1248998.2974 | 2681910.4806 | 1248985.0307 | 2681919.1004 | 1248979.3234 | 2681902.1865 | 1248951.8917
10 | 2681873.253 | 1248973.6656 | 2681868.6975 | 1248971.388 | 2681864.6738 | 1248968.9047
11 | 2681902.1865 | 1248951.8917 | 2681887.4821 | 1248928.0456
12 | 2681699.5213 | 1248843.7518 | 2681691.3298 | 1248822.4351
13 | 2681680.5898 | 1248794.4863 | 2681691.201 | 1248822.0999
14 | 2681691.201 | 1248822.0999 | 2681691.3298 | 1248822.4351
15 | 2681864.6738 | 1248968.9047 | 2681855.9555 | 1248963.5239
16 | 2681729.6233 | 1248816.9141 | 2681722.7968 | 1248820.0415 | 2681727.7996 | 1248832.3751 | 2681735.1639 | 1248828.9963 | 2681734.5033 | 1248827.5767
17 | 2681729.6233 | 1248816.9141 | 2681730.3133 | 1248816.598
18 | 2681730.3133 | 1248816.598 | 2681731.5826 | 1248816.0165
19 | 2681731.5826 | 1248816.0165 | 2681733.0434 | 1248815.3473
20 | 2681734.8123 | 1248814.5369 | 2681733.0434 | 1248815.3473
21 | 2681773.2406 | 1248886.0219 | 2681770.2579 | 1248881.997 | 2681767.9052 | 1248878.1816
22 | 2681773.2406 | 1248886.0219 | 2681779.1294 | 1248893.9683
23 | 2681767.9052 | 1248878.1816 | 2681762.6855 | 1248869.7166
24 | 2681785.0476 | 1248901.3292 | 2681782.0382 | 1248897.8934 | 2681779.1294 | 1248893.9683
25 | 2681762.6855 | 1248869.7166 | 2681757.4765 | 1248861.269
26 | 2681785.0476 | 1248901.3292 | 2681791.1082 | 1248908.2484 | 2681803.5704 | 1248921.7859 | 2681808.7404 | 1248926.9248
27 | 2681752.7493 | 1248852.9561 | 2681755.0789 | 1248857.3807 | 2681757.4765 | 1248861.269
28 | 2681815.9713 | 1248933.809 | 2681812.2713 | 1248930.4345 | 2681808.7404 | 1248926.9248
29 | 2681752.7493 | 1248852.9561 | 2681749.9718 | 1248847.6809 | 2681746.5082 | 1248840.3722 | 2681744.3245 | 1248835.4599
30 | 2681815.9713 | 1248933.809 | 2681819.6246 | 1248937.1409 | 2681823.4324 | 1248940.1159
31 | 2681847.7599 | 1248958.1404 | 2681839.3966 | 1248952.2693
32 | 2681847.7599 | 1248958.1404 | 2681851.5955 | 1248960.833 | 2681855.9555 | 1248963.5239
33 | 2681831.5044 | 1248946.4224 | 2681835.3734 | 1248949.4451 | 2681839.3966 | 1248952.2693
34 | 2681831.5044 | 1248946.4224 | 2681823.4324 | 1248940.1159
35 | 2681737.3426 | 1248818.3185 | 2681735.7088 | 1248814.1262 | 2681734.8123 | 1248814.5369
36 | 2681737.3426 | 1248818.3185 | 2681741.9524 | 1248830.1241 | 2681744.3245 | 1248835.4599

## bus_geodata
| x | y | coords
0 | 2681882.8403 | 1248819.5825
1 | 2681863.8095 | 1248833.0155
2 | 2681821.4074 | 1248864.9123
3 | 2681792.8333 | 1248840.6323
4 | 2681704.8856 | 1248857.7113
5 | 2681883.1895 | 1248921.0844
6 | 2681774.5768 | 1248818.5765
7 | 2681884.3195 | 1248979.1984
8 | 2681873.253 | 1248973.6656
9 | 2681902.1865 | 1248951.8917
10 | 2681699.5213 | 1248843.7518
11 | 2681887.4821 | 1248928.0456
12 | 2681680.5898 | 1248794.4862
13 | 2681691.201 | 1248822.0999
14 | 2681691.3298 | 1248822.4351
15 | 2681864.6738 | 1248968.9047
16 | 2681734.5033 | 1248827.5767
17 | 2681729.6233 | 1248816.9141
18 | 2681730.3133 | 1248816.598
19 | 2681731.5826 | 1248816.0165
20 | 2681733.0434 | 1248815.3473
21 | 2681773.2406 | 1248886.0219
22 | 2681767.9052 | 1248878.1816
23 | 2681779.1294 | 1248893.9683
24 | 2681762.6855 | 1248869.7166
25 | 2681785.0476 | 1248901.3292
26 | 2681757.4765 | 1248861.269
27 | 2681808.7404 | 1248926.9248
28 | 2681752.7493 | 1248852.9561
29 | 2681815.9713 | 1248933.809
30 | 2681847.7599 | 1248958.1404
31 | 2681839.3966 | 1248952.2693
32 | 2681855.9555 | 1248963.5239
33 | 2681831.5045 | 1248946.4224
34 | 2681823.4324 | 1248940.1159
35 | 2681734.8123 | 1248814.5369
36 | 2681737.3426 | 1248818.3185
37 | 2681744.3245 | 1248835.4599
38 | 2681774.5768 | 1248818.5765

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99192 | -0.15448 | 0.02971 | 0.0074461
1 | 0.99256 | -0.14203 | 0.038748 | 0.0097113
2 | 0.99624 | -0.071156 | 0 | 0
3 | 1 | 0 | -0.3521 | -0.089973
4 | 0.9861 | -0.26629 | 0 | 0
5 | 0.99033 | -0.18333 | 0 | 0
6 | 0.99916 | -0.016103 | 0.031579 | 0.0079145
7 | 0.98173 | -0.34913 | 0 | 0
8 | 0.98103 | -0.36273 | 0.0091587 | 0.0022954
9 | 0.98826 | -0.22284 | 0 | 0
10 | 0.98534 | -0.28113 | 0.0063763 | 0.0015981
11 | 0.98985 | -0.19252 | 0.0073303 | 0.0018371
12 | 0.98383 | -0.31049 | 0.017129 | 0.004293
13 | 0.9843 | -0.30137 | 0.0072451 | 0.0018158
14 | 0.98431 | -0.30122 | 0.024566 | 0.0061569
15 | 0.9805 | -0.373 | 0.0092433 | 0.0023166
16 | 0.97036 | -0.57221 | 0.0024099 | 0.00060397
17 | 0.97043 | -0.57085 | 0.0031449 | 0.00078819
18 | 0.97043 | -0.57077 | 0.0037496 | 0.00093973
19 | 0.97044 | -0.57053 | 0.0066203 | 0.0016592
20 | 0.97047 | -0.57006 | 0.0066601 | 0.0016692
21 | 0.97326 | -0.5148 | 0.0032293 | 0.00080933
22 | 0.97285 | -0.5229 | 0.0032237 | 0.00080793
23 | 0.97372 | -0.50579 | 0.0032344 | 0.00081062
24 | 0.97245 | -0.53079 | 0.0033391 | 0.00083687
25 | 0.97419 | -0.49662 | 0.04522 | 0.011333
26 | 0.97209 | -0.53807 | 0.0034382 | 0.0008617
27 | 0.97738 | -0.43403 | 0.0095726 | 0.0023991
28 | 0.97176 | -0.54448 | 0.0035098 | 0.00087964
29 | 0.97788 | -0.42423 | 0.0094582 | 0.0023705
30 | 0.97951 | -0.39232 | 0.0092747 | 0.0023245
31 | 0.97905 | -0.40132 | 0.0093144 | 0.0023344
32 | 0.97998 | -0.38315 | 0.0092645 | 0.0023219
33 | 0.97863 | -0.40942 | 0.0094925 | 0.0023791
34 | 0.97823 | -0.41728 | 0.0094326 | 0.002364
35 | 0.97051 | -0.56924 | 0.0066893 | 0.0016765
36 | 0.97066 | -0.56627 | 0 | 0
37 | 0.97117 | -0.55625 | 0.0035365 | 0.00088633
38 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.02971 | -0.0074461 | 0.029728 | 0.0074571 | 1.7638e-05 | 1.0982e-05 | 0.04457 | 0.044569 | 0.04457 | 0.99192 | -0.15448 | 0.99256 | -0.14203 | 12.2444
1 | -0.068476 | -0.017168 | 0.068709 | 0.017316 | 0.00023211 | 0.00014779 | 0.10266 | 0.10266 | 0.10266 | 0.99256 | -0.14203 | 0.99624 | -0.071156 | 28.2033
2 | -0.31775 | -0.081341 | 0.31885 | 0.082043 | 0.0010991 | 0.00070189 | 0.47521 | 0.47521 | 0.47521 | 0.99624 | -0.071156 | 1 | 0 | 43.5177
3 | 0.055932 | 0.014254 | -0.055411 | -0.013923 | 0.00052138 | 0.00033112 | 0.083626 | 0.083627 | 0.083627 | 0.99624 | -0.071156 | 0.9861 | -0.26629 | 22.9745
4 | 0.19311 | 0.049771 | -0.19206 | -0.049104 | 0.0010485 | 0.00066716 | 0.28893 | 0.28893 | 0.28893 | 0.99624 | -0.071156 | 0.99033 | -0.18333 | 26.4588
5 | 0.031603 | 0.0079296 | -0.031579 | -0.0079145 | 2.4246e-05 | 1.5134e-05 | 0.047029 | 0.04703 | 0.04703 | 1 | 0 | 0.99916 | -0.016103 | 12.9202
6 | 0.055411 | 0.013923 | -0.055371 | -0.013898 | 3.922e-05 | 2.491e-05 | 0.083627 | 0.083627 | 0.083627 | 0.9861 | -0.26629 | 0.98534 | -0.28113 | 22.9745
7 | 0.19206 | 0.049104 | -0.19198 | -0.049049 | 8.5342e-05 | 5.4303e-05 | 0.28893 | 0.28893 | 0.28893 | 0.99033 | -0.18333 | 0.98985 | -0.19252 | 26.4588
8 | 0.18326 | 0.04633 | -0.18314 | -0.046254 | 0.00011945 | 7.5979e-05 | 0.27791 | 0.27791 | 0.27791 | 0.98173 | -0.34913 | 0.98103 | -0.36273 | 25.4499
9 | -0.18326 | -0.04633 | 0.18438 | 0.04704 | 0.0011172 | 0.00071061 | 0.27791 | 0.27791 | 0.27791 | 0.98173 | -0.34913 | 0.98826 | -0.22284 | 25.4499
10 | 0.17398 | 0.043958 | -0.1739 | -0.043904 | 8.5578e-05 | 5.4398e-05 | 0.26402 | 0.26402 | 0.26402 | 0.98103 | -0.36273 | 0.9805 | -0.373 | 24.1778
11 | -0.18438 | -0.04704 | 0.18465 | 0.047212 | 0.00027047 | 0.00017202 | 0.27791 | 0.27791 | 0.27791 | 0.98826 | -0.22284 | 0.98985 | -0.19252 | 25.4497
12 | 0.048995 | 0.0123 | -0.048948 | -0.01227 | 4.6892e-05 | 2.972e-05 | 0.073998 | 0.073998 | 0.073998 | 0.98534 | -0.28113 | 0.98431 | -0.30122 | 20.3291
13 | -0.017129 | -0.004293 | 0.017137 | 0.0042974 | 7.4458e-06 | 4.3895e-06 | 0.025907 | 0.025907 | 0.025907 | 0.98383 | -0.31049 | 0.9843 | -0.30137 | 7.1174
14 | -0.024382 | -0.0061132 | 0.024382 | 0.0061133 | 1.8299e-07 | 1.1255e-07 | 0.03686 | 0.03686 | 0.03686 | 0.9843 | -0.30137 | 0.98431 | -0.30122 | 10.1264
15 | 0.16465 | 0.041587 | -0.16457 | -0.041536 | 8.0036e-05 | 5.0835e-05 | 0.24999 | 0.24999 | 0.24999 | 0.9805 | -0.373 | 0.97998 | -0.38315 | 22.8932
16 | -0.0024099 | -0.00060397 | 0.00241 | 0.0006037 | 1.5612e-07 | -2.7671e-07 | 0.0036955 | 0.0036953 | 0.0036955 | 0.97036 | -0.57221 | 0.97043 | -0.57085 | 1.0152
17 | -0.0055549 | -0.0013919 | 0.005555 | 0.0013919 | 2.0646e-08 | 3.8377e-09 | 0.0085176 | 0.0085176 | 0.0085176 | 0.97043 | -0.57085 | 0.97043 | -0.57077 | 2.34
18 | -0.0093045 | -0.0023316 | 0.0093046 | 0.0023317 | 1.0658e-07 | 5.0957e-08 | 0.014267 | 0.014267 | 0.014267 | 0.97043 | -0.57077 | 0.97044 | -0.57053 | 3.9195
19 | -0.015925 | -0.0039909 | 0.015925 | 0.0039911 | 3.5925e-07 | 2.1007e-07 | 0.024418 | 0.024418 | 0.024418 | 0.97044 | -0.57053 | 0.97047 | -0.57006 | 6.7083
20 | -0.022585 | -0.0056603 | 0.022586 | 0.0056608 | 8.7503e-07 | 5.3598e-07 | 0.03463 | 0.03463 | 0.03463 | 0.97047 | -0.57006 | 0.97051 | -0.56924 | 9.5138
21 | 0.046419 | 0.01167 | -0.046401 | -0.011659 | 1.7935e-05 | 1.136e-05 | 0.070982 | 0.070982 | 0.070982 | 0.97326 | -0.5148 | 0.97285 | -0.5229 | 19.5006
22 | -0.049648 | -0.012479 | 0.049669 | 0.012493 | 2.1378e-05 | 1.3559e-05 | 0.075919 | 0.075919 | 0.075919 | 0.97326 | -0.5148 | 0.97372 | -0.50579 | 20.857
23 | 0.043177 | 0.010851 | -0.043161 | -0.01084 | 1.627e-05 | 1.029e-05 | 0.066052 | 0.066052 | 0.066052 | 0.97285 | -0.5229 | 0.97245 | -0.53079 | 18.146
24 | -0.052904 | -0.013304 | 0.052927 | 0.013318 | 2.3178e-05 | 1.4717e-05 | 0.080862 | 0.080862 | 0.080862 | 0.97372 | -0.50579 | 0.97419 | -0.49662 | 22.2149
25 | 0.039822 | 0.010004 | -0.039808 | -0.0099948 | 1.3822e-05 | 8.7231e-06 | 0.060942 | 0.060942 | 0.060942 | 0.97245 | -0.53079 | 0.97209 | -0.53807 | 16.7423
26 | -0.098147 | -0.024651 | 0.098441 | 0.024839 | 0.0002941 | 0.00018779 | 0.14993 | 0.14993 | 0.14993 | 0.97419 | -0.49662 | 0.97738 | -0.43403 | 41.1904
27 | 0.03637 | 0.0091331 | -0.036358 | -0.0091261 | 1.1124e-05 | 7.0007e-06 | 0.055679 | 0.055679 | 0.055679 | 0.97209 | -0.53807 | 0.97176 | -0.54448 | 15.2965
28 | -0.10801 | -0.027238 | 0.10806 | 0.027271 | 5.0672e-05 | 3.218e-05 | 0.16451 | 0.16451 | 0.16451 | 0.97738 | -0.43403 | 0.97788 | -0.42423 | 22.5971
29 | 0.032849 | 0.0082465 | -0.03283 | -0.0082349 | 1.8434e-05 | 1.1557e-05 | 0.050305 | 0.050305 | 0.050305 | 0.97176 | -0.54448 | 0.97117 | -0.55625 | 13.82
30 | -0.11752 | -0.029641 | 0.11756 | 0.029666 | 3.9113e-05 | 2.4664e-05 | 0.1789 | 0.1789 | 0.1789 | 0.97788 | -0.42423 | 0.97823 | -0.41728 | 16.3827
31 | 0.14596 | 0.036847 | -0.1459 | -0.036807 | 6.2858e-05 | 3.9843e-05 | 0.22184 | 0.22184 | 0.22184 | 0.97951 | -0.39232 | 0.97905 | -0.40132 | 20.3147
32 | -0.15524 | -0.039171 | 0.15531 | 0.039215 | 6.8253e-05 | 4.3312e-05 | 0.23593 | 0.23593 | 0.23593 | 0.97951 | -0.39232 | 0.97998 | -0.38315 | 21.605
33 | 0.13659 | 0.034472 | -0.13653 | -0.034439 | 5.2972e-05 | 3.3531e-05 | 0.20768 | 0.20768 | 0.20768 | 0.97905 | -0.40132 | 0.97863 | -0.40942 | 19.0184
34 | 0.12704 | 0.03206 | -0.12699 | -0.03203 | 4.7818e-05 | 3.0217e-05 | 0.19325 | 0.19325 | 0.19325 | 0.97863 | -0.40942 | 0.97823 | -0.41728 | 17.6966
35 | -0.029276 | -0.0073373 | 0.02928 | 0.0073399 | 4.1445e-06 | 2.5847e-06 | 0.044886 | 0.044886 | 0.044886 | 0.97051 | -0.56924 | 0.97066 | -0.56627 | 12.3314
36 | -0.02928 | -0.0073399 | 0.029294 | 0.0073486 | 1.3987e-05 | 8.723e-06 | 0.044886 | 0.044886 | 0.044886 | 0.97066 | -0.56627 | 0.97117 | -0.55625 | 12.3314

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.37925 | 0.096776

## res_load
| p_mw | q_mvar
0 | 0.02971 | 0.0074461
1 | 0.038748 | 0.0097113
2 | 0.027144 | 0.0068029
3 | 0.031579 | 0.0079145
4 | 0.0091587 | 0.0022954
5 | 0.0063763 | 0.0015981
6 | 0.0073303 | 0.0018371
7 | 0.017129 | 0.004293
8 | 0.0072451 | 0.0018158
9 | 0.024566 | 0.0061569
10 | 0.0092433 | 0.0023166
11 | 0.0024099 | 0.00060397
12 | 0.0031449 | 0.00078819
13 | 0.0037496 | 0.00093973
14 | 0.0066203 | 0.0016592
15 | 0.0066601 | 0.0016692
16 | 0.0032293 | 0.00080933
17 | 0.0032237 | 0.00080793
18 | 0.0032344 | 0.00081062
19 | 0.0033391 | 0.00083687
20 | 0.04522 | 0.011333
21 | 0.0034382 | 0.0008617
22 | 0.0095726 | 0.0023991
23 | 0.0035098 | 0.00087964
24 | 0.0094582 | 0.0023705
25 | 0.0092747 | 0.0023245
26 | 0.0093144 | 0.0023344
27 | 0.0092645 | 0.0023219
28 | 0.0094925 | 0.0023791
29 | 0.0094326 | 0.002364
30 | 0.0066893 | 0.0016765
31 | 0.0035365 | 0.00088633

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1