## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-680_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-680_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-680_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_261-680_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_261-680_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_261-680_0_3_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_261-680_0_3_node_14 | 0.4 | n |  | TRUE
7 | bus_LV_261-680_0_3_node_50 | 0.4 | n |  | TRUE
8 | bus_LV_261-680_0_3_node_25 | 0.4 | n |  | TRUE
9 | bus_LV_261-680_0_3_node_10 | 0.4 | n |  | TRUE
10 | bus_LV_261-680_0_3_node_15 | 0.4 | n |  | TRUE
11 | bus_LV_261-680_0_3_node_54 | 0.4 | n |  | TRUE
12 | bus_LV_261-680_0_3_node_13 | 0.4 | n |  | TRUE
13 | bus_LV_261-680_0_3_node_18 | 0.4 | n |  | TRUE
14 | bus_LV_261-680_0_3_node_41 | 0.4 | n |  | TRUE
15 | bus_LV_261-680_0_3_node_49 | 0.4 | n |  | TRUE
16 | bus_LV_261-680_0_3_node_48 | 0.4 | n |  | TRUE
17 | bus_LV_261-680_0_3_node_51 | 0.4 | n |  | TRUE
18 | bus_LV_261-680_0_3_node_47 | 0.4 | n |  | TRUE
19 | bus_LV_261-680_0_3_node_52 | 0.4 | n |  | TRUE
20 | bus_LV_261-680_0_3_node_53 | 0.4 | n |  | TRUE
21 | bus_LV_261-680_0_3_node_42 | 0.4 | n |  | TRUE
22 | bus_LV_261-680_0_3_node_46 | 0.4 | n |  | TRUE
23 | bus_LV_261-680_0_3_node_43 | 0.4 | n |  | TRUE
24 | bus_LV_261-680_0_3_node_44 | 0.4 | n |  | TRUE
25 | bus_LV_261-680_0_3_node_45 | 0.4 | n |  | TRUE
26 | bus_MV_536_0_node_14 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-680_0_3_load_0 | 0 | 0.013811 | 0.0034613 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-680_0_3_load_1 | 1 | 0.05675 | 0.014223 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-680_0_3_load_3 | 3 | 0.011781 | 0.0029525 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-680_0_3_load_4 | 4 | 0.059099 | 0.014812 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-680_0_3_load_5 | 5 | 0.044389 | 0.011125 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-680_0_3_load_50 | 7 | 0.011107 | 0.0027836 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-680_0_3_load_54 | 11 | 0.0030481 | 0.00076393 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-680_0_3_load_41 | 14 | 0.0099984 | 0.0025058 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-680_0_3_load_49 | 15 | 0.019606 | 0.0049138 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-680_0_3_load_48 | 16 | 0.013099 | 0.0032829 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-680_0_3_load_51 | 17 | 0.0056432 | 0.0014143 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-680_0_3_load_47 | 18 | 0.0091115 | 0.0022836 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-680_0_3_load_52 | 19 | 0.013965 | 0.0035 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-680_0_3_load_53 | 20 | 0.0088662 | 0.0022221 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-680_0_3_load_42 | 21 | 0.0063513 | 0.0015918 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-680_0_3_load_46 | 22 | 0.025459 | 0.0063807 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-680_0_3_load_43 | 23 | 0.01188 | 0.0029774 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_261-680_0_3_load_44 | 24 | 0.0043044 | 0.0010788 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_261-680_0_3_load_45 | 25 | 0.0063451 | 0.0015902 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 4 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-680_0_3_line_0 |  | 0 | 1 | 0.0096359 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-680_0_3_line_1 |  | 0 | 2 | 0.03002 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-680_0_3_line_2 |  | 1 | 3 | 0.0052869 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-680_0_3_line_3 |  | 2 | 4 | 0.028784 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
4 | LV_261-680_0_3_line_4 |  | 2 | 5 | 0.022107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_261-680_0_3_line_5 |  | 2 | 6 | 0.042379 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_261-680_0_3_line_6 |  | 3 | 7 | 0.0079425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_261-680_0_3_line_7 |  | 4 | 8 | 0.03949 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_261-680_0_3_line_8 |  | 6 | 15 | 0.010239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_261-680_0_3_line_9 |  | 6 | 16 | 0.01921 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_261-680_0_3_line_10 |  | 7 | 17 | 0.0055628 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_261-680_0_3_line_11 |  | 8 | 19 | 0.0066784 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_261-680_0_3_line_12 |  | 9 | 10 | 0.038248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-680_0_3_line_13 |  | 9 | 11 | 0.017898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_261-680_0_3_line_14 |  | 10 | 17 | 0.020271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_261-680_0_3_line_15 |  | 11 | 20 | 0.010307 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_261-680_0_3_line_16 |  | 12 | 13 | 0.055473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_261-680_0_3_line_17 |  | 12 | 14 | 0.019727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_261-680_0_3_line_18 |  | 13 | 18 | 0.017041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_261-680_0_3_line_19 |  | 14 | 21 | 0.011182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_261-680_0_3_line_20 |  | 15 | 22 | 0.012505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_261-680_0_3_line_21 |  | 16 | 18 | 0.01271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_261-680_0_3_line_22 |  | 21 | 23 | 0.0094988 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_261-680_0_3_line_23 |  | 22 | 25 | 0.0016291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_261-680_0_3_line_24 |  | 24 | 25 | 0.0076866 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-680_0_3_trafo_4 | 0.63 MVA 20/0.4 kV | 26 | 4 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2682642.5942 | 1248571.1825 | 2682649.5679 | 1248577.8321
1 | 2682620.8683 | 1248550.4663 | 2682642.5942 | 1248571.1825
2 | 2682653.3941 | 1248581.4805 | 2682649.5679 | 1248577.8321
3 | 2682620.8683 | 1248550.4663 | 2682639.9858 | 1248528.9477
4 | 2682620.8683 | 1248550.4663 | 2682606.0017 | 1248566.8275
5 | 2682620.8683 | 1248550.4663 | 2682617.4474 | 1248547.2051 | 2682638.2615 | 1248523.889 | 2682633.5566 | 1248519.5536
6 | 2682659.1423 | 1248586.9616 | 2682653.3941 | 1248581.4805
7 | 2682667.2667 | 1248501.3545 | 2682665.4882 | 1248503.2422 | 2682664.212 | 1248503.2355 | 2682662.9176 | 1248503.451 | 2682661.9092 | 1248504.2708 | 2682639.9858 | 1248528.9477
8 | 2682633.5566 | 1248519.5536 | 2682626.0327 | 1248512.6092
9 | 2682633.5566 | 1248519.5536 | 2682636.5899 | 1248518.117 | 2682647.4002 | 1248506.5209
10 | 2682659.1423 | 1248586.9616 | 2682663.1682 | 1248590.8004
11 | 2682667.2667 | 1248501.3545 | 2682672.1364 | 1248505.9247
12 | 2682651.6241 | 1248630.8876 | 2682653.6309 | 1248631.0379 | 2682655.48 | 1248630.5744 | 2682658.7514 | 1248627.7735 | 2682661.1877 | 1248623.1152 | 2682667.4259 | 1248616.6084 | 2682677.8389 | 1248604.7893
13 | 2682651.6241 | 1248630.8876 | 2682638.5923 | 1248618.6192
14 | 2682677.8389 | 1248604.7893 | 2682663.1682 | 1248590.8004
15 | 2682631.0876 | 1248611.5542 | 2682638.5923 | 1248618.6192
16 | 2682667.687 | 1248484.7592 | 2682657.866 | 1248475.7824 | 2682635.4722 | 1248455.2996 | 2682626.6878 | 1248447.2601
17 | 2682626.6878 | 1248447.2601 | 2682612.8748 | 1248461.3436
18 | 2682667.687 | 1248484.7592 | 2682656.0668 | 1248497.2243
19 | 2682612.8748 | 1248461.3436 | 2682605.0446 | 1248469.3271
20 | 2682626.0327 | 1248512.6092 | 2682616.8439 | 1248504.128
21 | 2682656.0668 | 1248497.2243 | 2682647.4002 | 1248506.5209
22 | 2682605.0446 | 1248469.3271 | 2682598.3933 | 1248476.1086
23 | 2682615.6467 | 1248503.0231 | 2682616.8439 | 1248504.128
24 | 2682609.9984 | 1248497.8098 | 2682615.6467 | 1248503.0231

## bus_geodata
| x | y | coords
0 | 2682642.5942 | 1248571.1825
1 | 2682649.5679 | 1248577.8321
2 | 2682620.8683 | 1248550.4663
3 | 2682653.3941 | 1248581.4805
4 | 2682639.9858 | 1248528.9477
5 | 2682606.0017 | 1248566.8275
6 | 2682633.5566 | 1248519.5536
7 | 2682659.1423 | 1248586.9616
8 | 2682667.2667 | 1248501.3545
9 | 2682651.6241 | 1248630.8876
10 | 2682677.8389 | 1248604.7893
11 | 2682638.5923 | 1248618.6192
12 | 2682626.6878 | 1248447.2601
13 | 2682667.687 | 1248484.7592
14 | 2682612.8748 | 1248461.3436
15 | 2682626.0327 | 1248512.6092
16 | 2682647.4002 | 1248506.5209
17 | 2682663.1682 | 1248590.8004
18 | 2682656.0668 | 1248497.2243
19 | 2682672.1364 | 1248505.9247
20 | 2682631.0876 | 1248611.5542
21 | 2682605.0446 | 1248469.3271
22 | 2682616.8439 | 1248504.128
23 | 2682598.3933 | 1248476.1086
24 | 2682609.9984 | 1248497.8098
25 | 2682615.6467 | 1248503.0231
26 | 2682620.8683 | 1248550.4663

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99351 | -0.1245 | 0.013811 | 0.0034613
1 | 0.99266 | -0.14105 | 0.05675 | 0.014223
2 | 0.99656 | -0.065838 | 0 | 0
3 | 0.99246 | -0.14484 | 0.011781 | 0.0029525
4 | 1 | 0 | -0.27902 | -0.070231
5 | 0.99567 | -0.083076 | 0.044389 | 0.011125
6 | 0.99244 | -0.14512 | 0 | 0
7 | 0.99226 | -0.14887 | 0.011107 | 0.0027836
8 | 0.9995 | -0.0096176 | 0 | 0
9 | 0.99153 | -0.16295 | 0 | 0
10 | 0.99195 | -0.15488 | 0 | 0
11 | 0.99133 | -0.16673 | 0.0030481 | 0.00076393
12 | 0.98924 | -0.2071 | 0 | 0
13 | 0.99068 | -0.17925 | 0 | 0
14 | 0.98873 | -0.21702 | 0.0099984 | 0.0025058
15 | 0.99192 | -0.15522 | 0.019606 | 0.0049138
16 | 0.99155 | -0.16229 | 0.013099 | 0.0032829
17 | 0.99217 | -0.1506 | 0.0056432 | 0.0014143
18 | 0.99112 | -0.17071 | 0.0091115 | 0.0022836
19 | 0.99942 | -0.011245 | 0.013965 | 0.0035
20 | 0.99125 | -0.16835 | 0.0088662 | 0.0022221
21 | 0.98854 | -0.22066 | 0.0063513 | 0.0015918
22 | 0.99151 | -0.16323 | 0.025459 | 0.0063807
23 | 0.98844 | -0.22267 | 0.01188 | 0.0029774
24 | 0.99146 | -0.16412 | 0.0043044 | 0.0010788
25 | 0.99149 | -0.16353 | 0.0063451 | 0.0015902
26 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.097296 | 0.024422 | -0.097219 | -0.024373 | 7.6747e-05 | 4.8993e-05 | 0.14574 | 0.14574 | 0.14574 | 0.99351 | -0.1245 | 0.99266 | -0.14105 | 40.0375
1 | -0.11111 | -0.027884 | 0.11142 | 0.028083 | 0.00031178 | 0.00019915 | 0.16642 | 0.16642 | 0.16642 | 0.99351 | -0.1245 | 0.99656 | -0.065838 | 45.7201
2 | 0.040469 | 0.01015 | -0.040462 | -0.010146 | 7.2968e-06 | 4.6016e-06 | 0.060667 | 0.060667 | 0.060667 | 0.99266 | -0.14105 | 0.99246 | -0.14484 | 16.6666
3 | -0.26257 | -0.066197 | 0.2634 | 0.066727 | 0.00083014 | 0.00053053 | 0.39219 | 0.39219 | 0.39219 | 0.99656 | -0.065838 | 1 | 0 | 53.8724
4 | 0.044425 | 0.011148 | -0.044389 | -0.011125 | 3.6483e-05 | 2.3061e-05 | 0.066338 | 0.066338 | 0.066338 | 0.99656 | -0.065838 | 0.99567 | -0.083076 | 18.2249
5 | 0.10672 | 0.026966 | -0.10632 | -0.026708 | 0.00040395 | 0.00025798 | 0.15943 | 0.15943 | 0.15943 | 0.99656 | -0.065838 | 0.99244 | -0.14512 | 43.7999
6 | 0.028681 | 0.0071934 | -0.028676 | -0.00719 | 5.5081e-06 | 3.4226e-06 | 0.043004 | 0.043004 | 0.043004 | 0.99246 | -0.14484 | 0.99226 | -0.14887 | 11.8142
7 | 0.013973 | 0.0035042 | -0.013966 | -0.0035006 | 6.4024e-06 | 3.5797e-06 | 0.020792 | 0.020793 | 0.020793 | 1 | 0 | 0.9995 | -0.0096176 | 5.7123
8 | 0.055756 | 0.013989 | -0.055729 | -0.013972 | 2.6837e-05 | 1.7043e-05 | 0.083603 | 0.083603 | 0.083603 | 0.99244 | -0.14512 | 0.99192 | -0.15522 | 22.9679
9 | 0.050563 | 0.012718 | -0.050522 | -0.012692 | 4.1421e-05 | 2.6261e-05 | 0.075829 | 0.075829 | 0.075829 | 0.99244 | -0.14512 | 0.99155 | -0.16229 | 20.832
10 | 0.017569 | 0.0044064 | -0.017567 | -0.0044055 | 1.4482e-06 | 8.5497e-07 | 0.026348 | 0.026348 | 0.026348 | 0.99226 | -0.14887 | 0.99217 | -0.1506 | 7.2384
11 | 0.013966 | 0.0035006 | -0.013965 | -0.0035 | 1.0827e-06 | 6.0543e-07 | 0.020793 | 0.020793 | 0.020793 | 0.9995 | -0.0096176 | 0.99942 | -0.011245 | 5.7123
12 | -0.011917 | -0.0029874 | 0.011922 | 0.0029899 | 4.5877e-06 | 2.4426e-06 | 0.017885 | 0.017884 | 0.017885 | 0.99153 | -0.16295 | 0.99195 | -0.15488 | 4.9134
13 | 0.011917 | 0.0029874 | -0.011915 | -0.0029863 | 2.1468e-06 | 1.1432e-06 | 0.017885 | 0.017885 | 0.017885 | 0.99153 | -0.16295 | 0.99133 | -0.16673 | 4.9134
14 | -0.011922 | -0.0029899 | 0.011924 | 0.0029912 | 2.4314e-06 | 1.2944e-06 | 0.017884 | 0.017884 | 0.017884 | 0.99195 | -0.15488 | 0.99217 | -0.1506 | 4.9133
15 | 0.0088668 | 0.0022224 | -0.0088662 | -0.0022221 | 6.8467e-07 | 3.0531e-07 | 0.013309 | 0.013309 | 0.013309 | 0.99133 | -0.16673 | 0.99125 | -0.16835 | 3.6564
16 | -0.028247 | -0.0070858 | 0.028285 | 0.0071091 | 3.756e-05 | 2.3325e-05 | 0.042492 | 0.042492 | 0.042492 | 0.98924 | -0.2071 | 0.99068 | -0.17925 | 11.6736
17 | 0.028247 | 0.0070858 | -0.028234 | -0.0070775 | 1.3357e-05 | 8.2952e-06 | 0.042492 | 0.042492 | 0.042492 | 0.98924 | -0.2071 | 0.98873 | -0.21702 | 11.6736
18 | -0.028285 | -0.0071091 | 0.028296 | 0.0071163 | 1.1538e-05 | 7.165e-06 | 0.042492 | 0.042492 | 0.042492 | 0.99068 | -0.17925 | 0.99112 | -0.17071 | 11.6735
19 | 0.018236 | 0.0045717 | -0.018232 | -0.0045698 | 3.1585e-06 | 1.8781e-06 | 0.027445 | 0.027445 | 0.027445 | 0.98873 | -0.21702 | 0.98854 | -0.22066 | 7.5398
20 | 0.036123 | 0.0090584 | -0.036109 | -0.0090497 | 1.3771e-05 | 8.6518e-06 | 0.054191 | 0.054191 | 0.054191 | 0.99192 | -0.15522 | 0.99151 | -0.16323 | 14.8876
21 | 0.037423 | 0.0094093 | -0.037408 | -0.0093999 | 1.5038e-05 | 9.4605e-06 | 0.056171 | 0.056171 | 0.056171 | 0.99155 | -0.16229 | 0.99112 | -0.17071 | 15.4316
22 | 0.011881 | 0.002978 | -0.01188 | -0.0029774 | 1.1393e-06 | 6.0741e-07 | 0.017884 | 0.017884 | 0.017884 | 0.98854 | -0.22066 | 0.98844 | -0.22267 | 4.9133
23 | 0.01065 | 0.0026691 | -0.01065 | -0.002669 | 1.5606e-07 | 7.8865e-08 | 0.015983 | 0.015983 | 0.015983 | 0.99151 | -0.16323 | 0.99149 | -0.16353 | 4.3909
24 | -0.0043044 | -0.0010788 | 0.0043045 | 0.0010788 | 1.203e-07 | -2.2141e-08 | 0.0064602 | 0.0064601 | 0.0064602 | 0.99146 | -0.16412 | 0.99149 | -0.16353 | 1.7748

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.33812 | 0.085043

## res_load
| p_mw | q_mvar
0 | 0.013811 | 0.0034613
1 | 0.05675 | 0.014223
2 | 0.011781 | 0.0029525
3 | 0.059099 | 0.014812
4 | 0.044389 | 0.011125
5 | 0.011107 | 0.0027836
6 | 0.0030481 | 0.00076393
7 | 0.0099984 | 0.0025058
8 | 0.019606 | 0.0049138
9 | 0.013099 | 0.0032829
10 | 0.0056432 | 0.0014143
11 | 0.0091115 | 0.0022836
12 | 0.013965 | 0.0035
13 | 0.0088662 | 0.0022221
14 | 0.0063513 | 0.0015918
15 | 0.025459 | 0.0063807
16 | 0.01188 | 0.0029774
17 | 0.0043044 | 0.0010788
18 | 0.0063451 | 0.0015902

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1