## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-697_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-697_0_3_node_2 | 0.4 | n |  | TRUE
2 | bus_LV_261-697_0_3_node_15 | 0.4 | n |  | TRUE
3 | bus_LV_261-697_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_261-697_0_3_node_43 | 0.4 | n |  | TRUE
5 | bus_LV_261-697_0_3_node_4 | 0.4 | n |  | TRUE
6 | bus_LV_261-697_0_3_node_30 | 0.4 | n |  | TRUE
7 | bus_LV_261-697_0_3_node_44 | 0.4 | n |  | TRUE
8 | bus_LV_261-697_0_3_node_7 | 0.4 | n |  | TRUE
9 | bus_LV_261-697_0_3_node_31 | 0.4 | n |  | TRUE
10 | bus_LV_261-697_0_3_node_45 | 0.4 | n |  | TRUE
11 | bus_LV_261-697_0_3_node_8 | 0.4 | n |  | TRUE
12 | bus_LV_261-697_0_3_node_13 | 0.4 | n |  | TRUE
13 | bus_LV_261-697_0_3_node_52 | 0.4 | n |  | TRUE
14 | bus_LV_261-697_0_3_node_10 | 0.4 | n |  | TRUE
15 | bus_LV_261-697_0_3_node_11 | 0.4 | n |  | TRUE
16 | bus_LV_261-697_0_3_node_46 | 0.4 | n |  | TRUE
17 | bus_LV_261-697_0_3_node_47 | 0.4 | n |  | TRUE
18 | bus_LV_261-697_0_3_node_24 | 0.4 | n |  | TRUE
19 | bus_LV_261-697_0_3_node_18 | 0.4 | n |  | TRUE
20 | bus_LV_261-697_0_3_node_41 | 0.4 | n |  | TRUE
21 | bus_LV_261-697_0_3_node_23 | 0.4 | n |  | TRUE
22 | bus_LV_261-697_0_3_node_29 | 0.4 | n |  | TRUE
23 | bus_LV_261-697_0_3_node_50 | 0.4 | n |  | TRUE
24 | bus_LV_261-697_0_3_node_48 | 0.4 | n |  | TRUE
25 | bus_LV_261-697_0_3_node_49 | 0.4 | n |  | TRUE
26 | bus_LV_261-697_0_3_node_42 | 0.4 | n |  | TRUE
27 | bus_LV_261-697_0_3_node_40 | 0.4 | n |  | TRUE
28 | bus_LV_261-697_0_3_node_32 | 0.4 | n |  | TRUE
29 | bus_LV_261-697_0_3_node_16 | 0.4 | n |  | TRUE
30 | bus_LV_261-697_0_3_node_17 | 0.4 | n |  | TRUE
31 | bus_LV_261-697_0_3_node_19 | 0.4 | n |  | TRUE
32 | bus_LV_261-697_0_3_node_22 | 0.4 | n |  | TRUE
33 | bus_LV_261-697_0_3_node_20 | 0.4 | n |  | TRUE
34 | bus_LV_261-697_0_3_node_21 | 0.4 | n |  | TRUE
35 | bus_LV_261-697_0_3_node_25 | 0.4 | n |  | TRUE
36 | bus_LV_261-697_0_3_node_26 | 0.4 | n |  | TRUE
37 | bus_LV_261-697_0_3_node_27 | 0.4 | n |  | TRUE
38 | bus_LV_261-697_0_3_node_28 | 0.4 | n |  | TRUE
39 | bus_LV_261-697_0_3_node_33 | 0.4 | n |  | TRUE
40 | bus_LV_261-697_0_3_node_34 | 0.4 | n |  | TRUE
41 | bus_LV_261-697_0_3_node_51 | 0.4 | n |  | TRUE
42 | bus_LV_261-697_0_3_node_37 | 0.4 | n |  | TRUE
43 | bus_LV_261-697_0_3_node_35 | 0.4 | n |  | TRUE
44 | bus_LV_261-697_0_3_node_36 | 0.4 | n |  | TRUE
45 | bus_LV_261-697_0_3_node_38 | 0.4 | n |  | TRUE
46 | bus_LV_261-697_0_3_node_39 | 0.4 | n |  | TRUE
47 | bus_MV_543_0_node_59 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-697_0_3_load_0 | 0 | 0.014892 | 0.0037323 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-697_0_3_load_43 | 4 | 0.0034388 | 0.00086184 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-697_0_3_load_44 | 7 | 0.011529 | 0.0028894 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-697_0_3_load_45 | 10 | 0.012812 | 0.003211 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-697_0_3_load_52 | 13 | 0.0093546 | 0.0023445 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-697_0_3_load_46 | 16 | 0.089632 | 0.022464 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-697_0_3_load_47 | 17 | 0.0057449 | 0.0014398 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-697_0_3_load_24 | 18 | 0.0019108 | 0.00047889 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-697_0_3_load_18 | 19 | 0.0021138 | 0.00052978 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-697_0_3_load_41 | 20 | 0.0050743 | 0.0012717 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-697_0_3_load_23 | 21 | 0.015373 | 0.0038527 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-697_0_3_load_50 | 23 | 0.012349 | 0.003095 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-697_0_3_load_48 | 24 | 0.014659 | 0.0036739 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-697_0_3_load_49 | 25 | 0.012623 | 0.0031636 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-697_0_3_load_42 | 26 | 0.014093 | 0.0035321 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-697_0_3_load_32 | 28 | 0.0076404 | 0.0019149 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-697_0_3_load_16 | 29 | 0.00091798 | 0.00023007 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_261-697_0_3_load_17 | 30 | 0.00095218 | 0.00023864 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_261-697_0_3_load_19 | 31 | 0.00094103 | 0.00023584 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_261-697_0_3_load_22 | 32 | 0.00092871 | 0.00023276 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_261-697_0_3_load_20 | 33 | 0.0030651 | 0.0007682 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_261-697_0_3_load_21 | 34 | 0.0031494 | 0.00078932 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_261-697_0_3_load_25 | 35 | 0.0029028 | 0.0007275 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_261-697_0_3_load_26 | 36 | 0.0024986 | 0.00062622 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_261-697_0_3_load_27 | 37 | 0.022789 | 0.0057115 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_261-697_0_3_load_34 | 40 | 0.023025 | 0.0057705 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_261-697_0_3_load_51 | 41 | 0.040358 | 0.010115 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_261-697_0_3_load_37 | 42 | 0.04481 | 0.01123 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_261-697_0_3_load_35 | 43 | 0.0020885 | 0.00052343 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_261-697_0_3_load_36 | 44 | 0.0036486 | 0.00091442 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_261-697_0_3_load_38 | 45 | 0.0044685 | 0.0011199 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_261-697_0_3_load_39 | 46 | 0.0019158 | 0.00048013 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 41 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-697_0_3_line_0 |  | 0 | 1 | 0.015645 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-697_0_3_line_1 |  | 1 | 2 | 0.025383 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-697_0_3_line_2 |  | 2 | 18 | 0.017475 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-697_0_3_line_3 |  | 2 | 19 | 0.013235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-697_0_3_line_4 |  | 2 | 3 | 0.033155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_261-697_0_3_line_5 |  | 3 | 4 | 0.036376 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_261-697_0_3_line_6 |  | 4 | 20 | 0.02748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_261-697_0_3_line_7 |  | 5 | 6 | 0.003698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
8 | LV_261-697_0_3_line_8 |  | 5 | 7 | 0.0016365 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
9 | LV_261-697_0_3_line_9 |  | 6 | 21 | 0.012835 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_261-697_0_3_line_10 |  | 6 | 22 | 0.015604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
11 | LV_261-697_0_3_line_11 |  | 7 | 8 | 0.033301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
12 | LV_261-697_0_3_line_12 |  | 8 | 9 | 0.007509 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-697_0_3_line_13 |  | 8 | 10 | 0.015068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_261-697_0_3_line_14 |  | 9 | 23 | 0.023362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_261-697_0_3_line_15 |  | 10 | 12 | 0.012808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_261-697_0_3_line_16 |  | 11 | 12 | 0.010489 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_261-697_0_3_line_17 |  | 11 | 13 | 0.0033825 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_261-697_0_3_line_18 |  | 12 | 14 | 0.015541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_261-697_0_3_line_19 |  | 14 | 15 | 0.015653 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_261-697_0_3_line_20 |  | 14 | 16 | 0.031843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_261-697_0_3_line_21 |  | 15 | 17 | 0.058467 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_261-697_0_3_line_22 |  | 18 | 28 | 0.035241 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_261-697_0_3_line_23 |  | 20 | 46 | 0.016686 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_261-697_0_3_line_24 |  | 21 | 34 | 0.016734 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_261-697_0_3_line_25 |  | 22 | 41 | 0.019069 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
26 | LV_261-697_0_3_line_26 |  | 22 | 37 | 0.01398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
27 | LV_261-697_0_3_line_27 |  | 23 | 25 | 0.0085669 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_261-697_0_3_line_28 |  | 24 | 25 | 0.021879 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_261-697_0_3_line_29 |  | 26 | 27 | 0.014622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_261-697_0_3_line_30 |  | 27 | 45 | 0.016201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_261-697_0_3_line_31 |  | 27 | 42 | 0.023077 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_261-697_0_3_line_32 |  | 29 | 30 | 0.016602 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_261-697_0_3_line_33 |  | 30 | 31 | 0.017859 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_261-697_0_3_line_34 |  | 31 | 32 | 0.009149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_261-697_0_3_line_35 |  | 32 | 33 | 0.016148 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_261-697_0_3_line_36 |  | 33 | 34 | 0.0090435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_261-697_0_3_line_37 |  | 35 | 36 | 0.00095217 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_261-697_0_3_line_38 |  | 35 | 37 | 0.011827 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_261-697_0_3_line_39 |  | 36 | 38 | 0.015438 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_261-697_0_3_line_40 |  | 38 | 39 | 0.012378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_261-697_0_3_line_41 |  | 38 | 40 | 0.029431 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_261-697_0_3_line_42 |  | 39 | 42 | 0.0044285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_261-697_0_3_line_43 |  | 39 | 43 | 0.0094256 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_261-697_0_3_line_44 |  | 43 | 44 | 0.021229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_261-697_0_3_line_45 |  | 45 | 46 | 0.0013203 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-697_0_3_trafo_51 | 0.63 MVA 20/0.4 kV | 47 | 41 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2684108.0024 | 1251306.784 | 2684122.9776 | 1251302.2551
1 | 2684098.8569 | 1251321.4207 | 2684101.3291 | 1251320.6219 | 2684097.1014 | 1251310.0206 | 2684108.0024 | 1251306.784
2 | 2684098.8569 | 1251321.4207 | 2684082.2207 | 1251326.7688
3 | 2684098.8569 | 1251321.4207 | 2684093.7596 | 1251309.207
4 | 2684098.8569 | 1251321.4207 | 2684106.3301 | 1251339.4959 | 2684111.5109 | 1251352.0788
5 | 2684111.5109 | 1251352.0788 | 2684077.2993 | 1251364.4406
6 | 2684051.4569 | 1251373.7854 | 2684071.1527 | 1251366.6616 | 2684077.2993 | 1251364.4406
7 | 2683974.49 | 1251299.7855 | 2683975.5949 | 1251303.3149
8 | 2683974.49 | 1251299.7855 | 2683972.9049 | 1251300.1925
9 | 2683975.5949 | 1251303.3149 | 2683987.9598 | 1251299.8742
10 | 2683981.5123 | 1251317.7429 | 2683976.5842 | 1251306.4758 | 2683975.5949 | 1251303.3149
11 | 2683940.6042 | 1251308.2897 | 2683959.0571 | 1251303.7476 | 2683972.9049 | 1251300.1925
12 | 2683940.6042 | 1251308.2897 | 2683942.244 | 1251315.6184
13 | 2683940.6042 | 1251308.2897 | 2683937.32 | 1251293.5837
14 | 2683942.244 | 1251315.6184 | 2683943.1595 | 1251319.7344 | 2683946.486 | 1251338.5887
15 | 2683934.1872 | 1251281.1674 | 2683936.2672 | 1251288.8692 | 2683937.32 | 1251293.5837
16 | 2683934.1872 | 1251281.1674 | 2683934.1115 | 1251277.9861 | 2683934.9902 | 1251274.5738 | 2683937.0208 | 1251271.3779
17 | 2683937.0208 | 1251271.3779 | 2683939.8928 | 1251269.5911
18 | 2683920.4525 | 1251284.6199 | 2683922.5119 | 1251283.6483 | 2683924.7207 | 1251283.8575 | 2683925.4352 | 1251285.113 | 2683926.8179 | 1251284.4877 | 2683929.2186 | 1251283.4098 | 2683934.1872 | 1251281.1674
19 | 2683914.6497 | 1251270.0824 | 2683917.3544 | 1251276.848 | 2683919.986 | 1251283.4457 | 2683920.4525 | 1251284.6199
20 | 2683920.4525 | 1251284.6199 | 2683892.0454 | 1251299.0076
21 | 2683914.6497 | 1251270.0824 | 2683903.325 | 1251274.9924 | 2683874.126 | 1251288.8895 | 2683861.8559 | 1251295.1741
22 | 2684048.6709 | 1251337.5542 | 2684082.2207 | 1251326.7688
23 | 2684051.4569 | 1251373.7854 | 2684045.1502 | 1251376.0665 | 2684036.1733 | 1251380.4258
24 | 2683987.9598 | 1251299.8742 | 2683991.2598 | 1251298.9559 | 2684004.138 | 1251295.598
25 | 2683981.5123 | 1251317.7429 | 2683963.1444 | 1251322.8646
26 | 2683981.5123 | 1251317.7429 | 2683987.358 | 1251330.4421
27 | 2683947.7082 | 1251347.0633 | 2683947.268 | 1251343.0212 | 2683946.486 | 1251338.5887
28 | 2683948.9587 | 1251368.873 | 2683948.9912 | 1251358.8463 | 2683947.7082 | 1251347.0633
29 | 2684021.1307 | 1251389.3581 | 2684030.8715 | 1251400.2625
30 | 2684021.1307 | 1251389.3581 | 2684031.4456 | 1251382.7216 | 2684034.9857 | 1251381.0025
31 | 2684021.1307 | 1251389.3581 | 2684017.8876 | 1251384.9088 | 2684007.9279 | 1251370.4335
32 | 2684070.7813 | 1251278.5098 | 2684068.5988 | 1251279.0931 | 2684054.6717 | 1251282.5194
33 | 2684054.6717 | 1251282.5194 | 2684046.8051 | 1251284.4547 | 2684037.3644 | 1251286.9226
34 | 2684028.5129 | 1251289.2365 | 2684037.3644 | 1251286.9226
35 | 2684012.8889 | 1251293.3162 | 2684019.8544 | 1251291.5 | 2684028.5129 | 1251289.2365
36 | 2684012.8889 | 1251293.3162 | 2684004.138 | 1251295.598
37 | 2683992.3755 | 1251341.1517 | 2683992.7825 | 1251342.0126
38 | 2683987.358 | 1251330.4421 | 2683989.055 | 1251334.1287 | 2683992.3755 | 1251341.1517
39 | 2683999.3813 | 1251355.9692 | 2683992.7825 | 1251342.0126
40 | 2684005.4177 | 1251366.7851 | 2683999.3813 | 1251355.9692
41 | 2683999.3813 | 1251355.9692 | 2683981.7181 | 1251363.9138 | 2683977.9838 | 1251354.5687
42 | 2684005.4177 | 1251366.7851 | 2684007.9279 | 1251370.4335
43 | 2684005.4177 | 1251366.7851 | 2684014.3231 | 1251363.697
44 | 2684014.3231 | 1251363.697 | 2684019.0648 | 1251362.0528 | 2684033.2626 | 1251354.2289
45 | 2684034.9857 | 1251381.0025 | 2684036.1733 | 1251380.4258

## bus_geodata
| x | y | coords
0 | 2684122.9776 | 1251302.2551
1 | 2684108.0024 | 1251306.784
2 | 2684098.8569 | 1251321.4207
3 | 2684111.5109 | 1251352.0788
4 | 2684077.2993 | 1251364.4406
5 | 2683974.49 | 1251299.7855
6 | 2683975.5949 | 1251303.3149
7 | 2683972.9049 | 1251300.1925
8 | 2683940.6042 | 1251308.2897
9 | 2683942.244 | 1251315.6184
10 | 2683937.32 | 1251293.5837
11 | 2683937.0208 | 1251271.3779
12 | 2683934.1872 | 1251281.1674
13 | 2683939.8928 | 1251269.5911
14 | 2683920.4525 | 1251284.6199
15 | 2683914.6497 | 1251270.0824
16 | 2683892.0454 | 1251299.0076
17 | 2683861.8559 | 1251295.1741
18 | 2684082.2207 | 1251326.7688
19 | 2684093.7597 | 1251309.207
20 | 2684051.4569 | 1251373.7854
21 | 2683987.9598 | 1251299.8742
22 | 2683981.5123 | 1251317.7429
23 | 2683946.486 | 1251338.5887
24 | 2683948.9587 | 1251368.873
25 | 2683947.7082 | 1251347.0633
26 | 2684030.8715 | 1251400.2625
27 | 2684021.1307 | 1251389.3581
28 | 2684048.6709 | 1251337.5542
29 | 2684070.7813 | 1251278.5098
30 | 2684054.6717 | 1251282.5194
31 | 2684037.3644 | 1251286.9226
32 | 2684028.5129 | 1251289.2365
33 | 2684012.8889 | 1251293.3162
34 | 2684004.138 | 1251295.598
35 | 2683992.3755 | 1251341.1517
36 | 2683992.7825 | 1251342.0126
37 | 2683987.358 | 1251330.4421
38 | 2683999.3813 | 1251355.9692
39 | 2684005.4177 | 1251366.7851
40 | 2683977.9838 | 1251354.5687
41 | 2683963.1444 | 1251322.8646
42 | 2684007.9279 | 1251370.4335
43 | 2684014.3231 | 1251363.697
44 | 2684033.2626 | 1251354.2289
45 | 2684034.9857 | 1251381.0025
46 | 2684036.1733 | 1251380.4258
47 | 2683949.5838 | 1251326.6306

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98655 | -0.25919 | 0.014892 | 0.0037323
1 | 0.98677 | -0.25502 | 0 | 0
2 | 0.98712 | -0.24826 | 0 | 0
3 | 0.98792 | -0.23252 | 0 | 0
4 | 0.98881 | -0.21528 | 0.0034388 | 0.00086184
5 | 0.99684 | -0.060333 | 0 | 0
6 | 0.99703 | -0.056686 | 0 | 0
7 | 0.99676 | -0.061947 | 0.011529 | 0.0028894
8 | 0.99436 | -0.10797 | 0 | 0
9 | 0.99409 | -0.11322 | 0 | 0
10 | 0.99273 | -0.13924 | 0.012812 | 0.003211
11 | 0.99141 | -0.16474 | 0 | 0
12 | 0.9915 | -0.163 | 0 | 0
13 | 0.99138 | -0.1653 | 0.0093546 | 0.0023445
14 | 0.99014 | -0.18932 | 0 | 0
15 | 0.99006 | -0.19091 | 0 | 0
16 | 0.98752 | -0.24019 | 0.089632 | 0.022464
17 | 0.98975 | -0.19689 | 0.0057449 | 0.0014398
18 | 0.98696 | -0.25124 | 0.0019108 | 0.00047889
19 | 0.98709 | -0.24876 | 0.0021138 | 0.00052978
20 | 0.98957 | -0.20059 | 0.0050743 | 0.0012717
21 | 0.99674 | -0.062388 | 0.015373 | 0.0038527
22 | 0.99796 | -0.039006 | 0 | 0
23 | 0.99324 | -0.12956 | 0.012349 | 0.003095
24 | 0.99273 | -0.13936 | 0.014659 | 0.0036739
25 | 0.99303 | -0.13369 | 0.012623 | 0.0031636
26 | 0.99058 | -0.18104 | 0.014093 | 0.0035321
27 | 0.99077 | -0.17738 | 0 | 0
28 | 0.98671 | -0.25606 | 0.0076404 | 0.0019149
29 | 0.99641 | -0.068758 | 0.00091798 | 0.00023007
30 | 0.99642 | -0.06849 | 0.00095218 | 0.00023864
31 | 0.99645 | -0.067904 | 0.00094103 | 0.00023584
32 | 0.99647 | -0.067452 | 0.00092871 | 0.00023276
33 | 0.99653 | -0.066392 | 0.0030651 | 0.0007682
34 | 0.99658 | -0.065311 | 0.0031494 | 0.00078932
35 | 0.99549 | -0.086214 | 0.0029028 | 0.0007275
36 | 0.99538 | -0.088418 | 0.0024986 | 0.00062622
37 | 0.99695 | -0.058271 | 0.022789 | 0.0057115
38 | 0.99355 | -0.12355 | 0 | 0
39 | 0.99235 | -0.14677 | 0 | 0
40 | 0.99294 | -0.13552 | 0.023025 | 0.0057705
41 | 1 | 0 | -0.35581 | -0.08985
42 | 0.99194 | -0.15464 | 0.04481 | 0.01123
43 | 0.9923 | -0.14773 | 0.0020885 | 0.00052343
44 | 0.99223 | -0.1491 | 0.0036486 | 0.00091442
45 | 0.99015 | -0.18931 | 0.0044685 | 0.0011199
46 | 0.99011 | -0.19018 | 0.0019158 | 0.00048013
47 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.014892 | -0.0037323 | 0.014895 | 0.003734 | 2.96e-06 | 1.6946e-06 | 0.022462 | 0.022462 | 0.022462 | 0.98655 | -0.25919 | 0.98677 | -0.25502 | 6.1708
1 | -0.014895 | -0.003734 | 0.0149 | 0.0037368 | 4.8023e-06 | 2.7491e-06 | 0.022462 | 0.022462 | 0.022462 | 0.98677 | -0.25502 | 0.98712 | -0.24826 | 6.1708
2 | 0.0095543 | 0.0023951 | -0.0095529 | -0.0023944 | 1.3594e-06 | 6.4663e-07 | 0.014403 | 0.014403 | 0.014403 | 0.98712 | -0.24826 | 0.98696 | -0.25124 | 3.9568
3 | 0.0021139 | 0.00052964 | -0.0021138 | -0.00052978 | 5.0395e-08 | -1.3693e-07 | 0.0031865 | 0.0031866 | 0.0031866 | 0.98712 | -0.24826 | 0.98709 | -0.24876 | 0.87543
4 | -0.026568 | -0.0066615 | 0.026588 | 0.0066738 | 1.9944e-05 | 1.234e-05 | 0.040051 | 0.040051 | 0.040051 | 0.98712 | -0.24826 | 0.98792 | -0.23252 | 11.003
5 | -0.026588 | -0.0066738 | 0.02661 | 0.0066874 | 2.1881e-05 | 1.3538e-05 | 0.040051 | 0.040051 | 0.040051 | 0.98792 | -0.23252 | 0.98881 | -0.21528 | 11.0029
6 | -0.030049 | -0.0075492 | 0.03007 | 0.0075623 | 2.1077e-05 | 1.3137e-05 | 0.045225 | 0.045225 | 0.045225 | 0.98881 | -0.21528 | 0.98957 | -0.20059 | 12.4246
7 | -0.16975 | -0.042949 | 0.16978 | 0.042968 | 2.9714e-05 | 1.8872e-05 | 0.25354 | 0.25354 | 0.25354 | 0.99684 | -0.060333 | 0.99703 | -0.056686 | 23.2178
8 | 0.16975 | 0.042949 | -0.16974 | -0.042941 | 1.315e-05 | 8.3517e-06 | 0.25354 | 0.25354 | 0.25354 | 0.99684 | -0.060333 | 0.99676 | -0.061947 | 23.2178
9 | 0.025336 | 0.006352 | -0.025329 | -0.0063478 | 6.8819e-06 | 4.2371e-06 | 0.037813 | 0.037814 | 0.037814 | 0.99703 | -0.056686 | 0.99674 | -0.062388 | 10.3883
10 | -0.19512 | -0.04932 | 0.19528 | 0.049425 | 0.00016557 | 0.00010535 | 0.29135 | 0.29135 | 0.29135 | 0.99703 | -0.056686 | 0.99796 | -0.039006 | 26.6806
11 | 0.15821 | 0.040051 | -0.15786 | -0.039829 | 0.00034872 | 0.00022232 | 0.23633 | 0.23633 | 0.23633 | 0.99676 | -0.061947 | 0.99436 | -0.10797 | 32.4626
12 | 0.039681 | 0.0099638 | -0.039671 | -0.0099576 | 9.9314e-06 | 6.2587e-06 | 0.059388 | 0.059388 | 0.059388 | 0.99436 | -0.10797 | 0.99409 | -0.11322 | 16.3154
13 | 0.11818 | 0.029865 | -0.118 | -0.029752 | 0.00017691 | 0.00011303 | 0.17694 | 0.17694 | 0.17694 | 0.99436 | -0.10797 | 0.99273 | -0.13924 | 48.6099
14 | 0.039671 | 0.0099576 | -0.03964 | -0.0099381 | 3.0899e-05 | 1.9473e-05 | 0.059388 | 0.059388 | 0.059388 | 0.99409 | -0.11322 | 0.99324 | -0.12956 | 16.3154
15 | 0.10519 | 0.026541 | -0.10507 | -0.026465 | 0.0001195 | 7.6318e-05 | 0.15774 | 0.15774 | 0.15774 | 0.99273 | -0.13924 | 0.9915 | -0.163 | 43.334
16 | -0.0093548 | -0.0023446 | 0.0093556 | 0.002345 | 7.7543e-07 | 3.6101e-07 | 0.014041 | 0.014041 | 0.014041 | 0.99141 | -0.16474 | 0.9915 | -0.163 | 3.8573
17 | 0.0093548 | 0.0023446 | -0.0093546 | -0.0023445 | 2.5006e-07 | 1.1642e-07 | 0.014041 | 0.014041 | 0.014041 | 0.99141 | -0.16474 | 0.99138 | -0.1653 | 3.8573
18 | 0.095717 | 0.02412 | -0.095596 | -0.024043 | 0.00012033 | 7.6813e-05 | 0.1437 | 0.1437 | 0.1437 | 0.9915 | -0.163 | 0.99014 | -0.18932 | 39.4767
19 | 0.005747 | 0.0014402 | -0.0057465 | -0.0014401 | 4.3785e-07 | 7.8915e-08 | 0.0086367 | 0.0086368 | 0.0086368 | 0.99014 | -0.18932 | 0.99006 | -0.19091 | 2.3727
20 | 0.089849 | 0.022603 | -0.089632 | -0.022464 | 0.00021782 | 0.00013899 | 0.13506 | 0.13506 | 0.13506 | 0.99014 | -0.18932 | 0.98752 | -0.24019 | 37.104
21 | 0.0057465 | 0.0014401 | -0.0057449 | -0.0014398 | 1.6355e-06 | 2.951e-07 | 0.0086368 | 0.008637 | 0.008637 | 0.99006 | -0.19091 | 0.98975 | -0.19689 | 2.3728
22 | 0.0076421 | 0.0019155 | -0.0076404 | -0.0019149 | 1.7544e-06 | 6.7258e-07 | 0.011522 | 0.011522 | 0.011522 | 0.98696 | -0.25124 | 0.98671 | -0.25606 | 3.1654
23 | -0.035144 | -0.0088341 | 0.035162 | 0.0088451 | 1.7481e-05 | 1.0973e-05 | 0.052856 | 0.052855 | 0.052856 | 0.98957 | -0.20059 | 0.99011 | -0.19018 | 14.5208
24 | 0.0099565 | 0.002495 | -0.0099551 | -0.0024944 | 1.3864e-06 | 6.6924e-07 | 0.014864 | 0.014864 | 0.014864 | 0.99674 | -0.062388 | 0.99658 | -0.065311 | 4.0835
25 | -0.3535 | -0.089426 | 0.35416 | 0.08985 | 0.00066296 | 0.00042354 | 0.52739 | 0.52739 | 0.52739 | 0.99796 | -0.039006 | 1 | 0 | 48.2955
26 | 0.15822 | 0.040001 | -0.15807 | -0.039908 | 0.00014604 | 9.3099e-05 | 0.23604 | 0.23604 | 0.23604 | 0.99796 | -0.039006 | 0.99695 | -0.058271 | 32.4224
27 | 0.027291 | 0.0068431 | -0.027286 | -0.0068397 | 5.3707e-06 | 3.3264e-06 | 0.040887 | 0.040887 | 0.040887 | 0.99324 | -0.12956 | 0.99303 | -0.13369 | 11.2328
28 | -0.014659 | -0.0036739 | 0.014663 | 0.0036761 | 3.9611e-06 | 2.2521e-06 | 0.021972 | 0.021972 | 0.021972 | 0.99273 | -0.13936 | 0.99303 | -0.13369 | 6.0363
29 | -0.014093 | -0.0035321 | 0.014096 | 0.0035335 | 2.4574e-06 | 1.3845e-06 | 0.02117 | 0.02117 | 0.02117 | 0.99058 | -0.18104 | 0.99077 | -0.17738 | 5.816
30 | 0.041571 | 0.010461 | -0.041547 | -0.010446 | 2.3694e-05 | 1.4955e-05 | 0.06245 | 0.06245 | 0.06245 | 0.99077 | -0.17738 | 0.99015 | -0.18931 | 17.1566
31 | -0.055667 | -0.013995 | 0.055727 | 0.014033 | 6.0509e-05 | 3.8429e-05 | 0.08362 | 0.08362 | 0.08362 | 0.99077 | -0.17738 | 0.99194 | -0.15464 | 22.9726
32 | -0.00091798 | -0.00023007 | 0.00091799 | 0.00022986 | 1.1699e-08 | -2.0875e-07 | 0.0013709 | 0.0013708 | 0.0013709 | 0.99641 | -0.068758 | 0.99642 | -0.06849 | 0.37662
33 | -0.0018702 | -0.0004685 | 0.0018702 | 0.0004683 | 5.2233e-08 | -1.992e-07 | 0.0027928 | 0.0027927 | 0.0027928 | 0.99642 | -0.06849 | 0.99645 | -0.067904 | 0.76724
34 | -0.0028113 | -0.00070414 | 0.0028113 | 0.00070406 | 6.0461e-08 | -8.0486e-08 | 0.0041979 | 0.0041979 | 0.0041979 | 0.99645 | -0.067904 | 0.99647 | -0.067452 | 1.1533
35 | -0.00374 | -0.00093682 | 0.0037402 | 0.00093673 | 1.8886e-07 | -8.9496e-08 | 0.0055847 | 0.0055847 | 0.0055847 | 0.99647 | -0.067452 | 0.99653 | -0.066392 | 1.5343
36 | -0.0068054 | -0.0017049 | 0.0068057 | 0.001705 | 3.5018e-07 | 1.0628e-07 | 0.010162 | 0.010161 | 0.010162 | 0.99653 | -0.066392 | 0.99658 | -0.065311 | 2.7916
37 | 0.1322 | 0.033353 | -0.13218 | -0.033344 | 1.3953e-05 | 8.9178e-06 | 0.19768 | 0.19768 | 0.19768 | 0.99549 | -0.086214 | 0.99538 | -0.088418 | 54.3083
38 | -0.1351 | -0.034081 | 0.13528 | 0.034197 | 0.00018101 | 0.00011569 | 0.20202 | 0.20202 | 0.20202 | 0.99549 | -0.086214 | 0.99695 | -0.058271 | 55.5003
39 | 0.12969 | 0.032718 | -0.12947 | -0.032579 | 0.00021777 | 0.00013917 | 0.19395 | 0.19395 | 0.19395 | 0.99538 | -0.088418 | 0.99355 | -0.12355 | 53.2821
40 | 0.10643 | 0.026801 | -0.10631 | -0.026725 | 0.000118 | 7.5361e-05 | 0.15944 | 0.15944 | 0.15944 | 0.99355 | -0.12355 | 0.99235 | -0.14677 | 43.8029
41 | 0.023038 | 0.0057785 | -0.023025 | -0.0057705 | 1.314e-05 | 8.0286e-06 | 0.034504 | 0.034505 | 0.034505 | 0.99355 | -0.12355 | 0.99294 | -0.13552 | 9.4793
42 | 0.10057 | 0.025287 | -0.10054 | -0.025263 | 3.7785e-05 | 2.4125e-05 | 0.15084 | 0.15084 | 0.15084 | 0.99235 | -0.14677 | 0.99194 | -0.15464 | 41.4393
43 | 0.0057376 | 0.0014378 | -0.0057374 | -0.0014377 | 2.6163e-07 | 4.5675e-08 | 0.0086034 | 0.0086034 | 0.0086034 | 0.99235 | -0.14677 | 0.9923 | -0.14773 | 2.3636
44 | 0.0036488 | 0.0009143 | -0.0036486 | -0.00091442 | 2.3834e-07 | -1.2168e-07 | 0.0054716 | 0.0054717 | 0.0054717 | 0.9923 | -0.14773 | 0.99223 | -0.1491 | 1.5032
45 | 0.037079 | 0.0093262 | -0.037077 | -0.0093252 | 1.538e-06 | 9.6733e-07 | 0.055735 | 0.055735 | 0.055735 | 0.99015 | -0.18931 | 0.99011 | -0.19018 | 15.3117

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.39617 | 0.099965

## res_load
| p_mw | q_mvar
0 | 0.014892 | 0.0037323
1 | 0.0034388 | 0.00086184
2 | 0.011529 | 0.0028894
3 | 0.012812 | 0.003211
4 | 0.0093546 | 0.0023445
5 | 0.089632 | 0.022464
6 | 0.0057449 | 0.0014398
7 | 0.0019108 | 0.00047889
8 | 0.0021138 | 0.00052978
9 | 0.0050743 | 0.0012717
10 | 0.015373 | 0.0038527
11 | 0.012349 | 0.003095
12 | 0.014659 | 0.0036739
13 | 0.012623 | 0.0031636
14 | 0.014093 | 0.0035321
15 | 0.0076404 | 0.0019149
16 | 0.00091798 | 0.00023007
17 | 0.00095218 | 0.00023864
18 | 0.00094103 | 0.00023584
19 | 0.00092871 | 0.00023276
20 | 0.0030651 | 0.0007682
21 | 0.0031494 | 0.00078932
22 | 0.0029028 | 0.0007275
23 | 0.0024986 | 0.00062622
24 | 0.022789 | 0.0057115
25 | 0.023025 | 0.0057705
26 | 0.040358 | 0.010115
27 | 0.04481 | 0.01123
28 | 0.0020885 | 0.00052343
29 | 0.0036486 | 0.00091442
30 | 0.0044685 | 0.0011199
31 | 0.0019158 | 0.00048013

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1