## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-702_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-702_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-702_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_261-702_0_3_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_261-702_0_3_node_17 | 0.4 | n |  | TRUE
5 | bus_LV_261-702_0_3_node_157 | 0.4 | n |  | TRUE
6 | bus_LV_261-702_0_3_node_37 | 0.4 | n |  | TRUE
7 | bus_LV_261-702_0_3_node_158 | 0.4 | n |  | TRUE
8 | bus_LV_261-702_0_3_node_12 | 0.4 | n |  | TRUE
9 | bus_LV_261-702_0_3_node_155 | 0.4 | n |  | TRUE
10 | bus_LV_261-702_0_3_node_13 | 0.4 | n |  | TRUE
11 | bus_LV_261-702_0_3_node_156 | 0.4 | n |  | TRUE
12 | bus_LV_261-702_0_3_node_5 | 0.4 | n |  | TRUE
13 | bus_LV_261-702_0_3_node_6 | 0.4 | n |  | TRUE
14 | bus_LV_261-702_0_3_node_7 | 0.4 | n |  | TRUE
15 | bus_LV_261-702_0_3_node_8 | 0.4 | n |  | TRUE
16 | bus_LV_261-702_0_3_node_9 | 0.4 | n |  | TRUE
17 | bus_LV_261-702_0_3_node_63 | 0.4 | n |  | TRUE
18 | bus_LV_261-702_0_3_node_60 | 0.4 | n |  | TRUE
19 | bus_LV_261-702_0_3_node_128 | 0.4 | n |  | TRUE
20 | bus_LV_261-702_0_3_node_76 | 0.4 | n |  | TRUE
21 | bus_LV_261-702_0_3_node_61 | 0.4 | n |  | TRUE
22 | bus_LV_261-702_0_3_node_82 | 0.4 | n |  | TRUE
23 | bus_LV_261-702_0_3_node_10 | 0.4 | n |  | TRUE
24 | bus_LV_261-702_0_3_node_11 | 0.4 | n |  | TRUE
25 | bus_LV_261-702_0_3_node_16 | 0.4 | n |  | TRUE
26 | bus_LV_261-702_0_3_node_18 | 0.4 | n |  | TRUE
27 | bus_LV_261-702_0_3_node_59 | 0.4 | n |  | TRUE
28 | bus_LV_261-702_0_3_node_97 | 0.4 | n |  | TRUE
29 | bus_LV_261-702_0_3_node_20 | 0.4 | n |  | TRUE
30 | bus_LV_261-702_0_3_node_46 | 0.4 | n |  | TRUE
31 | bus_LV_261-702_0_3_node_21 | 0.4 | n |  | TRUE
32 | bus_LV_261-702_0_3_node_92 | 0.4 | n |  | TRUE
33 | bus_LV_261-702_0_3_node_23 | 0.4 | n |  | TRUE
34 | bus_LV_261-702_0_3_node_140 | 0.4 | n |  | TRUE
35 | bus_LV_261-702_0_3_node_22 | 0.4 | n |  | TRUE
36 | bus_LV_261-702_0_3_node_138 | 0.4 | n |  | TRUE
37 | bus_LV_261-702_0_3_node_139 | 0.4 | n |  | TRUE
38 | bus_LV_261-702_0_3_node_130 | 0.4 | n |  | TRUE
39 | bus_LV_261-702_0_3_node_25 | 0.4 | n |  | TRUE
40 | bus_LV_261-702_0_3_node_93 | 0.4 | n |  | TRUE
41 | bus_LV_261-702_0_3_node_45 | 0.4 | n |  | TRUE
42 | bus_LV_261-702_0_3_node_94 | 0.4 | n |  | TRUE
43 | bus_LV_261-702_0_3_node_26 | 0.4 | n |  | TRUE
44 | bus_LV_261-702_0_3_node_134 | 0.4 | n |  | TRUE
45 | bus_LV_261-702_0_3_node_32 | 0.4 | n |  | TRUE
46 | bus_LV_261-702_0_3_node_133 | 0.4 | n |  | TRUE
47 | bus_LV_261-702_0_3_node_28 | 0.4 | n |  | TRUE
48 | bus_LV_261-702_0_3_node_50 | 0.4 | n |  | TRUE
49 | bus_LV_261-702_0_3_node_29 | 0.4 | n |  | TRUE
50 | bus_LV_261-702_0_3_node_48 | 0.4 | n |  | TRUE
51 | bus_LV_261-702_0_3_node_95 | 0.4 | n |  | TRUE
52 | bus_LV_261-702_0_3_node_30 | 0.4 | n |  | TRUE
53 | bus_LV_261-702_0_3_node_39 | 0.4 | n |  | TRUE
54 | bus_LV_261-702_0_3_node_31 | 0.4 | n |  | TRUE
55 | bus_LV_261-702_0_3_node_33 | 0.4 | n |  | TRUE
56 | bus_LV_261-702_0_3_node_85 | 0.4 | n |  | TRUE
57 | bus_LV_261-702_0_3_node_41 | 0.4 | n |  | TRUE
58 | bus_LV_261-702_0_3_node_38 | 0.4 | n |  | TRUE
59 | bus_LV_261-702_0_3_node_36 | 0.4 | n |  | TRUE
60 | bus_LV_261-702_0_3_node_126 | 0.4 | n |  | TRUE
61 | bus_LV_261-702_0_3_node_124 | 0.4 | n |  | TRUE
62 | bus_LV_261-702_0_3_node_154 | 0.4 | n |  | TRUE
63 | bus_LV_261-702_0_3_node_153 | 0.4 | n |  | TRUE
64 | bus_LV_261-702_0_3_node_87 | 0.4 | n |  | TRUE
65 | bus_LV_261-702_0_3_node_86 | 0.4 | n |  | TRUE
66 | bus_LV_261-702_0_3_node_58 | 0.4 | n |  | TRUE
67 | bus_LV_261-702_0_3_node_96 | 0.4 | n |  | TRUE
68 | bus_LV_261-702_0_3_node_148 | 0.4 | n |  | TRUE
69 | bus_LV_261-702_0_3_node_44 | 0.4 | n |  | TRUE
70 | bus_LV_261-702_0_3_node_143 | 0.4 | n |  | TRUE
71 | bus_LV_261-702_0_3_node_131 | 0.4 | n |  | TRUE
72 | bus_LV_261-702_0_3_node_160 | 0.4 | n |  | TRUE
73 | bus_LV_261-702_0_3_node_67 | 0.4 | n |  | TRUE
74 | bus_LV_261-702_0_3_node_43 | 0.4 | n |  | TRUE
75 | bus_LV_261-702_0_3_node_137 | 0.4 | n |  | TRUE
76 | bus_LV_261-702_0_3_node_135 | 0.4 | n |  | TRUE
77 | bus_LV_261-702_0_3_node_49 | 0.4 | n |  | TRUE
78 | bus_LV_261-702_0_3_node_161 | 0.4 | n |  | TRUE
79 | bus_LV_261-702_0_3_node_55 | 0.4 | n |  | TRUE
80 | bus_LV_261-702_0_3_node_40 | 0.4 | n |  | TRUE
81 | bus_LV_261-702_0_3_node_65 | 0.4 | n |  | TRUE
82 | bus_LV_261-702_0_3_node_64 | 0.4 | n |  | TRUE
83 | bus_LV_261-702_0_3_node_104 | 0.4 | n |  | TRUE
84 | bus_LV_261-702_0_3_node_105 | 0.4 | n |  | TRUE
85 | bus_LV_261-702_0_3_node_127 | 0.4 | n |  | TRUE
86 | bus_LV_261-702_0_3_node_150 | 0.4 | n |  | TRUE
87 | bus_LV_261-702_0_3_node_151 | 0.4 | n |  | TRUE
88 | bus_LV_261-702_0_3_node_42 | 0.4 | n |  | TRUE
89 | bus_LV_261-702_0_3_node_47 | 0.4 | n |  | TRUE
90 | bus_LV_261-702_0_3_node_121 | 0.4 | n |  | TRUE
91 | bus_LV_261-702_0_3_node_145 | 0.4 | n |  | TRUE
92 | bus_LV_261-702_0_3_node_57 | 0.4 | n |  | TRUE
93 | bus_LV_261-702_0_3_node_147 | 0.4 | n |  | TRUE
94 | bus_LV_261-702_0_3_node_120 | 0.4 | n |  | TRUE
95 | bus_LV_261-702_0_3_node_144 | 0.4 | n |  | TRUE
96 | bus_LV_261-702_0_3_node_51 | 0.4 | n |  | TRUE
97 | bus_LV_261-702_0_3_node_53 | 0.4 | n |  | TRUE
98 | bus_LV_261-702_0_3_node_52 | 0.4 | n |  | TRUE
99 | bus_LV_261-702_0_3_node_54 | 0.4 | n |  | TRUE
100 | bus_LV_261-702_0_3_node_56 | 0.4 | n |  | TRUE
101 | bus_LV_261-702_0_3_node_66 | 0.4 | n |  | TRUE
102 | bus_LV_261-702_0_3_node_159 | 0.4 | n |  | TRUE
103 | bus_LV_261-702_0_3_node_62 | 0.4 | n |  | TRUE
104 | bus_LV_261-702_0_3_node_74 | 0.4 | n |  | TRUE
105 | bus_LV_261-702_0_3_node_68 | 0.4 | n |  | TRUE
106 | bus_LV_261-702_0_3_node_69 | 0.4 | n |  | TRUE
107 | bus_LV_261-702_0_3_node_70 | 0.4 | n |  | TRUE
108 | bus_LV_261-702_0_3_node_71 | 0.4 | n |  | TRUE
109 | bus_LV_261-702_0_3_node_72 | 0.4 | n |  | TRUE
110 | bus_LV_261-702_0_3_node_78 | 0.4 | n |  | TRUE
111 | bus_LV_261-702_0_3_node_108 | 0.4 | n |  | TRUE
112 | bus_LV_261-702_0_3_node_110 | 0.4 | n |  | TRUE
113 | bus_LV_261-702_0_3_node_106 | 0.4 | n |  | TRUE
114 | bus_LV_261-702_0_3_node_73 | 0.4 | n |  | TRUE
115 | bus_LV_261-702_0_3_node_75 | 0.4 | n |  | TRUE
116 | bus_LV_261-702_0_3_node_77 | 0.4 | n |  | TRUE
117 | bus_LV_261-702_0_3_node_101 | 0.4 | n |  | TRUE
118 | bus_LV_261-702_0_3_node_99 | 0.4 | n |  | TRUE
119 | bus_LV_261-702_0_3_node_111 | 0.4 | n |  | TRUE
120 | bus_LV_261-702_0_3_node_79 | 0.4 | n |  | TRUE
121 | bus_LV_261-702_0_3_node_80 | 0.4 | n |  | TRUE
122 | bus_LV_261-702_0_3_node_81 | 0.4 | n |  | TRUE
123 | bus_LV_261-702_0_3_node_83 | 0.4 | n |  | TRUE
124 | bus_LV_261-702_0_3_node_84 | 0.4 | n |  | TRUE
125 | bus_LV_261-702_0_3_node_89 | 0.4 | n |  | TRUE
126 | bus_LV_261-702_0_3_node_129 | 0.4 | n |  | TRUE
127 | bus_LV_261-702_0_3_node_88 | 0.4 | n |  | TRUE
128 | bus_LV_261-702_0_3_node_90 | 0.4 | n |  | TRUE
129 | bus_LV_261-702_0_3_node_91 | 0.4 | n |  | TRUE
130 | bus_LV_261-702_0_3_node_122 | 0.4 | n |  | TRUE
131 | bus_LV_261-702_0_3_node_115 | 0.4 | n |  | TRUE
132 | bus_LV_261-702_0_3_node_125 | 0.4 | n |  | TRUE
133 | bus_LV_261-702_0_3_node_114 | 0.4 | n |  | TRUE
134 | bus_LV_261-702_0_3_node_98 | 0.4 | n |  | TRUE
135 | bus_LV_261-702_0_3_node_100 | 0.4 | n |  | TRUE
136 | bus_LV_261-702_0_3_node_102 | 0.4 | n |  | TRUE
137 | bus_LV_261-702_0_3_node_103 | 0.4 | n |  | TRUE
138 | bus_LV_261-702_0_3_node_113 | 0.4 | n |  | TRUE
139 | bus_LV_261-702_0_3_node_112 | 0.4 | n |  | TRUE
140 | bus_LV_261-702_0_3_node_107 | 0.4 | n |  | TRUE
141 | bus_LV_261-702_0_3_node_109 | 0.4 | n |  | TRUE
142 | bus_LV_261-702_0_3_node_116 | 0.4 | n |  | TRUE
143 | bus_LV_261-702_0_3_node_117 | 0.4 | n |  | TRUE
144 | bus_LV_261-702_0_3_node_118 | 0.4 | n |  | TRUE
145 | bus_LV_261-702_0_3_node_119 | 0.4 | n |  | TRUE
146 | bus_LV_261-702_0_3_node_146 | 0.4 | n |  | TRUE
147 | bus_LV_261-702_0_3_node_132 | 0.4 | n |  | TRUE
148 | bus_LV_261-702_0_3_node_141 | 0.4 | n |  | TRUE
149 | bus_LV_261-702_0_3_node_142 | 0.4 | n |  | TRUE
150 | bus_LV_261-702_0_3_node_152 | 0.4 | n |  | TRUE
151 | bus_MV_530_0_node_190 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-702_0_3_load_0 | 0 | 0.0038944 | 0.00097603 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-702_0_3_load_2 | 2 | 0.0073248 | 0.0018358 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-702_0_3_load_157 | 5 | 0.0044291 | 0.00111 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-702_0_3_load_158 | 7 | 0.0047285 | 0.0011851 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-702_0_3_load_155 | 9 | 0.0042571 | 0.0010669 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-702_0_3_load_156 | 11 | 0.0086915 | 0.0021783 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-702_0_3_load_5 | 12 | 0.0015395 | 0.00038584 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-702_0_3_load_6 | 13 | 0.0014885 | 0.00037304 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-702_0_3_load_7 | 14 | 0.0015368 | 0.00038515 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-702_0_3_load_9 | 16 | 0.0015373 | 0.00038528 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-702_0_3_load_63 | 17 | 0.0014919 | 0.0003739 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-702_0_3_load_60 | 18 | 0.0016854 | 0.00042239 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-702_0_3_load_128 | 19 | 0.0014919 | 0.0003739 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-702_0_3_load_76 | 20 | 0.0015294 | 0.00038329 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-702_0_3_load_61 | 21 | 0.0016854 | 0.00042239 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-702_0_3_load_82 | 22 | 0.0014909 | 0.00037365 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-702_0_3_load_10 | 23 | 0.0048445 | 0.0012141 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_261-702_0_3_load_59 | 27 | 0.0039801 | 0.00099752 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_261-702_0_3_load_97 | 28 | 0.0040092 | 0.0010048 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_261-702_0_3_load_92 | 32 | 0.010197 | 0.0025555 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_261-702_0_3_load_140 | 34 | 0.0042632 | 0.0010685 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_261-702_0_3_load_138 | 36 | 0.0089017 | 0.002231 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_261-702_0_3_load_130 | 38 | 0.0057187 | 0.0014333 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_261-702_0_3_load_94 | 42 | 0.0069903 | 0.0017519 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_261-702_0_3_load_134 | 44 | 0.004252 | 0.0010657 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_261-702_0_3_load_133 | 46 | 0.0013265 | 0.00033244 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_261-702_0_3_load_50 | 48 | 0.0052412 | 0.0013136 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_261-702_0_3_load_48 | 50 | 0.0038368 | 0.00096159 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_261-702_0_3_load_85 | 56 | 0.0038443 | 0.00096346 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_261-702_0_3_load_41 | 57 | 0.005126 | 0.0012847 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_261-702_0_3_load_38 | 58 | 0.0046012 | 0.0011532 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_261-702_0_3_load_126 | 60 | 0.0014892 | 0.00037323 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_261-702_0_3_load_124 | 61 | 0.0014909 | 0.00037366 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_261-702_0_3_load_154 | 62 | 0.0042589 | 0.0010674 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_261-702_0_3_load_153 | 63 | 0.0042608 | 0.0010679 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_261-702_0_3_load_87 | 64 | 0.0064532 | 0.0016173 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_261-702_0_3_load_86 | 65 | 0.0063679 | 0.0015959 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_261-702_0_3_load_58 | 66 | 0.0051984 | 0.0013028 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_261-702_0_3_load_96 | 67 | 0.014979 | 0.003754 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_261-702_0_3_load_148 | 68 | 0.0035172 | 0.0008815 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_261-702_0_3_load_143 | 70 | 0.008244 | 0.0020661 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_261-702_0_3_load_131 | 71 | 0.0024326 | 0.00060967 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_261-702_0_3_load_160 | 72 | 0.010022 | 0.0025119 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_261-702_0_3_load_67 | 73 | 0.0051572 | 0.0012925 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_261-702_0_3_load_43 | 74 | 0.0099724 | 0.0024993 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_261-702_0_3_load_137 | 75 | 0.0041636 | 0.0010435 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_261-702_0_3_load_135 | 76 | 0.0086418 | 0.0021658 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_261-702_0_3_load_49 | 77 | 0.0038391 | 0.00096217 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_261-702_0_3_load_161 | 78 | 0.0071716 | 0.0017974 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_261-702_0_3_load_40 | 80 | 0.004277 | 0.0010719 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_261-702_0_3_load_65 | 81 | 0.0075061 | 0.0018812 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_261-702_0_3_load_64 | 82 | 0.0076117 | 0.0019077 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_261-702_0_3_load_104 | 83 | 0.002622 | 0.00065712 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_261-702_0_3_load_105 | 84 | 0.002622 | 0.00065714 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_261-702_0_3_load_127 | 85 | 0.0018013 | 0.00045145 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_261-702_0_3_load_150 | 86 | 0.0051485 | 0.0012903 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_261-702_0_3_load_151 | 87 | 0.0042979 | 0.0010771 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_261-702_0_3_load_42 | 88 | 0.003653 | 0.00091552 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_261-702_0_3_load_121 | 90 | 0.00081853 | 0.00020514 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_261-702_0_3_load_145 | 91 | 0.002879 | 0.00072155 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_261-702_0_3_load_57 | 92 | 0.0051572 | 0.0012925 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_261-702_0_3_load_147 | 93 | 0.0034093 | 0.00085444 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_261-702_0_3_load_120 | 94 | 0.0008004 | 0.0002006 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_261-702_0_3_load_144 | 95 | 0.00098196 | 0.0002461 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_261-702_0_3_load_51 | 96 | 0.0055075 | 0.0013803 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_261-702_0_3_load_52 | 98 | 0.0016872 | 0.00042285 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_261-702_0_3_load_56 | 100 | 0.0053521 | 0.0013414 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_261-702_0_3_load_66 | 101 | 0.0016872 | 0.00042285 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_261-702_0_3_load_159 | 102 | 0.0052412 | 0.0013136 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_261-702_0_3_load_62 | 103 | 0.0015895 | 0.00039837 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_261-702_0_3_load_74 | 104 | 0.0015277 | 0.00038287 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_261-702_0_3_load_68 | 105 | 0.0014885 | 0.00037304 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_261-702_0_3_load_69 | 106 | 0.0014919 | 0.0003739 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_261-702_0_3_load_70 | 107 | 0.0014909 | 0.00037365 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_261-702_0_3_load_71 | 108 | 0.0014919 | 0.0003739 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_261-702_0_3_load_72 | 109 | 0.0014909 | 0.00037365 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_261-702_0_3_load_78 | 110 | 0.0014909 | 0.00037365 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_261-702_0_3_load_108 | 111 | 0.0014895 | 0.0003733 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_261-702_0_3_load_110 | 112 | 0.0014892 | 0.00037322 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_261-702_0_3_load_106 | 113 | 0.0014902 | 0.00037348 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_261-702_0_3_load_73 | 114 | 0.0015276 | 0.00038285 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_261-702_0_3_load_75 | 115 | 0.0014899 | 0.0003734 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_261-702_0_3_load_77 | 116 | 0.0014902 | 0.00037348 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_261-702_0_3_load_101 | 117 | 0.0015587 | 0.00039065 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_261-702_0_3_load_99 | 118 | 0.0027483 | 0.00068879 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_261-702_0_3_load_111 | 119 | 0.0026291 | 0.00065891 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_261-702_0_3_load_79 | 120 | 0.0014909 | 0.00037365 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_261-702_0_3_load_80 | 121 | 0.0014895 | 0.0003733 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_261-702_0_3_load_83 | 123 | 0.0015159 | 0.00037991 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_261-702_0_3_load_84 | 124 | 0.0015388 | 0.00038567 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_261-702_0_3_load_89 | 125 | 0.001484 | 0.00037192 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_261-702_0_3_load_129 | 126 | 0.003855 | 0.00096617 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_261-702_0_3_load_88 | 127 | 0.0015141 | 0.00037948 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_261-702_0_3_load_90 | 128 | 0.001536 | 0.00038495 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_261-702_0_3_load_115 | 131 | 0.00079517 | 0.00019929 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_261-702_0_3_load_125 | 132 | 0.0015635 | 0.00039186 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_261-702_0_3_load_114 | 133 | 0.000785 | 0.00019674 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_261-702_0_3_load_98 | 134 | 0.0027484 | 0.00068882 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_261-702_0_3_load_100 | 135 | 0.0027482 | 0.00068878 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_261-702_0_3_load_102 | 136 | 0.0026273 | 0.00065846 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_261-702_0_3_load_103 | 137 | 0.0026333 | 0.00065997 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_261-702_0_3_load_113 | 138 | 0.0026315 | 0.00065953 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_261-702_0_3_load_112 | 139 | 0.0014892 | 0.00037322 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_261-702_0_3_load_107 | 140 | 0.0014909 | 0.00037365 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_261-702_0_3_load_109 | 141 | 0.0014892 | 0.00037323 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_261-702_0_3_load_116 | 142 | 0.00079656 | 0.00019964 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_261-702_0_3_load_117 | 143 | 0.00078577 | 0.00019693 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_261-702_0_3_load_118 | 144 | 0.00079577 | 0.00019944 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_261-702_0_3_load_119 | 145 | 0.00078577 | 0.00019693 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_261-702_0_3_load_146 | 146 | 0.0028873 | 0.00072362 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_261-702_0_3_load_132 | 147 | 0.0043328 | 0.0010859 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_261-702_0_3_load_141 | 148 | 0.0049023 | 0.0012286 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_261-702_0_3_load_142 | 149 | 0.0051084 | 0.0012803 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_261-702_0_3_load_152 | 150 | 0.0038944 | 0.00097603 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 78 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-702_0_3_line_0 |  | 0 | 1 | 0.021022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-702_0_3_line_1 |  | 1 | 2 | 0.044441 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-702_0_3_line_2 |  | 1 | 3 | 0.014543 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-702_0_3_line_3 |  | 3 | 4 | 0.007136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-702_0_3_line_4 |  | 3 | 5 | 0.0109 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_261-702_0_3_line_5 |  | 4 | 11 | 0.017658 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_261-702_0_3_line_6 |  | 5 | 7 | 0.01911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_261-702_0_3_line_7 |  | 6 | 7 | 0.011198 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_261-702_0_3_line_8 |  | 6 | 8 | 0.010578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_261-702_0_3_line_9 |  | 8 | 23 | 0.021248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_261-702_0_3_line_10 |  | 9 | 10 | 0.024649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_261-702_0_3_line_11 |  | 10 | 24 | 0.00221 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_261-702_0_3_line_12 |  | 11 | 36 | 0.01988 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-702_0_3_line_13 |  | 12 | 13 | 0.003176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_261-702_0_3_line_14 |  | 12 | 14 | 6.3398e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_261-702_0_3_line_15 |  | 13 | 15 | 0.015513 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_261-702_0_3_line_16 |  | 14 | 16 | 6.5125e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_261-702_0_3_line_17 |  | 15 | 17 | 0.013084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_261-702_0_3_line_18 |  | 15 | 18 | 0.00090761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_261-702_0_3_line_19 |  | 16 | 19 | 0.0025396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_261-702_0_3_line_20 |  | 17 | 20 | 0.0049339 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_261-702_0_3_line_21 |  | 18 | 21 | 0.0063575 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_261-702_0_3_line_22 |  | 19 | 22 | 0.0058488 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_261-702_0_3_line_23 |  | 20 | 104 | 0.0059332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_261-702_0_3_line_24 |  | 21 | 103 | 0.0052201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_261-702_0_3_line_25 |  | 22 | 121 | 0.0058441 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_261-702_0_3_line_26 |  | 23 | 24 | 0.029799 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_261-702_0_3_line_27 |  | 25 | 26 | 0.020072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_261-702_0_3_line_28 |  | 25 | 27 | 0.024884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_261-702_0_3_line_29 |  | 26 | 28 | 0.014125 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_261-702_0_3_line_30 |  | 27 | 66 | 0.017396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_261-702_0_3_line_31 |  | 28 | 67 | 0.010214 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_261-702_0_3_line_32 |  | 29 | 30 | 0.002142 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
33 | LV_261-702_0_3_line_33 |  | 29 | 31 | 0.01394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
34 | LV_261-702_0_3_line_34 |  | 29 | 32 | 0.019454 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_261-702_0_3_line_35 |  | 30 | 68 | 0.020955 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_261-702_0_3_line_36 |  | 30 | 69 | 0.033154 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
37 | LV_261-702_0_3_line_37 |  | 31 | 33 | 0.078694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_261-702_0_3_line_38 |  | 31 | 34 | 0.040395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
39 | LV_261-702_0_3_line_39 |  | 33 | 38 | 0.018665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_261-702_0_3_line_40 |  | 34 | 45 | 0.013293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
41 | LV_261-702_0_3_line_41 |  | 35 | 36 | 0.010222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_261-702_0_3_line_42 |  | 35 | 37 | 0.012641 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_261-702_0_3_line_43 |  | 37 | 70 | 0.0095305 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_261-702_0_3_line_44 |  | 38 | 71 | 0.015196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_261-702_0_3_line_45 |  | 39 | 40 | 0.009208 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_261-702_0_3_line_46 |  | 39 | 41 | 0.031792 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_261-702_0_3_line_47 |  | 39 | 42 | 0.015131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_261-702_0_3_line_48 |  | 40 | 72 | 0.007226 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_261-702_0_3_line_49 |  | 41 | 73 | 0.014367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
50 | LV_261-702_0_3_line_50 |  | 41 | 74 | 0.018593 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
51 | LV_261-702_0_3_line_51 |  | 43 | 44 | 0.020486 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_261-702_0_3_line_52 |  | 43 | 45 | 0.014567 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_261-702_0_3_line_53 |  | 43 | 46 | 0.01112 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_261-702_0_3_line_54 |  | 44 | 75 | 0.014864 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_261-702_0_3_line_55 |  | 44 | 76 | 0.018104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_261-702_0_3_line_56 |  | 46 | 52 | 0.017091 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_261-702_0_3_line_57 |  | 47 | 48 | 0.012065 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_261-702_0_3_line_58 |  | 47 | 49 | 0.069154 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_261-702_0_3_line_59 |  | 47 | 50 | 0.014404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_261-702_0_3_line_60 |  | 49 | 51 | 0.020606 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_261-702_0_3_line_61 |  | 50 | 77 | 0.0175 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_261-702_0_3_line_62 |  | 51 | 78 | 0.010503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
63 | LV_261-702_0_3_line_63 |  | 51 | 79 | 0.004114 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
64 | LV_261-702_0_3_line_64 |  | 52 | 53 | 0.046866 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_261-702_0_3_line_65 |  | 53 | 80 | 0.042924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_261-702_0_3_line_66 |  | 53 | 58 | 0.034967 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_261-702_0_3_line_67 |  | 54 | 55 | 0.11231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_261-702_0_3_line_68 |  | 54 | 56 | 0.0034417 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_261-702_0_3_line_69 |  | 55 | 57 | 0.023643 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_261-702_0_3_line_70 |  | 55 | 58 | 0.039321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_261-702_0_3_line_71 |  | 56 | 65 | 0.018958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_261-702_0_3_line_72 |  | 59 | 60 | 0.021617 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_261-702_0_3_line_73 |  | 59 | 61 | 0.019975 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_261-702_0_3_line_74 |  | 60 | 85 | 8.4195e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_261-702_0_3_line_75 |  | 62 | 63 | 0.014533 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_261-702_0_3_line_76 |  | 63 | 150 | 0.014534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_261-702_0_3_line_77 |  | 64 | 65 | 0.028818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_261-702_0_3_line_78 |  | 66 | 100 | 0.029353 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_261-702_0_3_line_79 |  | 68 | 93 | 0.021202 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_261-702_0_3_line_80 |  | 69 | 89 | 0.027387 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
81 | LV_261-702_0_3_line_81 |  | 69 | 88 | 0.019762 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
82 | LV_261-702_0_3_line_82 |  | 70 | 149 | 0.015472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_261-702_0_3_line_83 |  | 71 | 147 | 0.0067818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_261-702_0_3_line_84 |  | 73 | 92 | 0.017525 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
85 | LV_261-702_0_3_line_85 |  | 74 | 88 | 0.025035 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
86 | LV_261-702_0_3_line_86 |  | 75 | 148 | 0.014596 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_261-702_0_3_line_87 |  | 79 | 102 | 0.00678 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_261-702_0_3_line_88 |  | 79 | 97 | 0.010578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
89 | LV_261-702_0_3_line_89 |  | 80 | 86 | 0.011264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_261-702_0_3_line_90 |  | 81 | 82 | 0.023402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_261-702_0_3_line_91 |  | 82 | 99 | 0.016959 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_261-702_0_3_line_92 |  | 83 | 84 | 0.012462 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_261-702_0_3_line_93 |  | 84 | 136 | 0.0091632 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_261-702_0_3_line_94 |  | 85 | 141 | 0.0057575 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_261-702_0_3_line_95 |  | 86 | 87 | 0.0077077 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_261-702_0_3_line_96 |  | 87 | 150 | 0.04266 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_261-702_0_3_line_97 |  | 89 | 90 | 0.012885 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
98 | LV_261-702_0_3_line_98 |  | 89 | 91 | 0.01457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_261-702_0_3_line_99 |  | 90 | 94 | 0.0012072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
100 | LV_261-702_0_3_line_100 |  | 91 | 95 | 0.0094869 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_261-702_0_3_line_101 |  | 92 | 97 | 0.018771 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
102 | LV_261-702_0_3_line_102 |  | 94 | 145 | 0.018817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
103 | LV_261-702_0_3_line_103 |  | 95 | 146 | 0.0052284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_261-702_0_3_line_104 |  | 96 | 97 | 0.013731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_261-702_0_3_line_105 |  | 97 | 100 | 0.028073 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_261-702_0_3_line_106 |  | 98 | 99 | 0.014104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_261-702_0_3_line_107 |  | 99 | 101 | 0.015491 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_261-702_0_3_line_108 |  | 101 | 103 | 0.00114 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_261-702_0_3_line_109 |  | 104 | 114 | 0.0059309 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_261-702_0_3_line_110 |  | 105 | 106 | 0.00035704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_261-702_0_3_line_111 |  | 105 | 107 | 0.015228 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_261-702_0_3_line_112 |  | 106 | 108 | 0.0054873 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_261-702_0_3_line_113 |  | 107 | 109 | 8.8878e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_261-702_0_3_line_114 |  | 108 | 110 | 0.00036176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_261-702_0_3_line_115 |  | 109 | 111 | 0.0057554 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_261-702_0_3_line_116 |  | 110 | 112 | 0.0054846 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_261-702_0_3_line_117 |  | 111 | 113 | 9.0917e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_261-702_0_3_line_118 |  | 112 | 119 | 0.00035972 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_261-702_0_3_line_119 |  | 113 | 140 | 0.0057534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_261-702_0_3_line_120 |  | 114 | 115 | 0.013728 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_261-702_0_3_line_121 |  | 115 | 116 | 7.8826e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_261-702_0_3_line_122 |  | 116 | 117 | 0.0029749 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_261-702_0_3_line_123 |  | 117 | 118 | 0.0059911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_261-702_0_3_line_124 |  | 118 | 134 | 0.0059921 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_261-702_0_3_line_125 |  | 119 | 139 | 0.0054832 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_261-702_0_3_line_126 |  | 120 | 121 | 0.0058441 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_261-702_0_3_line_127 |  | 120 | 122 | 0.0075394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_261-702_0_3_line_128 |  | 122 | 123 | 0.0087312 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_261-702_0_3_line_129 |  | 122 | 124 | 0.028501 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_261-702_0_3_line_130 |  | 123 | 125 | 0.0060054 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_261-702_0_3_line_131 |  | 124 | 126 | 0.00021849 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_261-702_0_3_line_132 |  | 125 | 127 | 0.011448 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_261-702_0_3_line_133 |  | 127 | 128 | 0.0011339 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_261-702_0_3_line_134 |  | 128 | 129 | 0.017357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_261-702_0_3_line_135 |  | 129 | 130 | 0.00448 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_261-702_0_3_line_136 |  | 129 | 131 | 0.017609 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
137 | LV_261-702_0_3_line_137 |  | 130 | 132 | 0.0094591 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_261-702_0_3_line_138 |  | 131 | 133 | 0.0019952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
139 | LV_261-702_0_3_line_139 |  | 133 | 142 | 0.0039544 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
140 | LV_261-702_0_3_line_140 |  | 134 | 135 | 0.0051664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_261-702_0_3_line_141 |  | 135 | 136 | 0.0096352 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_261-702_0_3_line_142 |  | 135 | 137 | 0.01476 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_261-702_0_3_line_143 |  | 137 | 138 | 0.005849 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_261-702_0_3_line_144 |  | 138 | 139 | 0.00036109 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
145 | LV_261-702_0_3_line_145 |  | 140 | 141 | 9.1541e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
146 | LV_261-702_0_3_line_146 |  | 142 | 143 | 0.0018785 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
147 | LV_261-702_0_3_line_147 |  | 143 | 144 | 0.0040727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
148 | LV_261-702_0_3_line_148 |  | 144 | 145 | 0.0017631 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
149 | LV_261-702_0_3_line_149 |  | 148 | 149 | 0.0059203 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-702_0_3_trafo_161 | 0.63 MVA 20/0.4 kV | 151 | 78 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2682824.7333 | 1250032.9748 | 2682828.7482 | 1250038.5016 | 2682827.066 | 1250042.7146 | 2682832.5136 | 1250050.6855
1 | 2682860.4628 | 1250006.4099 | 2682824.7333 | 1250032.9748
2 | 2682816.185 | 1250021.191 | 2682824.7333 | 1250032.9748
3 | 2682821.2463 | 1250016.1469 | 2682816.185 | 1250021.191
4 | 2682816.185 | 1250021.191 | 2682808.4506 | 1250028.8713
5 | 2682821.2463 | 1250016.1469 | 2682834.3261 | 1250004.2837
6 | 2682808.4506 | 1250028.8713 | 2682794.8905 | 1250042.3363
7 | 2682786.9447 | 1250050.2264 | 2682794.8905 | 1250042.3363
8 | 2682778.9872 | 1250057.2205 | 2682786.9447 | 1250050.2264
9 | 2682778.9872 | 1250057.2205 | 2682764.2909 | 1250072.5666
10 | 2682745.4208 | 1250095.458 | 2682764.512 | 1250079.8664
11 | 2682743.6808 | 1250094.0883 | 2682745.4208 | 1250095.458
12 | 2682849.0518 | 1249990.9278 | 2682834.3261 | 1250004.2837
13 | 2682756.2308 | 1249883.6251 | 2682754.4951 | 1249886.2849
14 | 2682756.2654 | 1249883.572 | 2682756.2308 | 1249883.6251
15 | 2682746.0169 | 1249899.2763 | 2682754.4951 | 1249886.2849
16 | 2682756.301 | 1249883.5175 | 2682756.2654 | 1249883.572
17 | 2682746.0169 | 1249899.2763 | 2682735.0933 | 1249892.0743
18 | 2682746.0169 | 1249899.2763 | 2682745.4739 | 1249900.0035
19 | 2682757.689 | 1249881.3907 | 2682756.301 | 1249883.5175
20 | 2682730.974 | 1249889.3585 | 2682735.0933 | 1249892.0743
21 | 2682745.4739 | 1249900.0035 | 2682741.6702 | 1249905.0976
22 | 2682760.8854 | 1249876.4927 | 2682757.689 | 1249881.3907
23 | 2682726.0206 | 1249886.0927 | 2682730.974 | 1249889.3585
24 | 2682738.5471 | 1249909.2803 | 2682741.6702 | 1249905.0976
25 | 2682764.0793 | 1249871.5985 | 2682760.8854 | 1249876.4927
26 | 2682743.6808 | 1250094.0883 | 2682764.2909 | 1250072.5666
27 | 2682689.8748 | 1250026.7208 | 2682698.0196 | 1250030.6484 | 2682708.5834 | 1250033.8204
28 | 2682708.5834 | 1250033.8204 | 2682726.3437 | 1250016.3912
29 | 2682689.8748 | 1250026.7208 | 2682689.6879 | 1250024.4276 | 2682690.6877 | 1250020.9501 | 2682692.7373 | 1250016.9201 | 2682694.4459 | 1250013.6562
30 | 2682738.7598 | 1250004.2066 | 2682726.3437 | 1250016.3912
31 | 2682691.7416 | 1250006.5763 | 2682693.1862 | 1250006.3963 | 2682694.1553 | 1250006.7435 | 2682695.3582 | 1250008.1946 | 2682695.8581 | 1250009.7027 | 2682695.5919 | 1250011.467 | 2682694.4459 | 1250013.6562
32 | 2682886.5919 | 1249909.9925 | 2682885.1034 | 1249908.4483
33 | 2682886.5919 | 1249909.9925 | 2682890.0882 | 1249913.1993 | 2682893.3532 | 1249916.2027 | 2682897.7431 | 1249914.3628
34 | 2682886.5919 | 1249909.9925 | 2682872.7967 | 1249923.7098
35 | 2682885.1034 | 1249908.4483 | 2682894.1402 | 1249898.8119 | 2682899.0905 | 1249892.8565
36 | 2682861.8167 | 1249884.783 | 2682882.2456 | 1249905.4839 | 2682885.1034 | 1249908.4483
37 | 2682897.7431 | 1249914.3628 | 2682904.4005 | 1249905.8829 | 2682915.7913 | 1249892.0542 | 2682923.8768 | 1249879.7248 | 2682931.9025 | 1249869.5072 | 2682950.6483 | 1249881.5117
38 | 2682897.7431 | 1249914.3628 | 2682901.7096 | 1249918.4991 | 2682902.699 | 1249919.5581 | 2682906.3395 | 1249923.79 | 2682907.1881 | 1249924.658 | 2682924.5752 | 1249944.5484
39 | 2682950.6483 | 1249881.5117 | 2682949.4255 | 1249883.1069 | 2682939.2931 | 1249896.3248
40 | 2682933.3243 | 1249954.5569 | 2682924.5752 | 1249944.5484
41 | 2682855.8186 | 1249983.25 | 2682849.0518 | 1249990.9278
42 | 2682855.8186 | 1249983.25 | 2682864.5988 | 1249974.1326
43 | 2682864.5988 | 1249974.1326 | 2682871.4607 | 1249967.5186
44 | 2682939.2931 | 1249896.3248 | 2682930.048 | 1249908.3852
45 | 2682846.5673 | 1249945.615 | 2682839.0553 | 1249950.9695
46 | 2682816.2007 | 1249928.8004 | 2682822.8456 | 1249935.2425 | 2682839.0553 | 1249950.9695
47 | 2682839.0553 | 1249950.9695 | 2682833.7626 | 1249954.7428 | 2682827.6195 | 1249960.8061
48 | 2682852.0767 | 1249940.9218 | 2682846.5673 | 1249945.615
49 | 2682816.2007 | 1249928.8004 | 2682805.8618 | 1249938.7763
50 | 2682816.2007 | 1249928.8004 | 2682829.5806 | 1249915.8895
51 | 2682921.1461 | 1249962.6037 | 2682905.3041 | 1249975.6473
52 | 2682933.3243 | 1249954.5569 | 2682921.1461 | 1249962.6037
53 | 2682921.1461 | 1249962.6037 | 2682927.8096 | 1249971.5061
54 | 2682905.3041 | 1249975.6473 | 2682895.9996 | 1249964.0553
55 | 2682905.3041 | 1249975.6473 | 2682890.9578 | 1249986.6893
56 | 2682937.3204 | 1249985.6915 | 2682932.8158 | 1249978.4676 | 2682931.0037 | 1249975.7736 | 2682927.8096 | 1249971.5061
57 | 2682764.252 | 1249992.7113 | 2682755.5204 | 1250001.0622
58 | 2682755.5204 | 1250001.0622 | 2682771.3208 | 1250016.3609 | 2682804.8918 | 1249983.2384
59 | 2682755.5204 | 1250001.0622 | 2682745.1107 | 1250011.0173
60 | 2682790.366 | 1249968.5802 | 2682804.8918 | 1249983.2384
61 | 2682732.463 | 1250023.1127 | 2682745.1107 | 1250011.0173
62 | 2682790.366 | 1249968.5802 | 2682798.047 | 1249961.3933
63 | 2682787.337 | 1249971.3733 | 2682790.366 | 1249968.5802
64 | 2682937.3204 | 1249985.6915 | 2682930.7539 | 1249990.3809 | 2682903.2373 | 1250010.0328 | 2682900.1758 | 1250014.0708
65 | 2682900.1758 | 1250014.0708 | 2682892.7716 | 1250024.6751 | 2682868.767 | 1250042.6531
66 | 2682900.1758 | 1250014.0708 | 2682909.0574 | 1250026.3041 | 2682920.5579 | 1250042.4823
67 | 2682922.9328 | 1250147.7996 | 2682929.7314 | 1250147.55 | 2682973.5273 | 1250116.9957 | 2682968.6996 | 1250110.212 | 2682943.3399 | 1250074.5306
68 | 2682922.9328 | 1250147.7996 | 2682919.7072 | 1250148.9998
69 | 2682943.3399 | 1250074.5306 | 2682923.9353 | 1250088.0388
70 | 2682943.3399 | 1250074.5306 | 2682920.5579 | 1250042.4823
71 | 2682919.7072 | 1250148.9998 | 2682904.3214 | 1250160.0754
72 | 2682743.0916 | 1249785.9958 | 2682731.3854 | 1249804.1686
73 | 2682743.0916 | 1249785.9958 | 2682759.9805 | 1249796.6626
74 | 2682731.3398 | 1249804.2394 | 2682731.3854 | 1249804.1686
75 | 2682807.5827 | 1250088.0122 | 2682795.8736 | 1250096.6215
76 | 2682819.2918 | 1250079.4029 | 2682807.5827 | 1250088.0122
77 | 2682904.3214 | 1250160.0754 | 2682880.9331 | 1250176.9116
78 | 2682738.7598 | 1250004.2066 | 2682759.7099 | 1249983.6471
79 | 2682899.0905 | 1249892.8565 | 2682905.2682 | 1249885.4243 | 2682911.622 | 1249875.7944
80 | 2682842.9701 | 1249864.8603 | 2682861.8167 | 1249884.783
81 | 2682861.8167 | 1249884.783 | 2682847.5962 | 1249898.5052
82 | 2682882.6005 | 1249956.781 | 2682871.4607 | 1249967.5186
83 | 2682925.9221 | 1249913.7675 | 2682930.048 | 1249908.3852
84 | 2682793.2501 | 1249950.9451 | 2682805.8618 | 1249938.7763
85 | 2682847.5962 | 1249898.5052 | 2682829.5806 | 1249915.8895
86 | 2682895.9996 | 1249964.0553 | 2682886.863 | 1249952.6724
87 | 2682787.337 | 1249971.3733 | 2682782.3424 | 1249975.9737
88 | 2682787.337 | 1249971.3733 | 2682783.553 | 1249967.6844 | 2682782.4729 | 1249966.6352 | 2682779.7465 | 1249963.9841
89 | 2682868.767 | 1250042.6531 | 2682859.7515 | 1250049.4051
90 | 2682717.2873 | 1249935.2429 | 2682714.5076 | 1249938.3099 | 2682700.1318 | 1249951.1318
91 | 2682728.5969 | 1249922.606 | 2682717.5826 | 1249934.917 | 2682717.2873 | 1249935.2429
92 | 2682665.7679 | 1249849.1751 | 2682669.1864 | 1249849.3117 | 2682676.8355 | 1249854.1308
93 | 2682676.8355 | 1249854.1308 | 2682684.5884 | 1249859.0152
94 | 2682731.3398 | 1249804.2394 | 2682728.2219 | 1249809.0795
95 | 2682853.5822 | 1250054.0256 | 2682859.7515 | 1250049.4051
96 | 2682853.5822 | 1250054.0256 | 2682841.5272 | 1250063.054 | 2682819.2918 | 1250079.4029
97 | 2682842.9701 | 1249864.8603 | 2682833.5802 | 1249856.0364
98 | 2682842.9701 | 1249864.8603 | 2682852.1957 | 1249853.5827
99 | 2682832.7004 | 1249855.2097 | 2682833.5802 | 1249856.0364
100 | 2682858.2025 | 1249846.2398 | 2682852.1957 | 1249853.5827
101 | 2682779.7465 | 1249963.9841 | 2682783.1218 | 1249960.7177 | 2682793.2501 | 1249950.9451
102 | 2682832.7004 | 1249855.2097 | 2682817.9216 | 1249843.5615
103 | 2682861.513 | 1249842.193 | 2682858.2025 | 1249846.2398
104 | 2682779.7465 | 1249963.9841 | 2682773.3134 | 1249958.0565 | 2682769.8719 | 1249954.4519
105 | 2682779.7465 | 1249963.9841 | 2682759.7099 | 1249983.6471
106 | 2682728.5969 | 1249922.606 | 2682740.0431 | 1249930.8471
107 | 2682728.5969 | 1249922.606 | 2682737.865 | 1249910.1938
108 | 2682738.5471 | 1249909.2803 | 2682737.865 | 1249910.1938
109 | 2682721.069 | 1249882.8281 | 2682726.0206 | 1249886.0927
110 | 2682713.4025 | 1249832.0852 | 2682713.5959 | 1249831.785
111 | 2682713.5959 | 1249831.785 | 2682721.8426 | 1249818.9829
112 | 2682713.4025 | 1249832.0852 | 2682710.431 | 1249836.6982
113 | 2682721.8426 | 1249818.9829 | 2682721.8907 | 1249818.9081
114 | 2682710.2351 | 1249837.0023 | 2682710.431 | 1249836.6982
115 | 2682721.8907 | 1249818.9081 | 2682725.0074 | 1249814.0697
116 | 2682710.2351 | 1249837.0023 | 2682707.265 | 1249841.6131
117 | 2682725.0074 | 1249814.0697 | 2682725.0567 | 1249813.9932
118 | 2682707.0702 | 1249841.9155 | 2682707.265 | 1249841.6131
119 | 2682725.0567 | 1249813.9932 | 2682728.1723 | 1249809.1565
120 | 2682721.069 | 1249882.8281 | 2682709.608 | 1249875.2719
121 | 2682709.5421 | 1249875.2285 | 2682709.608 | 1249875.2719
122 | 2682707.0585 | 1249873.591 | 2682709.5421 | 1249875.2285
123 | 2682702.0567 | 1249870.2933 | 2682707.0585 | 1249873.591
124 | 2682697.054 | 1249866.995 | 2682702.0567 | 1249870.2933
125 | 2682707.0702 | 1249841.9155 | 2682704.1008 | 1249846.5251
126 | 2682767.2732 | 1249866.7044 | 2682764.0793 | 1249871.5985
127 | 2682771.3936 | 1249860.3906 | 2682767.2732 | 1249866.7044
128 | 2682771.3936 | 1249860.3906 | 2682776.0491 | 1249853.0041
129 | 2682771.3936 | 1249860.3906 | 2682795.5572 | 1249875.5038
130 | 2682779.2512 | 1249847.9236 | 2682776.0491 | 1249853.0041
131 | 2682795.7425 | 1249875.6197 | 2682795.5572 | 1249875.5038
132 | 2682785.3555 | 1249838.2385 | 2682779.2512 | 1249847.9236
133 | 2682785.3555 | 1249838.2385 | 2682785.9601 | 1249837.2792
134 | 2682795.2151 | 1249822.5952 | 2682785.9601 | 1249837.2792
135 | 2682795.2151 | 1249822.5952 | 2682792.9664 | 1249818.7164
136 | 2682795.2151 | 1249822.5952 | 2682798.4885 | 1249828.2451 | 2682807.1902 | 1249835.1034
137 | 2682792.9664 | 1249818.7164 | 2682791.8456 | 1249816.7882 | 2682785.7338 | 1249812.9281
138 | 2682808.7572 | 1249836.3384 | 2682807.1902 | 1249835.1034
139 | 2682808.7572 | 1249836.3384 | 2682811.8629 | 1249838.7862
140 | 2682692.7406 | 1249864.1513 | 2682697.054 | 1249866.995
141 | 2682692.7406 | 1249864.1513 | 2682684.5884 | 1249859.0152
142 | 2682692.7406 | 1249864.1513 | 2682695.8276 | 1249859.3686 | 2682700.7379 | 1249851.7458
143 | 2682703.9053 | 1249846.8287 | 2682700.7379 | 1249851.7458
144 | 2682703.9053 | 1249846.8287 | 2682704.1008 | 1249846.5251
145 | 2682728.1723 | 1249809.1565 | 2682728.2219 | 1249809.0795
146 | 2682813.3382 | 1249839.9491 | 2682811.8629 | 1249838.7862
147 | 2682813.3382 | 1249839.9491 | 2682816.5368 | 1249842.4701
148 | 2682817.9216 | 1249843.5615 | 2682816.5368 | 1249842.4701
149 | 2682886.863 | 1249952.6724 | 2682886.863 | 1249952.6724 | 2682882.6005 | 1249956.781

## bus_geodata
| x | y | coords
0 | 2682832.5136 | 1250050.6855
1 | 2682824.7333 | 1250032.9748
2 | 2682860.4628 | 1250006.4099
3 | 2682816.185 | 1250021.191
4 | 2682821.2463 | 1250016.1469
5 | 2682808.4506 | 1250028.8713
6 | 2682786.9447 | 1250050.2264
7 | 2682794.8905 | 1250042.3363
8 | 2682778.9872 | 1250057.2205
9 | 2682764.512 | 1250079.8664
10 | 2682745.4208 | 1250095.458
11 | 2682834.3261 | 1250004.2837
12 | 2682756.2308 | 1249883.6251
13 | 2682754.4951 | 1249886.2849
14 | 2682756.2654 | 1249883.572
15 | 2682746.0169 | 1249899.2763
16 | 2682756.301 | 1249883.5175
17 | 2682735.0933 | 1249892.0743
18 | 2682745.4739 | 1249900.0035
19 | 2682757.689 | 1249881.3907
20 | 2682730.974 | 1249889.3585
21 | 2682741.6702 | 1249905.0976
22 | 2682760.8854 | 1249876.4927
23 | 2682764.2909 | 1250072.5666
24 | 2682743.6808 | 1250094.0883
25 | 2682708.5834 | 1250033.8204
26 | 2682689.8748 | 1250026.7208
27 | 2682726.3437 | 1250016.3912
28 | 2682694.4459 | 1250013.6562
29 | 2682886.5919 | 1249909.9925
30 | 2682885.1034 | 1249908.4483
31 | 2682897.7431 | 1249914.3628
32 | 2682872.7967 | 1249923.7098
33 | 2682950.6483 | 1249881.5117
34 | 2682924.5752 | 1249944.5484
35 | 2682855.8186 | 1249983.25
36 | 2682849.0518 | 1249990.9278
37 | 2682864.5988 | 1249974.1326
38 | 2682939.2931 | 1249896.3248
39 | 2682839.0553 | 1249950.9695
40 | 2682846.5673 | 1249945.615
41 | 2682816.2007 | 1249928.8004
42 | 2682827.6195 | 1249960.8061
43 | 2682921.1461 | 1249962.6037
44 | 2682905.3041 | 1249975.6473
45 | 2682933.3243 | 1249954.5569
46 | 2682927.8096 | 1249971.5061
47 | 2682755.5204 | 1250001.0622
48 | 2682764.252 | 1249992.7113
49 | 2682804.8918 | 1249983.2384
50 | 2682745.1107 | 1250011.0173
51 | 2682790.366 | 1249968.5802
52 | 2682937.3204 | 1249985.6915
53 | 2682900.1758 | 1250014.0708
54 | 2682922.9328 | 1250147.7996
55 | 2682943.3399 | 1250074.5306
56 | 2682919.7072 | 1250148.9998
57 | 2682923.9353 | 1250088.0388
58 | 2682920.5579 | 1250042.4823
59 | 2682743.0916 | 1249785.9958
60 | 2682731.3854 | 1249804.1686
61 | 2682759.9805 | 1249796.6626
62 | 2682795.8736 | 1250096.6215
63 | 2682807.5827 | 1250088.0122
64 | 2682880.9331 | 1250176.9116
65 | 2682904.3214 | 1250160.0754
66 | 2682738.7598 | 1250004.2066
67 | 2682691.7416 | 1250006.5763
68 | 2682899.0905 | 1249892.8565
69 | 2682861.8167 | 1249884.783
70 | 2682871.4607 | 1249967.5186
71 | 2682930.048 | 1249908.3852
72 | 2682852.0767 | 1249940.9218
73 | 2682805.8618 | 1249938.7763
74 | 2682829.5806 | 1249915.8895
75 | 2682895.9996 | 1249964.0553
76 | 2682890.9578 | 1249986.6893
77 | 2682732.463 | 1250023.1127
78 | 2682798.047 | 1249961.3933
79 | 2682787.337 | 1249971.3733
80 | 2682868.767 | 1250042.6531
81 | 2682700.1318 | 1249951.1318
82 | 2682717.2873 | 1249935.2429
83 | 2682665.7679 | 1249849.1751
84 | 2682676.8355 | 1249854.1308
85 | 2682731.3398 | 1249804.2394
86 | 2682859.7515 | 1250049.4051
87 | 2682853.5822 | 1250054.0256
88 | 2682847.5962 | 1249898.5052
89 | 2682842.9701 | 1249864.8603
90 | 2682833.5802 | 1249856.0364
91 | 2682852.1957 | 1249853.5827
92 | 2682793.2501 | 1249950.9451
93 | 2682911.622 | 1249875.7944
94 | 2682832.7004 | 1249855.2097
95 | 2682858.2025 | 1249846.2398
96 | 2682769.8719 | 1249954.4519
97 | 2682779.7465 | 1249963.9841
98 | 2682740.0431 | 1249930.8471
99 | 2682728.5969 | 1249922.606
100 | 2682759.7099 | 1249983.6471
101 | 2682737.865 | 1249910.1938
102 | 2682782.3424 | 1249975.9737
103 | 2682738.5471 | 1249909.2803
104 | 2682726.0206 | 1249886.0927
105 | 2682713.5959 | 1249831.785
106 | 2682713.4025 | 1249832.0852
107 | 2682721.8426 | 1249818.9829
108 | 2682710.431 | 1249836.6982
109 | 2682721.8907 | 1249818.9081
110 | 2682710.2351 | 1249837.0023
111 | 2682725.0074 | 1249814.0697
112 | 2682707.265 | 1249841.6131
113 | 2682725.0567 | 1249813.9932
114 | 2682721.069 | 1249882.8281
115 | 2682709.608 | 1249875.2719
116 | 2682709.5421 | 1249875.2285
117 | 2682707.0585 | 1249873.591
118 | 2682702.0567 | 1249870.2933
119 | 2682707.0702 | 1249841.9155
120 | 2682767.2732 | 1249866.7044
121 | 2682764.0793 | 1249871.5985
122 | 2682771.3936 | 1249860.3906
123 | 2682776.0491 | 1249853.0041
124 | 2682795.5572 | 1249875.5038
125 | 2682779.2512 | 1249847.9236
126 | 2682795.7425 | 1249875.6197
127 | 2682785.3555 | 1249838.2385
128 | 2682785.9601 | 1249837.2792
129 | 2682795.2151 | 1249822.5952
130 | 2682792.9664 | 1249818.7164
131 | 2682807.1902 | 1249835.1034
132 | 2682785.7338 | 1249812.9281
133 | 2682808.7572 | 1249836.3384
134 | 2682697.054 | 1249866.995
135 | 2682692.7406 | 1249864.1513
136 | 2682684.5884 | 1249859.0152
137 | 2682700.7379 | 1249851.7458
138 | 2682703.9053 | 1249846.8287
139 | 2682704.1008 | 1249846.5251
140 | 2682728.1723 | 1249809.1565
141 | 2682728.2219 | 1249809.0795
142 | 2682811.8629 | 1249838.7862
143 | 2682813.3382 | 1249839.9491
144 | 2682816.5368 | 1249842.4701
145 | 2682817.9216 | 1249843.5615
146 | 2682861.513 | 1249842.193
147 | 2682925.9221 | 1249913.7675
148 | 2682886.863 | 1249952.6724
149 | 2682882.6005 | 1249956.781
150 | 2682819.2918 | 1250079.4029
151 | 2682790.366 | 1249968.5802

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97159 | -0.54764 | 0.0038944 | 0.00097603
1 | 0.97167 | -0.54613 | 0 | 0
2 | 0.97136 | -0.55214 | 0.0073248 | 0.0018358
3 | 0.97182 | -0.54312 | 0 | 0
4 | 0.97201 | -0.53924 | 0 | 0
5 | 0.97163 | -0.54679 | 0.0044291 | 0.00111
6 | 0.97129 | -0.55356 | 0 | 0
7 | 0.97139 | -0.55167 | 0.0047285 | 0.0011851
8 | 0.9712 | -0.55534 | 0 | 0
9 | 0.97079 | -0.56337 | 0.0042571 | 0.0010669
10 | 0.97089 | -0.56143 | 0 | 0
11 | 0.9725 | -0.52964 | 0.0086915 | 0.0021783
12 | 0.97612 | -0.45831 | 0.0015395 | 0.00038584
13 | 0.97587 | -0.46309 | 0.0014885 | 0.00037304
14 | 0.97612 | -0.45821 | 0.0015368 | 0.00038515
15 | 0.9747 | -0.48604 | 0 | 0
16 | 0.97613 | -0.45811 | 0.0015373 | 0.00038528
17 | 0.974 | -0.49981 | 0.0014919 | 0.0003739
18 | 0.97468 | -0.48643 | 0.0016854 | 0.00042239
19 | 0.97633 | -0.45408 | 0.0014919 | 0.0003739
20 | 0.97375 | -0.50487 | 0.0015294 | 0.00038329
21 | 0.97456 | -0.48897 | 0.0016854 | 0.00042239
22 | 0.97681 | -0.44463 | 0.0014909 | 0.00037365
23 | 0.97102 | -0.55891 | 0.0048445 | 0.0012141
24 | 0.9709 | -0.56126 | 0 | 0
25 | 0.99465 | -0.10182 | 0 | 0
26 | 0.99431 | -0.10854 | 0 | 0
27 | 0.99508 | -0.093503 | 0.0039801 | 0.00099752
28 | 0.99406 | -0.11327 | 0.0040092 | 0.0010048
29 | 0.9843 | -0.299 | 0 | 0
30 | 0.98441 | -0.29691 | 0 | 0
31 | 0.98364 | -0.3118 | 0 | 0
32 | 0.98412 | -0.30257 | 0.010197 | 0.0025555
33 | 0.98274 | -0.32952 | 0 | 0
34 | 0.98188 | -0.34595 | 0.0042632 | 0.0010685
35 | 0.97366 | -0.50681 | 0 | 0
36 | 0.97321 | -0.51566 | 0.0089017 | 0.002231
37 | 0.97421 | -0.49587 | 0 | 0
38 | 0.98252 | -0.33373 | 0.0057187 | 0.0014333
39 | 0.99146 | -0.16184 | 0 | 0
40 | 0.99137 | -0.16348 | 0 | 0
41 | 0.99195 | -0.15225 | 0 | 0
42 | 0.99136 | -0.16372 | 0.0069903 | 0.0017519
43 | 0.97919 | -0.39836 | 0 | 0
44 | 0.97761 | -0.42909 | 0.004252 | 0.0010657
45 | 0.98104 | -0.36234 | 0 | 0
46 | 0.97863 | -0.40925 | 0.0013265 | 0.00033244
47 | 0.99769 | -0.043946 | 0 | 0
48 | 0.99763 | -0.045053 | 0.0052412 | 0.0013136
49 | 0.9985 | -0.028314 | 0 | 0
50 | 0.99759 | -0.045882 | 0.0038368 | 0.00096159
51 | 0.99874 | -0.023661 | 0 | 0
52 | 0.97779 | -0.42561 | 0 | 0
53 | 0.9755 | -0.47061 | 0 | 0
54 | 0.97209 | -0.53773 | 0 | 0
55 | 0.97384 | -0.50327 | 0 | 0
56 | 0.97204 | -0.53879 | 0.0038443 | 0.00096346
57 | 0.97373 | -0.5055 | 0.005126 | 0.0012847
58 | 0.97464 | -0.48753 | 0.0046012 | 0.0011532
59 | 0.97039 | -0.57113 | 0 | 0
60 | 0.97042 | -0.57053 | 0.0014892 | 0.00037323
61 | 0.97037 | -0.57168 | 0.0014909 | 0.00037366
62 | 0.97344 | -0.51122 | 0.0042589 | 0.0010674
63 | 0.9735 | -0.51008 | 0.0042608 | 0.0010679
64 | 0.97164 | -0.54671 | 0.0064532 | 0.0016173
65 | 0.97181 | -0.54328 | 0.0063679 | 0.0015959
66 | 0.99545 | -0.086471 | 0.0051984 | 0.0013028
67 | 0.99392 | -0.11597 | 0.014979 | 0.003754
68 | 0.98428 | -0.29952 | 0.0035172 | 0.0008815
69 | 0.98616 | -0.26315 | 0 | 0
70 | 0.97463 | -0.48763 | 0.008244 | 0.0020661
71 | 0.98243 | -0.33558 | 0.0024326 | 0.00060967
72 | 0.99131 | -0.16476 | 0.010022 | 0.0025119
73 | 0.99338 | -0.12517 | 0.0051572 | 0.0012925
74 | 0.99021 | -0.18555 | 0.0099724 | 0.0024993
75 | 0.97665 | -0.44795 | 0.0041636 | 0.0010435
76 | 0.97747 | -0.43194 | 0.0086418 | 0.0021658
77 | 0.99753 | -0.047059 | 0.0038391 | 0.00096217
78 | 1 | 0 | -0.39608 | -0.10164
79 | 0.99827 | -0.032635 | 0 | 0
80 | 0.97445 | -0.49118 | 0.004277 | 0.0010719
81 | 0.97379 | -0.504 | 0.0075061 | 0.0018812
82 | 0.97396 | -0.50077 | 0.0076117 | 0.0019077
83 | 0.97151 | -0.54904 | 0.002622 | 0.00065712
84 | 0.97154 | -0.54844 | 0.002622 | 0.00065714
85 | 0.97042 | -0.57053 | 0.0018013 | 0.00045145
86 | 0.97422 | -0.4957 | 0.0051485 | 0.0012903
87 | 0.9741 | -0.49807 | 0.0042979 | 0.0010771
88 | 0.98793 | -0.22908 | 0.003653 | 0.00091552
89 | 0.98515 | -0.28263 | 0 | 0
90 | 0.9847 | -0.29128 | 0.00081853 | 0.00020514
91 | 0.98506 | -0.28439 | 0.002879 | 0.00072155
92 | 0.99514 | -0.091704 | 0.0051572 | 0.0012925
93 | 0.98421 | -0.30082 | 0.0034093 | 0.00085444
94 | 0.98466 | -0.29209 | 0.0008004 | 0.0002006
95 | 0.98503 | -0.28505 | 0.00098196 | 0.0002461
96 | 0.99699 | -0.056751 | 0.0055075 | 0.0013803
97 | 0.99706 | -0.055425 | 0 | 0
98 | 0.97417 | -0.4965 | 0.0016872 | 0.00042285
99 | 0.9742 | -0.49606 | 0 | 0
100 | 0.9962 | -0.071938 | 0.0053521 | 0.0013414
101 | 0.97444 | -0.49128 | 0.0016872 | 0.00042285
102 | 0.99823 | -0.033256 | 0.0052412 | 0.0013136
103 | 0.97446 | -0.4909 | 0.0015895 | 0.00039837
104 | 0.97345 | -0.51079 | 0.0015277 | 0.00038287
105 | 0.97075 | -0.56414 | 0.0014885 | 0.00037304
106 | 0.97075 | -0.56404 | 0.0014919 | 0.0003739
107 | 0.97055 | -0.568 | 0.0014909 | 0.00037365
108 | 0.97084 | -0.56234 | 0.0014919 | 0.0003739
109 | 0.97055 | -0.56802 | 0.0014909 | 0.00037365
110 | 0.97084 | -0.56222 | 0.0014909 | 0.00037365
111 | 0.97049 | -0.56917 | 0.0014895 | 0.0003733
112 | 0.97094 | -0.56022 | 0.0014892 | 0.00037322
113 | 0.97049 | -0.56918 | 0.0014902 | 0.00037348
114 | 0.97315 | -0.51654 | 0.0015276 | 0.00038285
115 | 0.9725 | -0.52949 | 0.0014899 | 0.0003734
116 | 0.97249 | -0.52956 | 0.0014902 | 0.00037348
117 | 0.97236 | -0.53221 | 0.0015587 | 0.00039065
118 | 0.9721 | -0.53737 | 0.0027483 | 0.00068879
119 | 0.97095 | -0.56008 | 0.0026291 | 0.00065891
120 | 0.9778 | -0.42531 | 0.0014909 | 0.00037365
121 | 0.9773 | -0.43505 | 0.0014895 | 0.0003733
122 | 0.97845 | -0.41256 | 0 | 0
123 | 0.97925 | -0.39697 | 0.0015159 | 0.00037991
124 | 0.97831 | -0.41536 | 0.0015388 | 0.00038567
125 | 0.97981 | -0.38609 | 0.001484 | 0.00037192
126 | 0.97831 | -0.41538 | 0.003855 | 0.00096617
127 | 0.98089 | -0.36507 | 0.0015141 | 0.00037948
128 | 0.981 | -0.36296 | 0.001536 | 0.00038495
129 | 0.98269 | -0.33024 | 0 | 0
130 | 0.98268 | -0.33037 | 0 | 0
131 | 0.98355 | -0.31344 | 0.00079517 | 0.00019929
132 | 0.98267 | -0.33064 | 0.0015635 | 0.00039186
133 | 0.98362 | -0.31216 | 0.000785 | 0.00019674
134 | 0.97185 | -0.54222 | 0.0027484 | 0.00068882
135 | 0.97166 | -0.54615 | 0.0027482 | 0.00068878
136 | 0.97158 | -0.54755 | 0.0026273 | 0.00065846
137 | 0.97123 | -0.55448 | 0.0026333 | 0.00065997
138 | 0.97108 | -0.5575 | 0.0026315 | 0.00065953
139 | 0.97107 | -0.55767 | 0.0014892 | 0.00037322
140 | 0.97045 | -0.57001 | 0.0014909 | 0.00037365
141 | 0.97045 | -0.57002 | 0.0014892 | 0.00037323
142 | 0.98375 | -0.30961 | 0.00079656 | 0.00019964
143 | 0.98382 | -0.30839 | 0.00078577 | 0.00019693
144 | 0.98395 | -0.30573 | 0.00079577 | 0.00019944
145 | 0.98401 | -0.30457 | 0.00078577 | 0.00019693
146 | 0.98501 | -0.28532 | 0.0028873 | 0.00072362
147 | 0.9824 | -0.33611 | 0.0043328 | 0.0010859
148 | 0.97576 | -0.46539 | 0.0049023 | 0.0012286
149 | 0.97543 | -0.47194 | 0.0051084 | 0.0012803
150 | 0.97361 | -0.5078 | 0.0038944 | 0.00097603
151 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0038944 | -0.00097603 | 0.0038947 | 0.00097595 | 2.8044e-07 | -8.0888e-08 | 0.0059644 | 0.0059643 | 0.0059644 | 0.97159 | -0.54764 | 0.97167 | -0.54613 | 1.6386
1 | 0.0073269 | 0.0018366 | -0.0073248 | -0.0018358 | 2.0982e-06 | 7.9258e-07 | 0.011221 | 0.011221 | 0.011221 | 0.97167 | -0.54613 | 0.97136 | -0.55214 | 3.0826
2 | -0.011222 | -0.0028125 | 0.011223 | 0.0028134 | 1.6106e-06 | 8.506e-07 | 0.017185 | 0.017185 | 0.017185 | 0.97167 | -0.54613 | 0.97182 | -0.54312 | 4.7211
3 | -0.029493 | -0.0073946 | 0.029498 | 0.0073981 | 5.4574e-06 | 3.4043e-06 | 0.04516 | 0.04516 | 0.04516 | 0.97182 | -0.54312 | 0.97201 | -0.53924 | 12.4065
4 | 0.01827 | 0.0045813 | -0.018266 | -0.0045794 | 3.1988e-06 | 1.9122e-06 | 0.027975 | 0.027975 | 0.027975 | 0.97182 | -0.54312 | 0.97163 | -0.54679 | 7.6854
5 | -0.029498 | -0.0073981 | 0.029512 | 0.0074065 | 1.3505e-05 | 8.4239e-06 | 0.04516 | 0.04516 | 0.04516 | 0.97201 | -0.53924 | 0.9725 | -0.52964 | 12.4065
6 | 0.013837 | 0.0034693 | -0.013834 | -0.0034675 | 3.2183e-06 | 1.8231e-06 | 0.021192 | 0.021192 | 0.021192 | 0.97163 | -0.54679 | 0.97139 | -0.55167 | 5.822
7 | -0.0091048 | -0.002282 | 0.0091056 | 0.0022824 | 8.17e-07 | 3.8427e-07 | 0.013949 | 0.013949 | 0.013949 | 0.97129 | -0.55356 | 0.97139 | -0.55167 | 3.832
8 | 0.0091048 | 0.002282 | -0.009104 | -0.0022817 | 7.7179e-07 | 3.6303e-07 | 0.013949 | 0.013949 | 0.013949 | 0.97129 | -0.55356 | 0.9712 | -0.55534 | 3.832
9 | 0.009104 | 0.0022817 | -0.0091025 | -0.0022809 | 1.5503e-06 | 7.2931e-07 | 0.013949 | 0.013949 | 0.013949 | 0.9712 | -0.55534 | 0.97102 | -0.55891 | 3.8321
10 | -0.0042571 | -0.0010669 | 0.0042575 | 0.0010669 | 3.9356e-07 | -5.2917e-08 | 0.0065252 | 0.0065251 | 0.0065252 | 0.97079 | -0.56337 | 0.97089 | -0.56143 | 1.7926
11 | -0.0042575 | -0.0010669 | 0.0042575 | 0.0010669 | 3.5285e-08 | -4.748e-09 | 0.0065251 | 0.0065251 | 0.0065251 | 0.97089 | -0.56143 | 0.9709 | -0.56126 | 1.7926
12 | -0.038203 | -0.0095848 | 0.038229 | 0.0096008 | 2.5477e-05 | 1.6058e-05 | 0.058458 | 0.058458 | 0.058458 | 0.9725 | -0.52964 | 0.97321 | -0.51566 | 16.06
13 | 0.082528 | 0.020795 | -0.082509 | -0.020783 | 1.8863e-05 | 1.2032e-05 | 0.12585 | 0.12585 | 0.12585 | 0.97612 | -0.45831 | 0.97587 | -0.46309 | 34.5736
14 | -0.084067 | -0.021181 | 0.084068 | 0.021181 | 3.9071e-07 | 2.4926e-07 | 0.12819 | 0.12819 | 0.12819 | 0.97612 | -0.45831 | 0.97612 | -0.45821 | 35.2183
15 | 0.081021 | 0.02041 | -0.080932 | -0.020354 | 8.8841e-05 | 5.6665e-05 | 0.12358 | 0.12358 | 0.12358 | 0.97587 | -0.46309 | 0.9747 | -0.48604 | 33.9501
16 | -0.085605 | -0.021566 | 0.085605 | 0.021567 | 4.1615e-07 | 2.6552e-07 | 0.13054 | 0.13054 | 0.13054 | 0.97612 | -0.45821 | 0.97613 | -0.45811 | 35.8619
17 | 0.057466 | 0.014468 | -0.057428 | -0.014444 | 3.7783e-05 | 2.4018e-05 | 0.087753 | 0.087753 | 0.087753 | 0.9747 | -0.48604 | 0.974 | -0.49981 | 24.1079
18 | 0.023466 | 0.0058855 | -0.023466 | -0.0058852 | 4.3684e-07 | 2.6827e-07 | 0.035826 | 0.035826 | 0.035826 | 0.9747 | -0.48604 | 0.97468 | -0.48643 | 9.8423
19 | -0.087142 | -0.021952 | 0.087159 | 0.021963 | 1.6816e-05 | 1.073e-05 | 0.13288 | 0.13288 | 0.13288 | 0.97613 | -0.45811 | 0.97633 | -0.45408 | 36.5057
20 | 0.055936 | 0.01407 | -0.055922 | -0.014062 | 1.3517e-05 | 8.5896e-06 | 0.085473 | 0.085473 | 0.085473 | 0.974 | -0.49981 | 0.97375 | -0.50487 | 23.4817
21 | 0.02178 | 0.0054628 | -0.021778 | -0.0054612 | 2.6362e-06 | 1.6079e-06 | 0.033253 | 0.033253 | 0.033253 | 0.97468 | -0.48643 | 0.97456 | -0.48897 | 9.1354
22 | -0.088651 | -0.022337 | 0.088691 | 0.022362 | 4.0064e-05 | 2.5568e-05 | 0.13515 | 0.13515 | 0.13515 | 0.97633 | -0.45408 | 0.97681 | -0.44463 | 37.1304
23 | 0.054393 | 0.013678 | -0.054378 | -0.013668 | 1.5378e-05 | 9.7682e-06 | 0.083136 | 0.083136 | 0.083136 | 0.97375 | -0.50487 | 0.97345 | -0.51079 | 22.8397
24 | 0.020092 | 0.0050388 | -0.020091 | -0.0050377 | 1.8425e-06 | 1.1142e-06 | 0.030679 | 0.03068 | 0.03068 | 0.97456 | -0.48897 | 0.97446 | -0.4909 | 8.4284
25 | -0.090182 | -0.022736 | 0.090223 | 0.022762 | 4.1389e-05 | 2.6416e-05 | 0.13743 | 0.13743 | 0.13743 | 0.97681 | -0.44463 | 0.9773 | -0.43505 | 37.7543
26 | 0.004258 | 0.0010668 | -0.0042575 | -0.0010669 | 4.7576e-07 | -6.4074e-08 | 0.0065249 | 0.0065251 | 0.0065251 | 0.97102 | -0.55891 | 0.9709 | -0.56126 | 1.7926
27 | 0.019 | 0.0047661 | -0.018994 | -0.0047625 | 6.0821e-06 | 3.6321e-06 | 0.028426 | 0.028426 | 0.028426 | 0.99465 | -0.10182 | 0.99431 | -0.10854 | 7.8093
28 | -0.019 | -0.0047661 | 0.019008 | 0.0047706 | 7.5401e-06 | 4.5025e-06 | 0.028426 | 0.028426 | 0.028426 | 0.99465 | -0.10182 | 0.99508 | -0.093503 | 7.8093
29 | 0.018994 | 0.0047625 | -0.01899 | -0.0047599 | 4.28e-06 | 2.556e-06 | 0.028426 | 0.028426 | 0.028426 | 0.99431 | -0.10854 | 0.99406 | -0.11327 | 7.8094
30 | -0.022988 | -0.0057681 | 0.022995 | 0.0057728 | 7.7097e-06 | 4.7081e-06 | 0.034378 | 0.034378 | 0.034378 | 0.99508 | -0.093503 | 0.99545 | -0.086471 | 9.4444
31 | 0.014981 | 0.0037551 | -0.014979 | -0.003754 | 1.9261e-06 | 1.1003e-06 | 0.022425 | 0.022425 | 0.022425 | 0.99406 | -0.11327 | 0.99392 | -0.11597 | 6.1606
32 | -0.16459 | -0.041781 | 0.1646 | 0.041792 | 1.6601e-05 | 1.0543e-05 | 0.24901 | 0.24901 | 0.24901 | 0.9843 | -0.299 | 0.98441 | -0.29691 | 22.8027
33 | 0.15439 | 0.039225 | -0.15429 | -0.039165 | 9.508e-05 | 6.032e-05 | 0.23359 | 0.23359 | 0.23359 | 0.9843 | -0.299 | 0.98364 | -0.3118 | 21.3909
34 | 0.010198 | 0.0025564 | -0.010197 | -0.0025555 | 1.7341e-06 | 8.6259e-07 | 0.015417 | 0.015417 | 0.015417 | 0.9843 | -0.299 | 0.98412 | -0.30257 | 4.2356
35 | 0.0069276 | 0.0017361 | -0.0069267 | -0.0017358 | 8.6167e-07 | 2.8509e-07 | 0.010472 | 0.010472 | 0.010472 | 0.98441 | -0.29691 | 0.98428 | -0.29952 | 2.8768
36 | -0.17153 | -0.043528 | 0.17181 | 0.043705 | 0.00027902 | 0.00017731 | 0.25948 | 0.25948 | 0.25948 | 0.98441 | -0.29691 | 0.98616 | -0.26315 | 23.7616
37 | 0.012498 | 0.0031361 | -0.012487 | -0.0031304 | 1.055e-05 | 5.7541e-06 | 0.018908 | 0.018908 | 0.018908 | 0.98364 | -0.3118 | 0.98274 | -0.32952 | 5.1945
38 | 0.1418 | 0.036029 | -0.14156 | -0.035881 | 0.00023271 | 0.0001474 | 0.21468 | 0.21468 | 0.21468 | 0.98364 | -0.3118 | 0.98188 | -0.34595 | 19.6594
39 | 0.012487 | 0.0031304 | -0.012485 | -0.003129 | 2.5023e-06 | 1.3651e-06 | 0.018908 | 0.018908 | 0.018908 | 0.98274 | -0.32952 | 0.98252 | -0.33373 | 5.1946
40 | 0.1373 | 0.034813 | -0.13719 | -0.034744 | 0.00010807 | 6.8826e-05 | 0.20822 | 0.20822 | 0.20822 | 0.98188 | -0.34595 | 0.98104 | -0.36234 | 28.6017
41 | 0.04715 | 0.011844 | -0.047131 | -0.011832 | 1.991e-05 | 1.2615e-05 | 0.072069 | 0.072069 | 0.072069 | 0.97366 | -0.50681 | 0.97321 | -0.51566 | 19.7991
42 | -0.04715 | -0.011844 | 0.047175 | 0.01186 | 2.4621e-05 | 1.56e-05 | 0.072069 | 0.072069 | 0.072069 | 0.97366 | -0.50681 | 0.97421 | -0.49587 | 19.7991
43 | -0.047175 | -0.01186 | 0.047194 | 0.011872 | 1.8563e-05 | 1.1761e-05 | 0.072069 | 0.072069 | 0.072069 | 0.97421 | -0.49587 | 0.97463 | -0.48763 | 19.7991
44 | 0.0067661 | 0.0016957 | -0.0067655 | -0.0016956 | 5.9839e-07 | 1.9053e-07 | 0.010247 | 0.010247 | 0.010247 | 0.98252 | -0.33373 | 0.98243 | -0.33558 | 2.8152
45 | 0.010024 | 0.0025125 | -0.010023 | -0.0025122 | 7.8152e-07 | 3.8144e-07 | 0.015044 | 0.015044 | 0.015044 | 0.99146 | -0.16184 | 0.99137 | -0.16348 | 4.1331
46 | -0.017015 | -0.0042647 | 0.017023 | 0.0042693 | 7.7745e-06 | 4.5655e-06 | 0.025537 | 0.025536 | 0.025537 | 0.99146 | -0.16184 | 0.99195 | -0.15225 | 7.0156
47 | 0.006991 | 0.0017522 | -0.0069903 | -0.0017519 | 6.2468e-07 | 2.0468e-07 | 0.010492 | 0.010492 | 0.010492 | 0.99146 | -0.16184 | 0.99136 | -0.16372 | 2.8825
48 | 0.010023 | 0.0025122 | -0.010022 | -0.0025119 | 6.133e-07 | 2.9935e-07 | 0.015044 | 0.015044 | 0.015044 | 0.99137 | -0.16348 | 0.99131 | -0.16476 | 4.1331
49 | -0.32425 | -0.083018 | 0.32468 | 0.08329 | 0.00042598 | 0.00027207 | 0.48703 | 0.48703 | 0.48703 | 0.99195 | -0.15225 | 0.99338 | -0.12517 | 44.6
50 | 0.30723 | 0.078749 | -0.30673 | -0.078433 | 0.000495 | 0.00031608 | 0.4615 | 0.4615 | 0.4615 | 0.99195 | -0.15225 | 0.99021 | -0.18555 | 42.2615
51 | 0.082807 | 0.020913 | -0.082685 | -0.020836 | 0.00012176 | 7.7669e-05 | 0.12589 | 0.12589 | 0.12589 | 0.97919 | -0.39836 | 0.97761 | -0.42909 | 34.5864
52 | -0.13696 | -0.034592 | 0.13719 | 0.034744 | 0.00023684 | 0.00015139 | 0.20822 | 0.20822 | 0.20822 | 0.97919 | -0.39836 | 0.98104 | -0.36234 | 57.2035
53 | 0.054149 | 0.013679 | -0.054121 | -0.013661 | 2.8263e-05 | 1.7948e-05 | 0.082326 | 0.082326 | 0.082326 | 0.97919 | -0.39836 | 0.97863 | -0.40925 | 22.6171
54 | 0.06979 | 0.017604 | -0.069727 | -0.017564 | 6.2947e-05 | 4.01e-05 | 0.10627 | 0.10627 | 0.10627 | 0.97761 | -0.42909 | 0.97665 | -0.44795 | 29.1943
55 | 0.008643 | 0.0021664 | -0.0086418 | -0.0021658 | 1.1749e-06 | 5.2499e-07 | 0.013155 | 0.013156 | 0.013156 | 0.97761 | -0.42909 | 0.97747 | -0.43194 | 3.6142
56 | 0.052794 | 0.013329 | -0.052753 | -0.013302 | 4.1335e-05 | 2.624e-05 | 0.080309 | 0.080309 | 0.080309 | 0.97863 | -0.40925 | 0.97779 | -0.42561 | 22.063
57 | 0.0052414 | 0.0013136 | -0.0052412 | -0.0013136 | 2.7649e-07 | 1.9411e-08 | 0.0078174 | 0.0078174 | 0.0078174 | 0.99769 | -0.043946 | 0.99763 | -0.045053 | 2.1476
58 | -0.012918 | -0.0032375 | 0.012928 | 0.0032428 | 9.6265e-06 | 5.2572e-06 | 0.019267 | 0.019267 | 0.019267 | 0.99769 | -0.043946 | 0.9985 | -0.028314 | 5.2931
59 | 0.0076768 | 0.0019239 | -0.0076761 | -0.0019237 | 7.081e-07 | 2.6511e-07 | 0.01145 | 0.01145 | 0.01145 | 0.99769 | -0.043946 | 0.99759 | -0.045882 | 3.1455
60 | -0.012928 | -0.0032428 | 0.012931 | 0.0032443 | 2.8684e-06 | 1.5662e-06 | 0.019267 | 0.019267 | 0.019267 | 0.9985 | -0.028314 | 0.99874 | -0.023661 | 5.2931
61 | 0.0038393 | 0.00096208 | -0.0038391 | -0.00096217 | 2.1523e-07 | -9.0726e-08 | 0.0057268 | 0.0057268 | 0.0057268 | 0.99759 | -0.045882 | 0.99753 | -0.047059 | 1.5733
62 | -0.39397 | -0.10135 | 0.39443 | 0.10164 | 0.00045378 | 0.00029 | 0.58791 | 0.58791 | 0.58791 | 0.99874 | -0.023661 | 1 | 0 | 53.8376
63 | 0.38104 | 0.098108 | -0.38088 | -0.098001 | 0.00016628 | 0.00010626 | 0.56864 | 0.56864 | 0.56864 | 0.99874 | -0.023661 | 0.99827 | -0.032635 | 52.0733
64 | 0.052753 | 0.013302 | -0.05264 | -0.01323 | 0.00011335 | 7.1958e-05 | 0.080309 | 0.08031 | 0.08031 | 0.97779 | -0.42561 | 0.9755 | -0.47061 | 22.0631
65 | 0.026177 | 0.0065741 | -0.026151 | -0.0065582 | 2.567e-05 | 1.5894e-05 | 0.039935 | 0.039935 | 0.039935 | 0.9755 | -0.47061 | 0.97445 | -0.49118 | 10.9711
66 | 0.026463 | 0.0066564 | -0.026442 | -0.0066431 | 2.1375e-05 | 1.3244e-05 | 0.040375 | 0.040375 | 0.040375 | 0.9755 | -0.47061 | 0.97464 | -0.48753 | 11.0921
67 | -0.01667 | -0.004179 | 0.016697 | 0.0041952 | 2.7422e-05 | 1.6156e-05 | 0.025518 | 0.025517 | 0.025518 | 0.97209 | -0.53773 | 0.97384 | -0.50327 | 7.0104
68 | 0.01667 | 0.004179 | -0.016669 | -0.0041786 | 8.4039e-07 | 4.9519e-07 | 0.025518 | 0.025518 | 0.025518 | 0.97209 | -0.53773 | 0.97204 | -0.53879 | 7.0104
69 | 0.0051266 | 0.0012848 | -0.005126 | -0.0012847 | 5.4405e-07 | 5.4059e-08 | 0.0078333 | 0.0078334 | 0.0078334 | 0.97384 | -0.50327 | 0.97373 | -0.5055 | 2.152
70 | -0.021824 | -0.00548 | 0.02184 | 0.00549 | 1.64e-05 | 1.0007e-05 | 0.033351 | 0.03335 | 0.033351 | 0.97384 | -0.50327 | 0.97464 | -0.48753 | 9.1622
71 | 0.012825 | 0.0032151 | -0.012822 | -0.0032136 | 2.7402e-06 | 1.5188e-06 | 0.019633 | 0.019633 | 0.019633 | 0.97204 | -0.53879 | 0.97181 | -0.54328 | 5.3937
72 | -0.001491 | -0.00037344 | 0.001491 | 0.0003732 | 4.2366e-08 | -2.3995e-07 | 0.0022862 | 0.0022861 | 0.0022862 | 0.97039 | -0.57113 | 0.97042 | -0.57053 | 0.62807
73 | 0.001491 | 0.00037344 | -0.0014909 | -0.00037366 | 3.9153e-08 | -2.2171e-07 | 0.0022862 | 0.0022863 | 0.0022863 | 0.97039 | -0.57113 | 0.97037 | -0.57168 | 0.62809
74 | -0.0029802 | -0.00074642 | 0.0029802 | 0.00074642 | 6.5951e-10 | -6.1782e-10 | 0.0045695 | 0.0045695 | 0.0045695 | 0.97042 | -0.57053 | 0.97042 | -0.57053 | 1.2554
75 | -0.0042589 | -0.0010674 | 0.0042591 | 0.0010673 | 2.3098e-07 | -3.2855e-08 | 0.0065102 | 0.0065101 | 0.0065102 | 0.97344 | -0.51122 | 0.9735 | -0.51008 | 1.7885
76 | -0.0085199 | -0.0021352 | 0.0085209 | 0.0021356 | 9.2431e-07 | 4.1084e-07 | 0.013023 | 0.013023 | 0.013023 | 0.9735 | -0.51008 | 0.97361 | -0.5078 | 3.5777
77 | -0.0064532 | -0.0016173 | 0.0064542 | 0.0016176 | 1.0555e-06 | 3.185e-07 | 0.0098827 | 0.0098826 | 0.0098827 | 0.97164 | -0.54671 | 0.97181 | -0.54328 | 2.715
78 | -0.028194 | -0.0070757 | 0.028213 | 0.0070878 | 1.9554e-05 | 1.2133e-05 | 0.042148 | 0.042148 | 0.042148 | 0.99545 | -0.086471 | 0.9962 | -0.071938 | 11.5792
79 | 0.0034095 | 0.00085431 | -0.0034093 | -0.00085444 | 2.1123e-07 | -1.3427e-07 | 0.0051543 | 0.0051544 | 0.0051544 | 0.98428 | -0.29952 | 0.98421 | -0.30082 | 1.4161
80 | 0.12019 | 0.030607 | -0.12008 | -0.030536 | 0.00011281 | 7.1154e-05 | 0.18153 | 0.18153 | 0.18153 | 0.98616 | -0.26315 | 0.98515 | -0.28263 | 16.6239
81 | -0.292 | -0.074313 | 0.29248 | 0.074619 | 0.00048043 | 0.00030672 | 0.44101 | 0.44101 | 0.44101 | 0.98616 | -0.26315 | 0.98793 | -0.22908 | 40.3854
82 | -0.055438 | -0.013938 | 0.055479 | 0.013964 | 4.1581e-05 | 2.6419e-05 | 0.084655 | 0.084655 | 0.084655 | 0.97463 | -0.48763 | 0.97543 | -0.47194 | 23.2569
83 | 0.0043329 | 0.0010859 | -0.0043328 | -0.0010859 | 1.0954e-07 | -1.5767e-08 | 0.0065628 | 0.0065628 | 0.0065628 | 0.98243 | -0.33558 | 0.9824 | -0.33611 | 1.803
84 | -0.32983 | -0.084583 | 0.33037 | 0.084925 | 0.00053624 | 0.00034251 | 0.49476 | 0.49476 | 0.49476 | 0.99338 | -0.12517 | 0.99514 | -0.091704 | 45.3074
85 | 0.29676 | 0.075933 | -0.29614 | -0.075535 | 0.00062392 | 0.00039834 | 0.44651 | 0.44651 | 0.44651 | 0.99021 | -0.18555 | 0.98793 | -0.22908 | 40.8892
86 | 0.065563 | 0.01652 | -0.065509 | -0.016485 | 5.4652e-05 | 3.4795e-05 | 0.099924 | 0.099924 | 0.099924 | 0.97665 | -0.44795 | 0.97576 | -0.46539 | 27.4516
87 | 0.0052413 | 0.0013136 | -0.0052412 | -0.0013136 | 1.5519e-07 | 1.0684e-08 | 0.0078127 | 0.0078127 | 0.0078127 | 0.99827 | -0.032635 | 0.99823 | -0.033256 | 2.1464
88 | 0.37564 | 0.096688 | -0.37522 | -0.096422 | 0.00041589 | 0.00026575 | 0.56083 | 0.56083 | 0.56083 | 0.99827 | -0.032635 | 0.99706 | -0.055425 | 51.3579
89 | 0.021874 | 0.0054863 | -0.021869 | -0.0054834 | 4.713e-06 | 2.876e-06 | 0.033404 | 0.033404 | 0.033404 | 0.97445 | -0.49118 | 0.97422 | -0.4957 | 9.1768
90 | -0.0075061 | -0.0018812 | 0.0075073 | 0.0018817 | 1.1545e-06 | 4.477e-07 | 0.01147 | 0.01147 | 0.01147 | 0.97379 | -0.504 | 0.97396 | -0.50077 | 3.151
91 | -0.015119 | -0.0037893 | 0.015122 | 0.0037913 | 3.3932e-06 | 1.9605e-06 | 0.023099 | 0.023099 | 0.023099 | 0.97396 | -0.50077 | 0.9742 | -0.49606 | 6.3459
92 | -0.002622 | -0.00065712 | 0.002622 | 0.00065702 | 7.5366e-08 | -1.0608e-07 | 0.0040159 | 0.0040159 | 0.0040159 | 0.97151 | -0.54904 | 0.97154 | -0.54844 | 1.1033
93 | -0.005244 | -0.0013142 | 0.0052443 | 0.0013142 | 2.2167e-07 | 2.8391e-08 | 0.0080317 | 0.0080317 | 0.0080317 | 0.97154 | -0.54844 | 0.97158 | -0.54755 | 2.2065
94 | -0.0047815 | -0.0011979 | 0.0047816 | 0.0011979 | 1.1605e-07 | 3.1409e-09 | 0.0073316 | 0.0073316 | 0.0073316 | 0.97042 | -0.57053 | 0.97045 | -0.57002 | 2.0142
95 | 0.016721 | 0.0041931 | -0.016719 | -0.0041919 | 1.8854e-06 | 1.1107e-06 | 0.02554 | 0.02554 | 0.02554 | 0.97422 | -0.4957 | 0.9741 | -0.49807 | 7.0165
96 | 0.012421 | 0.0031148 | -0.012415 | -0.0031116 | 5.7598e-06 | 3.1555e-06 | 0.018975 | 0.018975 | 0.018975 | 0.9741 | -0.49807 | 0.97361 | -0.5078 | 5.2129
97 | 0.11333 | 0.028845 | -0.11328 | -0.028815 | 4.7284e-05 | 2.977e-05 | 0.17134 | 0.17134 | 0.17134 | 0.98515 | -0.28263 | 0.9847 | -0.29128 | 15.6904
98 | 0.006749 | 0.0016914 | -0.0067484 | -0.0016912 | 5.678e-07 | 1.7789e-07 | 0.010194 | 0.010194 | 0.010194 | 0.98515 | -0.28263 | 0.98506 | -0.28439 | 2.8006
99 | 0.11247 | 0.02861 | -0.11246 | -0.028607 | 4.3663e-06 | 2.7484e-06 | 0.1701 | 0.1701 | 0.1701 | 0.9847 | -0.29128 | 0.98466 | -0.29209 | 15.5771
100 | 0.0038694 | 0.00096964 | -0.0038693 | -0.00096968 | 1.2154e-07 | -4.2978e-08 | 0.005845 | 0.0058451 | 0.0058451 | 0.98506 | -0.28439 | 0.98503 | -0.28505 | 1.6058
101 | -0.33553 | -0.086218 | 0.33612 | 0.086596 | 0.00059241 | 0.00037841 | 0.50247 | 0.50247 | 0.50247 | 0.99514 | -0.091704 | 0.99706 | -0.055425 | 46.0135
102 | 0.11166 | 0.028407 | -0.11159 | -0.028364 | 6.7095e-05 | 4.2223e-05 | 0.16889 | 0.16889 | 0.16889 | 0.98466 | -0.29209 | 0.98401 | -0.30457 | 15.4664
103 | 0.0028873 | 0.00072358 | -0.0028873 | -0.00072362 | 3.73e-08 | -4.2681e-08 | 0.0043617 | 0.0043617 | 0.0043617 | 0.98503 | -0.28505 | 0.98501 | -0.28532 | 1.1983
104 | -0.0055075 | -0.0013803 | 0.0055078 | 0.0013803 | 3.4791e-07 | 4.3591e-08 | 0.0082199 | 0.0082198 | 0.0082199 | 0.99699 | -0.056751 | 0.99706 | -0.055425 | 2.2582
105 | 0.033592 | 0.0084457 | -0.033566 | -0.0084291 | 2.6469e-05 | 1.6574e-05 | 0.050142 | 0.050142 | 0.050142 | 0.99706 | -0.055425 | 0.9962 | -0.071938 | 13.7754
106 | -0.0016872 | -0.00042285 | 0.0016872 | 0.0004227 | 3.5127e-08 | -1.5313e-07 | 0.0025771 | 0.0025771 | 0.0025771 | 0.97417 | -0.4965 | 0.9742 | -0.49606 | 0.708
107 | -0.01681 | -0.004214 | 0.016813 | 0.0042163 | 3.8296e-06 | 2.258e-06 | 0.025676 | 0.025676 | 0.025676 | 0.9742 | -0.49606 | 0.97444 | -0.49128 | 7.0538
108 | -0.018501 | -0.0046391 | 0.018501 | 0.0046393 | 3.4124e-07 | 2.0419e-07 | 0.028252 | 0.028252 | 0.028252 | 0.97444 | -0.49128 | 0.97446 | -0.4909 | 7.7616
109 | 0.05285 | 0.013286 | -0.052835 | -0.013276 | 1.4521e-05 | 9.2196e-06 | 0.080801 | 0.080801 | 0.080801 | 0.97345 | -0.51079 | 0.97315 | -0.51654 | 22.1981
110 | -0.015215 | -0.0038137 | 0.015215 | 0.0038138 | 7.2829e-08 | 4.2196e-08 | 0.023323 | 0.023323 | 0.023323 | 0.97075 | -0.56414 | 0.97075 | -0.56404 | 6.4073
111 | 0.013727 | 0.0034407 | -0.013724 | -0.0034393 | 2.5283e-06 | 1.4299e-06 | 0.021041 | 0.021041 | 0.021041 | 0.97075 | -0.56414 | 0.97055 | -0.568 | 5.7805
112 | -0.016707 | -0.0041877 | 0.016708 | 0.0041885 | 1.3495e-06 | 7.9587e-07 | 0.02561 | 0.02561 | 0.02561 | 0.97075 | -0.56404 | 0.97084 | -0.56234 | 7.0356
113 | 0.012233 | 0.0030656 | -0.012233 | -0.0030656 | 1.1724e-08 | 6.4052e-09 | 0.018755 | 0.018755 | 0.018755 | 0.97055 | -0.568 | 0.97055 | -0.56802 | 5.1526
114 | -0.0182 | -0.0045624 | 0.0182 | 0.0045625 | 1.0557e-07 | 6.3091e-08 | 0.027896 | 0.027896 | 0.027896 | 0.97084 | -0.56234 | 0.97084 | -0.56222 | 7.6638
115 | 0.010742 | 0.002692 | -0.010742 | -0.0026917 | 5.8543e-07 | 3.0355e-07 | 0.01647 | 0.01647 | 0.01647 | 0.97055 | -0.56802 | 0.97049 | -0.56917 | 4.5246
116 | -0.019691 | -0.0049361 | 0.019693 | 0.0049372 | 1.8735e-06 | 1.1312e-06 | 0.030181 | 0.030181 | 0.030181 | 0.97084 | -0.56222 | 0.97094 | -0.56022 | 8.2915
117 | 0.0092522 | 0.0023184 | -0.0092522 | -0.0023184 | 6.8604e-09 | 3.2665e-09 | 0.014186 | 0.014186 | 0.014186 | 0.97049 | -0.56917 | 0.97049 | -0.56918 | 3.8972
118 | -0.021182 | -0.0053105 | 0.021182 | 0.0053105 | 1.4216e-07 | 8.6534e-08 | 0.032463 | 0.032463 | 0.032463 | 0.97094 | -0.56022 | 0.97095 | -0.56008 | 8.9185
119 | 0.007762 | 0.0019449 | -0.0077617 | -0.0019448 | 3.0558e-07 | 1.2448e-07 | 0.011901 | 0.011901 | 0.011901 | 0.97049 | -0.56918 | 0.97045 | -0.57001 | 3.2695
120 | 0.051308 | 0.012894 | -0.051276 | -0.012873 | 3.1695e-05 | 2.0114e-05 | 0.078465 | 0.078466 | 0.078466 | 0.97315 | -0.51654 | 0.9725 | -0.52949 | 21.5565
121 | 0.049786 | 0.0125 | -0.049786 | -0.0125 | 1.7157e-07 | 1.0883e-07 | 0.076186 | 0.076186 | 0.076186 | 0.9725 | -0.52949 | 0.97249 | -0.52956 | 20.9302
122 | 0.048296 | 0.012126 | -0.04829 | -0.012123 | 6.0933e-06 | 3.8628e-06 | 0.073906 | 0.073906 | 0.073906 | 0.97249 | -0.52956 | 0.97236 | -0.53221 | 20.3038
123 | 0.046731 | 0.011732 | -0.04672 | -0.011725 | 1.1492e-05 | 7.2806e-06 | 0.07152 | 0.07152 | 0.07152 | 0.97236 | -0.53221 | 0.9721 | -0.53737 | 19.6485
124 | 0.043971 | 0.011036 | -0.043961 | -0.011029 | 1.0182e-05 | 6.442e-06 | 0.067314 | 0.067314 | 0.067314 | 0.9721 | -0.53737 | 0.97185 | -0.54222 | 18.4927
125 | -0.023812 | -0.0059695 | 0.023814 | 0.0059711 | 2.7383e-06 | 1.6847e-06 | 0.036493 | 0.036493 | 0.036493 | 0.97095 | -0.56008 | 0.97107 | -0.55767 | 10.0254
126 | 0.091756 | 0.023163 | -0.091713 | -0.023136 | 4.2766e-05 | 2.7297e-05 | 0.13969 | 0.13969 | 0.13969 | 0.9778 | -0.42531 | 0.9773 | -0.43505 | 38.3773
127 | -0.093246 | -0.023537 | 0.093303 | 0.023573 | 5.6979e-05 | 3.6372e-05 | 0.14196 | 0.14196 | 0.14196 | 0.9778 | -0.42531 | 0.97845 | -0.41256 | 39.0006
128 | -0.098698 | -0.024925 | 0.098772 | 0.024972 | 7.3833e-05 | 4.7143e-05 | 0.15017 | 0.15017 | 0.15017 | 0.97845 | -0.41256 | 0.97925 | -0.39697 | 41.2545
129 | 0.0053946 | 0.0013519 | -0.0053939 | -0.0013518 | 7.1936e-07 | 1.0247e-07 | 0.008204 | 0.0082041 | 0.0082041 | 0.97845 | -0.41256 | 0.97831 | -0.41536 | 2.2539
130 | -0.10029 | -0.025352 | 0.10034 | 0.025385 | 5.2353e-05 | 3.343e-05 | 0.15247 | 0.15247 | 0.15247 | 0.97925 | -0.39697 | 0.97981 | -0.38609 | 41.8872
131 | 0.0038551 | 0.00096617 | -0.003855 | -0.00096617 | 2.8175e-09 | -9.4085e-10 | 0.0058636 | 0.0058636 | 0.0058636 | 0.97831 | -0.41536 | 0.97831 | -0.41538 | 1.6109
132 | -0.10182 | -0.025757 | 0.10193 | 0.025823 | 0.00010277 | 6.5631e-05 | 0.15472 | 0.15472 | 0.15472 | 0.97981 | -0.38609 | 0.98089 | -0.36507 | 42.5064
133 | -0.10344 | -0.026202 | 0.10345 | 0.026209 | 1.0484e-05 | 6.6954e-06 | 0.15702 | 0.15702 | 0.15702 | 0.98089 | -0.36507 | 0.981 | -0.36296 | 43.1374
134 | -0.10499 | -0.026594 | 0.10515 | 0.0267 | 0.00016528 | 0.00010556 | 0.15935 | 0.15935 | 0.15935 | 0.981 | -0.36296 | 0.98269 | -0.33024 | 43.7774
135 | 0.0015636 | 0.0003917 | -0.0015636 | -0.00039175 | 9.417e-09 | -5.073e-08 | 0.0023676 | 0.0023676 | 0.0023676 | 0.98269 | -0.33024 | 0.98268 | -0.33037 | 0.65043
136 | -0.10672 | -0.027091 | 0.1068 | 0.027146 | 8.6348e-05 | 5.4816e-05 | 0.16172 | 0.16172 | 0.16172 | 0.98269 | -0.33024 | 0.98355 | -0.31344 | 22.2139
137 | 0.0015636 | 0.00039175 | -0.0015635 | -0.00039186 | 1.9884e-08 | -1.0711e-07 | 0.0023676 | 0.0023676 | 0.0023676 | 0.98268 | -0.33037 | 0.98267 | -0.33064 | 0.65044
138 | -0.1076 | -0.027345 | 0.1076 | 0.02735 | 6.6199e-06 | 4.1607e-06 | 0.16292 | 0.16292 | 0.16292 | 0.98355 | -0.31344 | 0.98362 | -0.31216 | 14.9194
139 | -0.10839 | -0.027546 | 0.1084 | 0.027555 | 1.3312e-05 | 8.3691e-06 | 0.16411 | 0.16411 | 0.16411 | 0.98362 | -0.31216 | 0.98375 | -0.30961 | 15.0282
140 | 0.041213 | 0.010341 | -0.041205 | -0.010336 | 7.7153e-06 | 4.8738e-06 | 0.063105 | 0.063105 | 0.063105 | 0.97185 | -0.54222 | 0.97166 | -0.54615 | 17.3367
141 | 0.0078721 | 0.0019729 | -0.0078715 | -0.0019726 | 5.2512e-07 | 2.1674e-07 | 0.012055 | 0.012055 | 0.012055 | 0.97166 | -0.54615 | 0.97158 | -0.54755 | 3.3119
142 | 0.030585 | 0.0076741 | -0.030573 | -0.0076665 | 1.2144e-05 | 7.5896e-06 | 0.046841 | 0.046841 | 0.046841 | 0.97166 | -0.54615 | 0.97123 | -0.55448 | 12.8685
143 | 0.027939 | 0.0070065 | -0.027935 | -0.007004 | 4.0192e-06 | 2.4999e-06 | 0.042807 | 0.042807 | 0.042807 | 0.97123 | -0.55448 | 0.97108 | -0.5575 | 11.7601
144 | 0.025304 | 0.0063445 | -0.025303 | -0.0063444 | 2.0358e-07 | 1.2583e-07 | 0.038774 | 0.038774 | 0.038774 | 0.97108 | -0.5575 | 0.97107 | -0.55767 | 10.6523
145 | 0.0062708 | 0.0015711 | -0.0062708 | -0.0015711 | 3.1729e-09 | 8.9951e-10 | 0.009615 | 0.009615 | 0.009615 | 0.97045 | -0.57001 | 0.97045 | -0.57002 | 2.6415
146 | -0.1092 | -0.027754 | 0.10921 | 0.027758 | 6.4171e-06 | 4.0354e-06 | 0.16531 | 0.16531 | 0.16531 | 0.98375 | -0.30961 | 0.98382 | -0.30839 | 15.1385
147 | -0.10999 | -0.027955 | 0.11001 | 0.027964 | 1.4113e-05 | 8.8773e-06 | 0.1665 | 0.1665 | 0.1665 | 0.98382 | -0.30839 | 0.98395 | -0.30573 | 15.2473
148 | -0.1108 | -0.028164 | 0.11081 | 0.028167 | 6.1984e-06 | 3.8998e-06 | 0.1677 | 0.1677 | 0.1677 | 0.98395 | -0.30573 | 0.98401 | -0.30457 | 15.3575
149 | 0.060607 | 0.015257 | -0.060588 | -0.015245 | 1.8974e-05 | 1.207e-05 | 0.092448 | 0.092448 | 0.092448 | 0.97576 | -0.46539 | 0.97543 | -0.47194 | 25.3978

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.40325 | 0.10344

## res_load
| p_mw | q_mvar
0 | 0.0038944 | 0.00097603
1 | 0.0073248 | 0.0018358
2 | 0.0044291 | 0.00111
3 | 0.0047285 | 0.0011851
4 | 0.0042571 | 0.0010669
5 | 0.0086915 | 0.0021783
6 | 0.0015395 | 0.00038584
7 | 0.0014885 | 0.00037304
8 | 0.0015368 | 0.00038515
9 | 0.0015373 | 0.00038528
10 | 0.0014919 | 0.0003739
11 | 0.0016854 | 0.00042239
12 | 0.0014919 | 0.0003739
13 | 0.0015294 | 0.00038329
14 | 0.0016854 | 0.00042239
15 | 0.0014909 | 0.00037365
16 | 0.0048445 | 0.0012141
17 | 0.0039801 | 0.00099752
18 | 0.0040092 | 0.0010048
19 | 0.010197 | 0.0025555
20 | 0.0042632 | 0.0010685
21 | 0.0089017 | 0.002231
22 | 0.0057187 | 0.0014333
23 | 0.0069903 | 0.0017519
24 | 0.004252 | 0.0010657
25 | 0.0013265 | 0.00033244
26 | 0.0052412 | 0.0013136
27 | 0.0038368 | 0.00096159
28 | 0.0038443 | 0.00096346
29 | 0.005126 | 0.0012847
30 | 0.0046012 | 0.0011532
31 | 0.0014892 | 0.00037323
32 | 0.0014909 | 0.00037366
33 | 0.0042589 | 0.0010674
34 | 0.0042608 | 0.0010679
35 | 0.0064532 | 0.0016173
36 | 0.0063679 | 0.0015959
37 | 0.0051984 | 0.0013028
38 | 0.014979 | 0.003754
39 | 0.0035172 | 0.0008815
40 | 0.008244 | 0.0020661
41 | 0.0024326 | 0.00060967
42 | 0.010022 | 0.0025119
43 | 0.0051572 | 0.0012925
44 | 0.0099724 | 0.0024993
45 | 0.0041636 | 0.0010435
46 | 0.0086418 | 0.0021658
47 | 0.0038391 | 0.00096217
48 | 0.0071716 | 0.0017974
49 | 0.004277 | 0.0010719
50 | 0.0075061 | 0.0018812
51 | 0.0076117 | 0.0019077
52 | 0.002622 | 0.00065712
53 | 0.002622 | 0.00065714
54 | 0.0018013 | 0.00045145
55 | 0.0051485 | 0.0012903
56 | 0.0042979 | 0.0010771
57 | 0.003653 | 0.00091552
58 | 0.00081853 | 0.00020514
59 | 0.002879 | 0.00072155
60 | 0.0051572 | 0.0012925
61 | 0.0034093 | 0.00085444
62 | 0.0008004 | 0.0002006
63 | 0.00098196 | 0.0002461
64 | 0.0055075 | 0.0013803
65 | 0.0016872 | 0.00042285
66 | 0.0053521 | 0.0013414
67 | 0.0016872 | 0.00042285
68 | 0.0052412 | 0.0013136
69 | 0.0015895 | 0.00039837
70 | 0.0015277 | 0.00038287
71 | 0.0014885 | 0.00037304
72 | 0.0014919 | 0.0003739
73 | 0.0014909 | 0.00037365
74 | 0.0014919 | 0.0003739
75 | 0.0014909 | 0.00037365
76 | 0.0014909 | 0.00037365
77 | 0.0014895 | 0.0003733
78 | 0.0014892 | 0.00037322
79 | 0.0014902 | 0.00037348
80 | 0.0015276 | 0.00038285
81 | 0.0014899 | 0.0003734
82 | 0.0014902 | 0.00037348
83 | 0.0015587 | 0.00039065
84 | 0.0027483 | 0.00068879
85 | 0.0026291 | 0.00065891
86 | 0.0014909 | 0.00037365
87 | 0.0014895 | 0.0003733
88 | 0.0015159 | 0.00037991
89 | 0.0015388 | 0.00038567
90 | 0.001484 | 0.00037192
91 | 0.003855 | 0.00096617
92 | 0.0015141 | 0.00037948
93 | 0.001536 | 0.00038495
94 | 0.00079517 | 0.00019929
95 | 0.0015635 | 0.00039186
96 | 0.000785 | 0.00019674
97 | 0.0027484 | 0.00068882
98 | 0.0027482 | 0.00068878
99 | 0.0026273 | 0.00065846
100 | 0.0026333 | 0.00065997
101 | 0.0026315 | 0.00065953
102 | 0.0014892 | 0.00037322
103 | 0.0014909 | 0.00037365
104 | 0.0014892 | 0.00037323
105 | 0.00079656 | 0.00019964
106 | 0.00078577 | 0.00019693
107 | 0.00079577 | 0.00019944
108 | 0.00078577 | 0.00019693
109 | 0.0028873 | 0.00072362
110 | 0.0043328 | 0.0010859
111 | 0.0049023 | 0.0012286
112 | 0.0051084 | 0.0012803
113 | 0.0038944 | 0.00097603

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1