## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-703_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-703_0_5_node_2 | 0.4 | n |  | TRUE
2 | bus_LV_261-703_0_5_node_1 | 0.4 | n |  | TRUE
3 | bus_LV_261-703_0_5_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_261-703_0_5_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_261-703_0_5_node_59 | 0.4 | n |  | TRUE
6 | bus_LV_261-703_0_5_node_5 | 0.4 | n |  | TRUE
7 | bus_LV_261-703_0_5_node_18 | 0.4 | n |  | TRUE
8 | bus_LV_261-703_0_5_node_62 | 0.4 | n |  | TRUE
9 | bus_LV_261-703_0_5_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_261-703_0_5_node_12 | 0.4 | n |  | TRUE
11 | bus_LV_261-703_0_5_node_28 | 0.4 | n |  | TRUE
12 | bus_LV_261-703_0_5_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_261-703_0_5_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_261-703_0_5_node_126 | 0.4 | n |  | TRUE
15 | bus_LV_261-703_0_5_node_131 | 0.4 | n |  | TRUE
16 | bus_LV_261-703_0_5_node_115 | 0.4 | n |  | TRUE
17 | bus_LV_261-703_0_5_node_14 | 0.4 | n |  | TRUE
18 | bus_LV_261-703_0_5_node_114 | 0.4 | n |  | TRUE
19 | bus_LV_261-703_0_5_node_110 | 0.4 | n |  | TRUE
20 | bus_LV_261-703_0_5_node_23 | 0.4 | n |  | TRUE
21 | bus_LV_261-703_0_5_node_15 | 0.4 | n |  | TRUE
22 | bus_LV_261-703_0_5_node_21 | 0.4 | n |  | TRUE
23 | bus_LV_261-703_0_5_node_132 | 0.4 | n |  | TRUE
24 | bus_LV_261-703_0_5_node_117 | 0.4 | n |  | TRUE
25 | bus_LV_261-703_0_5_node_58 | 0.4 | n |  | TRUE
26 | bus_LV_261-703_0_5_node_60 | 0.4 | n |  | TRUE
27 | bus_LV_261-703_0_5_node_64 | 0.4 | n |  | TRUE
28 | bus_LV_261-703_0_5_node_69 | 0.4 | n |  | TRUE
29 | bus_LV_261-703_0_5_node_54 | 0.4 | n |  | TRUE
30 | bus_LV_261-703_0_5_node_56 | 0.4 | n |  | TRUE
31 | bus_LV_261-703_0_5_node_80 | 0.4 | n |  | TRUE
32 | bus_LV_261-703_0_5_node_52 | 0.4 | n |  | TRUE
33 | bus_LV_261-703_0_5_node_17 | 0.4 | n |  | TRUE
34 | bus_LV_261-703_0_5_node_53 | 0.4 | n |  | TRUE
35 | bus_LV_261-703_0_5_node_50 | 0.4 | n |  | TRUE
36 | bus_LV_261-703_0_5_node_55 | 0.4 | n |  | TRUE
37 | bus_LV_261-703_0_5_node_66 | 0.4 | n |  | TRUE
38 | bus_LV_261-703_0_5_node_61 | 0.4 | n |  | TRUE
39 | bus_LV_261-703_0_5_node_87 | 0.4 | n |  | TRUE
40 | bus_LV_261-703_0_5_node_78 | 0.4 | n |  | TRUE
41 | bus_LV_261-703_0_5_node_75 | 0.4 | n |  | TRUE
42 | bus_LV_261-703_0_5_node_116 | 0.4 | n |  | TRUE
43 | bus_LV_261-703_0_5_node_105 | 0.4 | n |  | TRUE
44 | bus_LV_261-703_0_5_node_24 | 0.4 | n |  | TRUE
45 | bus_LV_261-703_0_5_node_121 | 0.4 | n |  | TRUE
46 | bus_LV_261-703_0_5_node_119 | 0.4 | n |  | TRUE
47 | bus_LV_261-703_0_5_node_26 | 0.4 | n |  | TRUE
48 | bus_LV_261-703_0_5_node_127 | 0.4 | n |  | TRUE
49 | bus_LV_261-703_0_5_node_128 | 0.4 | n |  | TRUE
50 | bus_LV_261-703_0_5_node_31 | 0.4 | n |  | TRUE
51 | bus_LV_261-703_0_5_node_29 | 0.4 | n |  | TRUE
52 | bus_LV_261-703_0_5_node_63 | 0.4 | n |  | TRUE
53 | bus_LV_261-703_0_5_node_86 | 0.4 | n |  | TRUE
54 | bus_LV_261-703_0_5_node_85 | 0.4 | n |  | TRUE
55 | bus_LV_261-703_0_5_node_130 | 0.4 | n |  | TRUE
56 | bus_LV_261-703_0_5_node_122 | 0.4 | n |  | TRUE
57 | bus_LV_261-703_0_5_node_35 | 0.4 | n |  | TRUE
58 | bus_LV_261-703_0_5_node_36 | 0.4 | n |  | TRUE
59 | bus_LV_261-703_0_5_node_39 | 0.4 | n |  | TRUE
60 | bus_LV_261-703_0_5_node_38 | 0.4 | n |  | TRUE
61 | bus_LV_261-703_0_5_node_102 | 0.4 | n |  | TRUE
62 | bus_LV_261-703_0_5_node_19 | 0.4 | n |  | TRUE
63 | bus_LV_261-703_0_5_node_20 | 0.4 | n |  | TRUE
64 | bus_LV_261-703_0_5_node_41 | 0.4 | n |  | TRUE
65 | bus_LV_261-703_0_5_node_40 | 0.4 | n |  | TRUE
66 | bus_LV_261-703_0_5_node_113 | 0.4 | n |  | TRUE
67 | bus_LV_261-703_0_5_node_120 | 0.4 | n |  | TRUE
68 | bus_LV_261-703_0_5_node_125 | 0.4 | n |  | TRUE
69 | bus_LV_261-703_0_5_node_123 | 0.4 | n |  | TRUE
70 | bus_LV_261-703_0_5_node_129 | 0.4 | n |  | TRUE
71 | bus_LV_261-703_0_5_node_30 | 0.4 | n |  | TRUE
72 | bus_LV_261-703_0_5_node_32 | 0.4 | n |  | TRUE
73 | bus_LV_261-703_0_5_node_33 | 0.4 | n |  | TRUE
74 | bus_LV_261-703_0_5_node_34 | 0.4 | n |  | TRUE
75 | bus_LV_261-703_0_5_node_93 | 0.4 | n |  | TRUE
76 | bus_LV_261-703_0_5_node_101 | 0.4 | n |  | TRUE
77 | bus_LV_261-703_0_5_node_90 | 0.4 | n |  | TRUE
78 | bus_LV_261-703_0_5_node_37 | 0.4 | n |  | TRUE
79 | bus_LV_261-703_0_5_node_49 | 0.4 | n |  | TRUE
80 | bus_LV_261-703_0_5_node_47 | 0.4 | n |  | TRUE
81 | bus_LV_261-703_0_5_node_42 | 0.4 | n |  | TRUE
82 | bus_LV_261-703_0_5_node_43 | 0.4 | n |  | TRUE
83 | bus_LV_261-703_0_5_node_44 | 0.4 | n |  | TRUE
84 | bus_LV_261-703_0_5_node_51 | 0.4 | n |  | TRUE
85 | bus_LV_261-703_0_5_node_45 | 0.4 | n |  | TRUE
86 | bus_LV_261-703_0_5_node_46 | 0.4 | n |  | TRUE
87 | bus_LV_261-703_0_5_node_48 | 0.4 | n |  | TRUE
88 | bus_LV_261-703_0_5_node_65 | 0.4 | n |  | TRUE
89 | bus_LV_261-703_0_5_node_79 | 0.4 | n |  | TRUE
90 | bus_LV_261-703_0_5_node_84 | 0.4 | n |  | TRUE
91 | bus_LV_261-703_0_5_node_76 | 0.4 | n |  | TRUE
92 | bus_LV_261-703_0_5_node_77 | 0.4 | n |  | TRUE
93 | bus_LV_261-703_0_5_node_104 | 0.4 | n |  | TRUE
94 | bus_LV_261-703_0_5_node_70 | 0.4 | n |  | TRUE
95 | bus_LV_261-703_0_5_node_71 | 0.4 | n |  | TRUE
96 | bus_LV_261-703_0_5_node_72 | 0.4 | n |  | TRUE
97 | bus_LV_261-703_0_5_node_73 | 0.4 | n |  | TRUE
98 | bus_LV_261-703_0_5_node_74 | 0.4 | n |  | TRUE
99 | bus_LV_261-703_0_5_node_81 | 0.4 | n |  | TRUE
100 | bus_LV_261-703_0_5_node_82 | 0.4 | n |  | TRUE
101 | bus_LV_261-703_0_5_node_83 | 0.4 | n |  | TRUE
102 | bus_LV_261-703_0_5_node_88 | 0.4 | n |  | TRUE
103 | bus_LV_261-703_0_5_node_89 | 0.4 | n |  | TRUE
104 | bus_LV_261-703_0_5_node_91 | 0.4 | n |  | TRUE
105 | bus_LV_261-703_0_5_node_92 | 0.4 | n |  | TRUE
106 | bus_LV_261-703_0_5_node_106 | 0.4 | n |  | TRUE
107 | bus_LV_261-703_0_5_node_103 | 0.4 | n |  | TRUE
108 | bus_LV_261-703_0_5_node_99 | 0.4 | n |  | TRUE
109 | bus_LV_261-703_0_5_node_94 | 0.4 | n |  | TRUE
110 | bus_LV_261-703_0_5_node_95 | 0.4 | n |  | TRUE
111 | bus_LV_261-703_0_5_node_96 | 0.4 | n |  | TRUE
112 | bus_LV_261-703_0_5_node_97 | 0.4 | n |  | TRUE
113 | bus_LV_261-703_0_5_node_98 | 0.4 | n |  | TRUE
114 | bus_LV_261-703_0_5_node_112 | 0.4 | n |  | TRUE
115 | bus_LV_261-703_0_5_node_100 | 0.4 | n |  | TRUE
116 | bus_LV_261-703_0_5_node_111 | 0.4 | n |  | TRUE
117 | bus_LV_261-703_0_5_node_108 | 0.4 | n |  | TRUE
118 | bus_LV_261-703_0_5_node_118 | 0.4 | n |  | TRUE
119 | bus_MV_530_0_node_58 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-703_0_5_load_0 | 0 | 0.050747 | 0.012719 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-703_0_5_load_1 | 2 | 0.0047748 | 0.0011967 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-703_0_5_load_3 | 3 | 0.017086 | 0.0042823 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-703_0_5_load_18 | 7 | 0.01019 | 0.0025539 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-703_0_5_load_62 | 8 | 0.0073751 | 0.0018484 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-703_0_5_load_28 | 11 | 0.0029605 | 0.00074198 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-703_0_5_load_131 | 15 | 0.010137 | 0.0025405 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-703_0_5_load_115 | 16 | 0.0040577 | 0.0010169 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-703_0_5_load_114 | 18 | 0.0043855 | 0.0010991 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-703_0_5_load_110 | 19 | 0.0024383 | 0.00061109 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-703_0_5_load_21 | 22 | 0.012182 | 0.0030532 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-703_0_5_load_132 | 23 | 0.0039084 | 0.00097953 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-703_0_5_load_117 | 24 | 0.012064 | 0.0030236 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-703_0_5_load_64 | 27 | 0.0072823 | 0.0018251 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-703_0_5_load_69 | 28 | 0.0087788 | 0.0022002 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-703_0_5_load_80 | 31 | 0.0076127 | 0.0019079 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-703_0_5_load_17 | 33 | 0.0074522 | 0.0018677 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_261-703_0_5_load_50 | 35 | 0.0043697 | 0.0010951 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_261-703_0_5_load_66 | 37 | 0.0154 | 0.0038595 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_261-703_0_5_load_87 | 39 | 0.0026134 | 0.00065497 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_261-703_0_5_load_78 | 40 | 0.0044259 | 0.0011092 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_261-703_0_5_load_75 | 41 | 0.0092202 | 0.0023108 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_261-703_0_5_load_116 | 42 | 0.016172 | 0.004053 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_261-703_0_5_load_105 | 43 | 0.0051703 | 0.0012958 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_261-703_0_5_load_121 | 45 | 0.0043849 | 0.001099 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_261-703_0_5_load_119 | 46 | 0.0033488 | 0.00083929 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_261-703_0_5_load_128 | 49 | 0.0047044 | 0.001179 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_261-703_0_5_load_31 | 50 | 0.0025274 | 0.00063344 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_261-703_0_5_load_29 | 51 | 0.002962 | 0.00074235 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_261-703_0_5_load_63 | 52 | 0.0072852 | 0.0018258 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_261-703_0_5_load_86 | 53 | 0.0028196 | 0.00070667 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_261-703_0_5_load_85 | 54 | 0.0028217 | 0.0007072 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_261-703_0_5_load_130 | 55 | 0.0091873 | 0.0023025 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_261-703_0_5_load_122 | 56 | 0.0042759 | 0.0010716 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_261-703_0_5_load_35 | 57 | 0.0091412 | 0.002291 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_261-703_0_5_load_36 | 58 | 0.012257 | 0.0030719 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_261-703_0_5_load_39 | 59 | 0.0089725 | 0.0022487 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_261-703_0_5_load_38 | 60 | 0.011573 | 0.0029004 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_261-703_0_5_load_19 | 62 | 0.0079985 | 0.0020046 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_261-703_0_5_load_20 | 63 | 0.00987 | 0.0024736 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_261-703_0_5_load_41 | 64 | 0.0050347 | 0.0012618 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_261-703_0_5_load_40 | 65 | 0.0054018 | 0.0013538 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_261-703_0_5_load_113 | 66 | 0.0015004 | 0.00037603 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_261-703_0_5_load_120 | 67 | 0.00404 | 0.0010125 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_261-703_0_5_load_123 | 69 | 0.0032919 | 0.00082502 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_261-703_0_5_load_129 | 70 | 0.0092053 | 0.0023071 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_261-703_0_5_load_30 | 71 | 0.0077591 | 0.0019446 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_261-703_0_5_load_33 | 73 | 0.002218 | 0.00055589 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_261-703_0_5_load_34 | 74 | 0.0049289 | 0.0012353 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_261-703_0_5_load_37 | 78 | 0.0054051 | 0.0013546 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_261-703_0_5_load_49 | 79 | 0.0055556 | 0.0013924 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_261-703_0_5_load_47 | 80 | 0.0045267 | 0.0011345 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_261-703_0_5_load_42 | 81 | 0.0059088 | 0.0014809 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_261-703_0_5_load_43 | 82 | 0.0041414 | 0.0010379 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_261-703_0_5_load_44 | 83 | 0.0048777 | 0.0012225 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_261-703_0_5_load_51 | 84 | 0.0051159 | 0.0012822 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_261-703_0_5_load_45 | 85 | 0.0089055 | 0.0022319 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_261-703_0_5_load_46 | 86 | 0.026104 | 0.0065422 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_261-703_0_5_load_48 | 87 | 0.0082792 | 0.002075 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_261-703_0_5_load_65 | 88 | 0.010723 | 0.0026874 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_261-703_0_5_load_79 | 89 | 0.0053015 | 0.0013287 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_261-703_0_5_load_84 | 90 | 0.0040604 | 0.0010176 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_261-703_0_5_load_76 | 91 | 0.012606 | 0.0031594 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_261-703_0_5_load_77 | 92 | 0.004843 | 0.0012138 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_261-703_0_5_load_70 | 94 | 0.013941 | 0.0034939 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_261-703_0_5_load_71 | 95 | 0.0044568 | 0.001117 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_261-703_0_5_load_72 | 96 | 0.0063595 | 0.0015938 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_261-703_0_5_load_73 | 97 | 0.0024885 | 0.00062368 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_261-703_0_5_load_74 | 98 | 0.0027051 | 0.00067796 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_261-703_0_5_load_81 | 99 | 0.0081908 | 0.0020528 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_261-703_0_5_load_82 | 100 | 0.0047172 | 0.0011822 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_261-703_0_5_load_83 | 101 | 0.0071996 | 0.0018044 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_261-703_0_5_load_88 | 102 | 0.0045754 | 0.0011467 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_261-703_0_5_load_89 | 103 | 0.0052197 | 0.0013082 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_261-703_0_5_load_91 | 104 | 0.0052894 | 0.0013257 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_261-703_0_5_load_106 | 106 | 0.0014142 | 0.00035442 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_261-703_0_5_load_99 | 108 | 0.0033169 | 0.00083128 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_261-703_0_5_load_94 | 109 | 0.005219 | 0.001308 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_261-703_0_5_load_95 | 110 | 0.0023847 | 0.00059765 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_261-703_0_5_load_96 | 111 | 0.0052939 | 0.0013268 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_261-703_0_5_load_97 | 112 | 0.0045611 | 0.0011431 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_261-703_0_5_load_98 | 113 | 0.002216 | 0.00055539 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_261-703_0_5_load_112 | 114 | 0.0045085 | 0.0011299 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_261-703_0_5_load_100 | 115 | 0.0068515 | 0.0017171 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_261-703_0_5_load_111 | 116 | 0.0029094 | 0.00072917 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_261-703_0_5_load_118 | 118 | 0.0046456 | 0.0011643 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 28 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-703_0_5_line_0 |  | 0 | 1 | 0.01458 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-703_0_5_line_1 |  | 1 | 4 | 0.003639 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-703_0_5_line_2 |  | 2 | 3 | 0.0089186 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-703_0_5_line_3 |  | 3 | 5 | 0.021895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-703_0_5_line_4 |  | 4 | 6 | 0.0095298 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_261-703_0_5_line_5 |  | 4 | 7 | 0.017006 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_261-703_0_5_line_6 |  | 5 | 24 | 0.019461 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
7 | LV_261-703_0_5_line_7 |  | 5 | 25 | 0.0073963 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
8 | LV_261-703_0_5_line_8 |  | 6 | 8 | 0.032714 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_261-703_0_5_line_9 |  | 7 | 33 | 0.015408 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_261-703_0_5_line_10 |  | 8 | 52 | 0.020565 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_261-703_0_5_line_11 |  | 9 | 10 | 0.017536 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_261-703_0_5_line_12 |  | 9 | 11 | 0.023223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-703_0_5_line_13 |  | 10 | 19 | 0.018004 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_261-703_0_5_line_14 |  | 10 | 20 | 0.033898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_261-703_0_5_line_15 |  | 10 | 18 | 0.013412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_261-703_0_5_line_16 |  | 12 | 13 | 0.051212 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_261-703_0_5_line_17 |  | 12 | 14 | 0.005587 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_261-703_0_5_line_18 |  | 12 | 15 | 0.017069 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_261-703_0_5_line_19 |  | 13 | 16 | 0.031941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_261-703_0_5_line_20 |  | 13 | 17 | 0.036719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_261-703_0_5_line_21 |  | 13 | 18 | 0.016969 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_261-703_0_5_line_22 |  | 14 | 55 | 0.010029 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_261-703_0_5_line_23 |  | 16 | 56 | 0.017716 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_261-703_0_5_line_24 |  | 17 | 21 | 0.068749 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_261-703_0_5_line_25 |  | 17 | 22 | 0.014035 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_261-703_0_5_line_26 |  | 19 | 61 | 0.040757 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_261-703_0_5_line_27 |  | 20 | 50 | 0.0075987 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_261-703_0_5_line_28 |  | 20 | 51 | 0.025489 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_261-703_0_5_line_29 |  | 21 | 23 | 0.003479 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_261-703_0_5_line_30 |  | 24 | 92 | 0.016362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
31 | LV_261-703_0_5_line_31 |  | 25 | 26 | 0.0040318 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_261-703_0_5_line_32 |  | 25 | 27 | 0.02561 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_261-703_0_5_line_33 |  | 25 | 28 | 0.012859 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
34 | LV_261-703_0_5_line_34 |  | 26 | 42 | 0.07366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_261-703_0_5_line_35 |  | 27 | 52 | 0.012067 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_261-703_0_5_line_36 |  | 28 | 88 | 0.019423 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_261-703_0_5_line_37 |  | 29 | 30 | 0.026532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
38 | LV_261-703_0_5_line_38 |  | 29 | 31 | 0.0077617 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_261-703_0_5_line_39 |  | 29 | 32 | 0.0098059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
40 | LV_261-703_0_5_line_40 |  | 30 | 40 | 0.010546 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_261-703_0_5_line_41 |  | 30 | 41 | 0.017575 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
42 | LV_261-703_0_5_line_42 |  | 31 | 89 | 0.012052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_261-703_0_5_line_43 |  | 32 | 34 | 0.009467 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
44 | LV_261-703_0_5_line_44 |  | 32 | 35 | 0.0083899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_261-703_0_5_line_45 |  | 33 | 62 | 0.01377 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_261-703_0_5_line_46 |  | 34 | 36 | 0.010498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
47 | LV_261-703_0_5_line_47 |  | 34 | 37 | 0.019014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_261-703_0_5_line_48 |  | 35 | 84 | 0.015618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_261-703_0_5_line_49 |  | 36 | 38 | 0.045707 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
50 | LV_261-703_0_5_line_50 |  | 36 | 39 | 0.061549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_261-703_0_5_line_51 |  | 38 | 43 | 0.017657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
52 | LV_261-703_0_5_line_52 |  | 40 | 90 | 0.0083375 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_261-703_0_5_line_53 |  | 41 | 91 | 0.019129 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
54 | LV_261-703_0_5_line_54 |  | 43 | 93 | 0.015855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
55 | LV_261-703_0_5_line_55 |  | 44 | 45 | 0.01526 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_261-703_0_5_line_56 |  | 44 | 46 | 0.0011357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_261-703_0_5_line_57 |  | 45 | 56 | 0.029423 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_261-703_0_5_line_58 |  | 46 | 67 | 0.007188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_261-703_0_5_line_59 |  | 47 | 48 | 0.001872 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_261-703_0_5_line_60 |  | 47 | 49 | 0.019251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_261-703_0_5_line_61 |  | 48 | 70 | 0.0097061 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_261-703_0_5_line_62 |  | 48 | 68 | 0.008186 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_261-703_0_5_line_63 |  | 50 | 66 | 0.014015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_261-703_0_5_line_64 |  | 53 | 54 | 0.0086503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_261-703_0_5_line_65 |  | 54 | 97 | 0.015235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_261-703_0_5_line_66 |  | 55 | 70 | 0.018193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_261-703_0_5_line_67 |  | 57 | 58 | 0.020534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_261-703_0_5_line_68 |  | 58 | 78 | 0.028512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_261-703_0_5_line_69 |  | 59 | 60 | 8.3209e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_261-703_0_5_line_70 |  | 60 | 65 | 0.030121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_261-703_0_5_line_71 |  | 61 | 116 | 0.048731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_261-703_0_5_line_72 |  | 61 | 115 | 0.032741 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_261-703_0_5_line_73 |  | 62 | 63 | 0.017697 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_261-703_0_5_line_74 |  | 63 | 64 | 0.018567 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_261-703_0_5_line_75 |  | 64 | 65 | 0.010974 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_261-703_0_5_line_76 |  | 66 | 73 | 0.014379 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_261-703_0_5_line_77 |  | 68 | 69 | 0.01908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_261-703_0_5_line_78 |  | 71 | 72 | 0.01739 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_261-703_0_5_line_79 |  | 72 | 73 | 0.015238 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_261-703_0_5_line_80 |  | 72 | 74 | 0.002704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
81 | LV_261-703_0_5_line_81 |  | 74 | 75 | 0.029985 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
82 | LV_261-703_0_5_line_82 |  | 75 | 76 | 0.020727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_261-703_0_5_line_83 |  | 75 | 77 | 0.007799 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
84 | LV_261-703_0_5_line_84 |  | 76 | 107 | 0.017271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_261-703_0_5_line_85 |  | 76 | 108 | 0.01395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_261-703_0_5_line_86 |  | 77 | 105 | 0.010186 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_261-703_0_5_line_87 |  | 77 | 102 | 0.016113 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
88 | LV_261-703_0_5_line_88 |  | 78 | 79 | 0.0024776 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_261-703_0_5_line_89 |  | 79 | 80 | 0.0013645 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_261-703_0_5_line_90 |  | 80 | 85 | 0.017811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_261-703_0_5_line_91 |  | 81 | 82 | 0.016765 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_261-703_0_5_line_92 |  | 82 | 83 | 0.0091366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_261-703_0_5_line_93 |  | 83 | 84 | 0.0093812 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_261-703_0_5_line_94 |  | 85 | 86 | 0.014162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_261-703_0_5_line_95 |  | 86 | 87 | 0.0037169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_261-703_0_5_line_96 |  | 87 | 88 | 0.012723 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_261-703_0_5_line_97 |  | 90 | 101 | 0.01739 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_261-703_0_5_line_98 |  | 91 | 92 | 0.0022004 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
99 | LV_261-703_0_5_line_99 |  | 93 | 104 | 0.015133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
100 | LV_261-703_0_5_line_100 |  | 94 | 95 | 0.0050689 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_261-703_0_5_line_101 |  | 94 | 96 | 0.0083982 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_261-703_0_5_line_102 |  | 95 | 97 | 0.00086598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_261-703_0_5_line_103 |  | 96 | 98 | 0.0008056 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_261-703_0_5_line_104 |  | 98 | 99 | 0.013554 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_261-703_0_5_line_105 |  | 99 | 100 | 0.0072682 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_261-703_0_5_line_106 |  | 100 | 101 | 0.00015326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_261-703_0_5_line_107 |  | 102 | 103 | 0.016152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
108 | LV_261-703_0_5_line_108 |  | 103 | 104 | 0.014829 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
109 | LV_261-703_0_5_line_109 |  | 105 | 106 | 0.020482 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_261-703_0_5_line_110 |  | 107 | 114 | 0.0073395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_261-703_0_5_line_111 |  | 107 | 112 | 0.015207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_261-703_0_5_line_112 |  | 109 | 110 | 0.015562 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_261-703_0_5_line_113 |  | 109 | 111 | 0.017779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_261-703_0_5_line_114 |  | 110 | 112 | 0.0001965 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_261-703_0_5_line_115 |  | 111 | 113 | 0.014275 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_261-703_0_5_line_116 |  | 114 | 117 | 0.014138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_261-703_0_5_line_117 |  | 117 | 118 | 0.001688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-703_0_5_trafo_69 | 0.63 MVA 20/0.4 kV | 119 | 28 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2682201.07 | 1249552.3159 | 2682214.498 | 1249546.6357
1 | 2682202.5567 | 1249555.639 | 2682201.07 | 1249552.3159
2 | 2682259.7199 | 1249527.3157 | 2682251.5276 | 1249530.8408
3 | 2682279.8322 | 1249518.6614 | 2682259.7199 | 1249527.3157
4 | 2682199.286 | 1249561.1644 | 2682197.3234 | 1249557.8569 | 2682199.7616 | 1249556.8233 | 2682202.5567 | 1249555.639
5 | 2682202.5567 | 1249555.639 | 2682204.102 | 1249559.0963 | 2682206.7941 | 1249563.7037 | 2682211.2265 | 1249570.2229
6 | 2682279.8322 | 1249518.6614 | 2682278.5717 | 1249515.9085 | 2682272.4835 | 1249504.1042 | 2682271.2202 | 1249501.2171
7 | 2682279.8322 | 1249518.6614 | 2682281.4226 | 1249522.1304 | 2682282.6464 | 1249524.805 | 2682282.9102 | 1249525.3868
8 | 2682199.286 | 1249561.1644 | 2682229.3628 | 1249548.2964
9 | 2682219.8899 | 1249582.965 | 2682211.2265 | 1249570.2229
10 | 2682229.3628 | 1249548.2964 | 2682248.2702 | 1249540.2071
11 | 2682383.8593 | 1249582.8535 | 2682387.1621 | 1249581.5429 | 2682383.7873 | 1249573.3677 | 2682388.4608 | 1249571.2311
12 | 2682383.8593 | 1249582.8535 | 2682371.4911 | 1249587.7408 | 2682361.6193 | 1249586.7183
13 | 2682388.4608 | 1249571.2311 | 2682396.6679 | 1249567.4757 | 2682402.4732 | 1249560.6263
14 | 2682372.8384 | 1249546.7737 | 2682383.7873 | 1249573.3677 | 2682388.4608 | 1249571.2311
15 | 2682388.4608 | 1249571.2311 | 2682391.7519 | 1249579.4496 | 2682393.5633 | 1249583.6338
16 | 2682404.957 | 1249594.7444 | 2682403.9165 | 1249598.4327 | 2682402.8522 | 1249602.2096 | 2682400.3976 | 1249604.9664 | 2682397.2094 | 1249606.7234 | 2682399.309 | 1249616.4598 | 2682400.4975 | 1249615.1531 | 2682419.3247 | 1249630.6707
17 | 2682419.3247 | 1249630.6707 | 2682423.1493 | 1249626.5876
18 | 2682419.3247 | 1249630.6707 | 2682416.556 | 1249633.7568 | 2682420.1278 | 1249636.9866 | 2682416.5723 | 1249641.2625 | 2682416.5716 | 1249643.8088
19 | 2682404.957 | 1249594.7444 | 2682407.8868 | 1249594.7407 | 2682411.2121 | 1249593.4415 | 2682414.1708 | 1249591.3589 | 2682416.5876 | 1249588.6016 | 2682428.383 | 1249574.799
20 | 2682386.4433 | 1249622.3742 | 2682389.886 | 1249617.5185 | 2682393.4094 | 1249616.6335 | 2682393.7379 | 1249613.1021 | 2682393.6178 | 1249608.7083 | 2682397.2094 | 1249606.7234 | 2682400.3976 | 1249604.9664 | 2682402.8522 | 1249602.2096 | 2682403.9165 | 1249598.4327 | 2682404.957 | 1249594.7444
21 | 2682404.957 | 1249594.7444 | 2682401.1882 | 1249593.7246 | 2682398.1184 | 1249591.8583 | 2682395.8634 | 1249588.9471 | 2682393.5633 | 1249583.6338
22 | 2682423.1493 | 1249626.5876 | 2682429.6328 | 1249618.9364
23 | 2682439.8922 | 1249561.3312 | 2682428.383 | 1249574.799
24 | 2682346.1363 | 1249651.2356 | 2682350.393 | 1249662.2362 | 2682357.6171 | 1249659.6569 | 2682367.346 | 1249655.6001 | 2682372.948 | 1249649.6736 | 2682379.8223 | 1249632.612 | 2682383.1312 | 1249627.6099 | 2682386.4433 | 1249622.3742
25 | 2682386.4433 | 1249622.3742 | 2682372.613 | 1249619.9852
26 | 2682428.4904 | 1249529.2564 | 2682415.837 | 1249544.8587 | 2682402.4732 | 1249560.6263
27 | 2682372.8384 | 1249546.7737 | 2682369.7995 | 1249539.8091
28 | 2682372.8384 | 1249546.7737 | 2682359.6861 | 1249553.7405 | 2682349.1847 | 1249552.2573
29 | 2682346.1363 | 1249651.2356 | 2682349.3491 | 1249649.8792
30 | 2682264.6612 | 1249486.2278 | 2682271.2202 | 1249501.2171
31 | 2682282.9102 | 1249525.3868 | 2682282.6464 | 1249524.805 | 2682285.6656 | 1249523.2568
32 | 2682282.9102 | 1249525.3868 | 2682259.3647 | 1249535.4605
33 | 2682282.9102 | 1249525.3868 | 2682284.7643 | 1249529.4378 | 2682288.1464 | 1249537.1309
34 | 2682285.6656 | 1249523.2568 | 2682297.4801 | 1249548.9954 | 2682312.2476 | 1249589.3525 | 2682313.0254 | 1249591.586
35 | 2682248.2702 | 1249540.2071 | 2682259.3647 | 1249535.4605
36 | 2682295.4836 | 1249555.1034 | 2682292.8451 | 1249547.8191 | 2682288.1464 | 1249537.1309
37 | 2682234.0275 | 1249431.6949 | 2682238.6768 | 1249431.3035 | 2682248.2732 | 1249450.9511
38 | 2682234.0275 | 1249431.6949 | 2682227.2958 | 1249435.5586
39 | 2682229.6793 | 1249422.9058 | 2682232.4856 | 1249428.5378 | 2682234.0275 | 1249431.6949
40 | 2682248.2732 | 1249450.9511 | 2682239.1778 | 1249456.2886
41 | 2682248.2732 | 1249450.9511 | 2682255.9141 | 1249466.7779
42 | 2682216.8431 | 1249441.5582 | 2682227.2958 | 1249435.5586
43 | 2682237.0489 | 1249416.937 | 2682229.6793 | 1249422.9058
44 | 2682229.6793 | 1249422.9058 | 2682222.4024 | 1249427.0817
45 | 2682219.8899 | 1249582.965 | 2682227.6323 | 1249594.3525
46 | 2682237.0489 | 1249416.937 | 2682246.6824 | 1249412.7008
47 | 2682237.0489 | 1249416.937 | 2682230.2837 | 1249399.167
48 | 2682222.4024 | 1249427.0817 | 2682208.856 | 1249434.8555
49 | 2682246.6824 | 1249412.7008 | 2682249.9621 | 1249419.0399 | 2682252.3694 | 1249423.4988 | 2682281.8506 | 1249407.585
50 | 2682246.6824 | 1249412.7008 | 2682263.7663 | 1249403.2086 | 2682285.4548 | 1249390.5669 | 2682299.3268 | 1249380.9117
51 | 2682281.8506 | 1249407.585 | 2682289.2108 | 1249423.6343
52 | 2682231.9871 | 1249460.5083 | 2682239.1778 | 1249456.2886
53 | 2682255.9141 | 1249466.7779 | 2682258.4389 | 1249472.0078 | 2682263.7792 | 1249484.2119
54 | 2682295.8198 | 1249438.0459 | 2682289.2108 | 1249423.6343
55 | 2682468.9216 | 1249527.3617 | 2682459.0076 | 1249538.9629
56 | 2682468.9216 | 1249527.3617 | 2682469.6609 | 1249526.4997
57 | 2682459.0076 | 1249538.9629 | 2682439.8922 | 1249561.3312
58 | 2682474.3405 | 1249521.0436 | 2682469.6609 | 1249526.4997
59 | 2682447.6692 | 1249597.6515 | 2682448.8821 | 1249596.2229
60 | 2682448.8821 | 1249596.2229 | 2682461.3252 | 1249581.5331
61 | 2682447.6692 | 1249597.6515 | 2682441.3943 | 1249605.0565
62 | 2682447.6692 | 1249597.6515 | 2682454.0612 | 1249602.7887
63 | 2682364.1358 | 1249526.9914 | 2682364.5987 | 1249527.8897 | 2682369.7995 | 1249539.8091
64 | 2682166.02 | 1249500.8082 | 2682172.9881 | 1249495.6824
65 | 2682172.9881 | 1249495.6824 | 2682180.3733 | 1249490.2497 | 2682185.6361 | 1249487.2317
66 | 2682441.3943 | 1249605.0565 | 2682429.6328 | 1249618.9364
67 | 2682322.553 | 1249631.1992 | 2682326.0859 | 1249641.1386 | 2682329.5028 | 1249650.5208
68 | 2682322.553 | 1249631.1992 | 2682316.9663 | 1249615.4818 | 2682313.0459 | 1249604.3192
69 | 2682271.1748 | 1249658.3944 | 2682271.128 | 1249658.3256
70 | 2682254.1919 | 1249633.4172 | 2682261.5075 | 1249644.1777 | 2682271.128 | 1249658.3256
71 | 2682428.4904 | 1249529.2564 | 2682460.0292 | 1249492.1074
72 | 2682428.4904 | 1249529.2564 | 2682408.4421 | 1249512.4764 | 2682403.304 | 1249508.3387
73 | 2682237.5828 | 1249608.9876 | 2682227.6323 | 1249594.3525
74 | 2682237.5828 | 1249608.9876 | 2682241.5507 | 1249614.8236 | 2682248.0218 | 1249624.3418
75 | 2682248.0218 | 1249624.3418 | 2682254.1919 | 1249633.4172
76 | 2682364.1358 | 1249526.9914 | 2682357.5496 | 1249514.209
77 | 2682454.0612 | 1249602.7887 | 2682441.7306 | 1249617.3496
78 | 2682350.57 | 1249500.6635 | 2682334.5292 | 1249507.379
79 | 2682350.57 | 1249500.6635 | 2682357.5496 | 1249514.209
80 | 2682350.57 | 1249500.6635 | 2682349.3273 | 1249498.2621
81 | 2682342.3263 | 1249471.1939 | 2682339.649 | 1249475.849 | 2682340.6356 | 1249481.4669 | 2682349.3273 | 1249498.2621
82 | 2682342.3263 | 1249471.1939 | 2682357.5415 | 1249457.0726
83 | 2682342.3263 | 1249471.1939 | 2682336.1097 | 1249466.4596
84 | 2682370.8564 | 1249446.0271 | 2682357.5415 | 1249457.0726
85 | 2682357.5415 | 1249457.0726 | 2682366.1678 | 1249468.035
86 | 2682336.1097 | 1249466.4596 | 2682333.6708 | 1249464.8245 | 2682329.7079 | 1249464.725 | 2682326.949 | 1249466.5547
87 | 2682336.1097 | 1249466.4596 | 2682340.9754 | 1249462.4464 | 2682333.5607 | 1249456.0291
88 | 2682312.2249 | 1249601.9815 | 2682313.0459 | 1249604.3192
89 | 2682312.2249 | 1249601.9815 | 2682311.7728 | 1249600.6941
90 | 2682305.8469 | 1249583.8974 | 2682308.4898 | 1249591.3463 | 2682311.7728 | 1249600.6941
91 | 2682192.8216 | 1249444.1176 | 2682181.8962 | 1249450.686 | 2682178.6001 | 1249452.9831
92 | 2682200.7194 | 1249439.5248 | 2682195.0388 | 1249442.7846 | 2682192.8216 | 1249444.1176
93 | 2682200.7194 | 1249439.5248 | 2682208.856 | 1249434.8555
94 | 2682305.8469 | 1249583.8974 | 2682302.6695 | 1249574.9422 | 2682301.0826 | 1249570.561
95 | 2682301.0826 | 1249570.561 | 2682299.8167 | 1249567.0662
96 | 2682299.8167 | 1249567.0662 | 2682295.4836 | 1249555.1034
97 | 2682216.9641 | 1249469.2664 | 2682221.2852 | 1249466.7885 | 2682231.9871 | 1249460.5083
98 | 2682263.7792 | 1249484.2119 | 2682264.6612 | 1249486.2278
99 | 2682295.8198 | 1249438.0459 | 2682310.6749 | 1249435.1611 | 2682310.6749 | 1249435.1611
100 | 2682190.7845 | 1249484.2793 | 2682186.3873 | 1249486.801
101 | 2682190.7845 | 1249484.2793 | 2682198.0698 | 1249480.1015
102 | 2682185.6361 | 1249487.2317 | 2682186.3873 | 1249486.801
103 | 2682198.0698 | 1249480.1015 | 2682198.7687 | 1249479.7008
104 | 2682210.5262 | 1249472.9583 | 2682198.7687 | 1249479.7008
105 | 2682210.5262 | 1249472.9583 | 2682216.8312 | 1249469.3427
106 | 2682216.8312 | 1249469.3427 | 2682216.9641 | 1249469.2664
107 | 2682333.5607 | 1249456.0291 | 2682322.5387 | 1249446.4897 | 2682321.3999 | 1249445.4022
108 | 2682310.6749 | 1249435.1611 | 2682321.3999 | 1249445.4022
109 | 2682326.949 | 1249466.5547 | 2682318.2305 | 1249472.3268 | 2682313.6974 | 1249472.5084 | 2682309.825 | 1249468.6184
110 | 2682370.8564 | 1249446.0271 | 2682376.5894 | 1249441.4444
111 | 2682370.8564 | 1249446.0271 | 2682359.679 | 1249435.7157
112 | 2682348.0962 | 1249425.0302 | 2682359.5346 | 1249435.5824
113 | 2682348.0962 | 1249425.0302 | 2682345.1577 | 1249422.3193 | 2682336.4624 | 1249411.6278
114 | 2682359.679 | 1249435.7157 | 2682359.5346 | 1249435.5824
115 | 2682325.7438 | 1249402.297 | 2682334.3555 | 1249409.0372 | 2682336.4624 | 1249411.6278
116 | 2682387.6324 | 1249432.617 | 2682376.5894 | 1249441.4444
117 | 2682387.6324 | 1249432.617 | 2682388.9364 | 1249431.5452

## bus_geodata
| x | y | coords
0 | 2682214.498 | 1249546.6357
1 | 2682201.07 | 1249552.3159
2 | 2682251.5276 | 1249530.8408
3 | 2682259.7199 | 1249527.3157
4 | 2682202.5567 | 1249555.639
5 | 2682279.8322 | 1249518.6614
6 | 2682199.286 | 1249561.1644
7 | 2682211.2265 | 1249570.2229
8 | 2682229.3628 | 1249548.2964
9 | 2682383.8593 | 1249582.8535
10 | 2682388.4608 | 1249571.2311
11 | 2682361.6194 | 1249586.7183
12 | 2682419.3247 | 1249630.6707
13 | 2682404.957 | 1249594.7444
14 | 2682423.1493 | 1249626.5876
15 | 2682416.5716 | 1249643.8088
16 | 2682428.383 | 1249574.799
17 | 2682386.4433 | 1249622.3742
18 | 2682393.5633 | 1249583.6338
19 | 2682402.4732 | 1249560.6263
20 | 2682372.8384 | 1249546.7737
21 | 2682346.1363 | 1249651.2356
22 | 2682372.613 | 1249619.9852
23 | 2682349.3491 | 1249649.8792
24 | 2682271.2202 | 1249501.2171
25 | 2682282.9102 | 1249525.3868
26 | 2682285.6656 | 1249523.2568
27 | 2682259.3647 | 1249535.4605
28 | 2682288.1464 | 1249537.1309
29 | 2682234.0275 | 1249431.6949
30 | 2682248.2732 | 1249450.9511
31 | 2682227.2958 | 1249435.5586
32 | 2682229.6793 | 1249422.9058
33 | 2682219.8899 | 1249582.965
34 | 2682237.0489 | 1249416.937
35 | 2682222.4024 | 1249427.0817
36 | 2682246.6824 | 1249412.7008
37 | 2682230.2837 | 1249399.167
38 | 2682281.8506 | 1249407.585
39 | 2682299.3268 | 1249380.9117
40 | 2682239.1778 | 1249456.2886
41 | 2682255.9141 | 1249466.7779
42 | 2682313.0254 | 1249591.586
43 | 2682289.2108 | 1249423.6343
44 | 2682468.9216 | 1249527.3617
45 | 2682459.0076 | 1249538.9629
46 | 2682469.6609 | 1249526.4997
47 | 2682448.8821 | 1249596.2229
48 | 2682447.6692 | 1249597.6515
49 | 2682461.3252 | 1249581.5331
50 | 2682369.7995 | 1249539.8091
51 | 2682349.1847 | 1249552.2573
52 | 2682248.2702 | 1249540.2071
53 | 2682166.02 | 1249500.8082
54 | 2682172.9881 | 1249495.6824
55 | 2682429.6328 | 1249618.9364
56 | 2682439.8922 | 1249561.3312
57 | 2682329.5028 | 1249650.5208
58 | 2682322.553 | 1249631.1992
59 | 2682271.1748 | 1249658.3944
60 | 2682271.128 | 1249658.3256
61 | 2682428.4904 | 1249529.2564
62 | 2682227.6323 | 1249594.3525
63 | 2682237.5828 | 1249608.9876
64 | 2682248.0218 | 1249624.3418
65 | 2682254.1919 | 1249633.4172
66 | 2682364.1358 | 1249526.9914
67 | 2682474.3405 | 1249521.0436
68 | 2682454.0612 | 1249602.7887
69 | 2682441.7306 | 1249617.3496
70 | 2682441.3943 | 1249605.0565
71 | 2682334.5292 | 1249507.379
72 | 2682350.57 | 1249500.6635
73 | 2682357.5496 | 1249514.2091
74 | 2682349.3273 | 1249498.2621
75 | 2682342.3263 | 1249471.1939
76 | 2682357.5415 | 1249457.0726
77 | 2682336.1097 | 1249466.4596
78 | 2682313.0459 | 1249604.3192
79 | 2682312.2249 | 1249601.9815
80 | 2682311.7728 | 1249600.6941
81 | 2682178.6001 | 1249452.9831
82 | 2682192.8216 | 1249444.1176
83 | 2682200.7194 | 1249439.5248
84 | 2682208.856 | 1249434.8555
85 | 2682305.8469 | 1249583.8974
86 | 2682301.0826 | 1249570.561
87 | 2682299.8167 | 1249567.0662
88 | 2682295.4836 | 1249555.1034
89 | 2682216.8431 | 1249441.5582
90 | 2682231.9871 | 1249460.5083
91 | 2682263.7792 | 1249484.2119
92 | 2682264.6612 | 1249486.2278
93 | 2682295.8198 | 1249438.0459
94 | 2682190.7845 | 1249484.2793
95 | 2682186.3873 | 1249486.801
96 | 2682198.0698 | 1249480.1015
97 | 2682185.6361 | 1249487.2317
98 | 2682198.7687 | 1249479.7008
99 | 2682210.5262 | 1249472.9583
100 | 2682216.8312 | 1249469.3427
101 | 2682216.9641 | 1249469.2664
102 | 2682333.5607 | 1249456.0291
103 | 2682321.3999 | 1249445.4022
104 | 2682310.6749 | 1249435.1611
105 | 2682326.949 | 1249466.5547
106 | 2682309.825 | 1249468.6184
107 | 2682370.8564 | 1249446.0271
108 | 2682366.1678 | 1249468.035
109 | 2682348.0962 | 1249425.0302
110 | 2682359.5346 | 1249435.5824
111 | 2682336.4624 | 1249411.6278
112 | 2682359.679 | 1249435.7157
113 | 2682325.7438 | 1249402.297
114 | 2682376.5894 | 1249441.4444
115 | 2682403.304 | 1249508.3387
116 | 2682460.0292 | 1249492.1074
117 | 2682387.6324 | 1249432.617
118 | 2682388.9364 | 1249431.5452
119 | 2682282.9102 | 1249525.3868

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98599 | -0.26896 | 0.050747 | 0.012719
1 | 0.98667 | -0.25571 | 0 | 0
2 | 0.99744 | -0.048645 | 0.0047748 | 0.0011967
3 | 0.99748 | -0.047899 | 0.017086 | 0.0042823
4 | 0.98684 | -0.2524 | 0 | 0
5 | 0.99792 | -0.039517 | 0 | 0
6 | 0.98787 | -0.23243 | 0 | 0
7 | 0.9858 | -0.27266 | 0.01019 | 0.0025539
8 | 0.9914 | -0.16417 | 0.0073751 | 0.0018484
9 | 0.97495 | -0.4824 | 0 | 0
10 | 0.975 | -0.48145 | 0 | 0
11 | 0.97489 | -0.48366 | 0.0029605 | 0.00074198
12 | 0.97114 | -0.55764 | 0 | 0
13 | 0.97288 | -0.52313 | 0 | 0
14 | 0.971 | -0.56037 | 0 | 0
15 | 0.97097 | -0.56084 | 0.010137 | 0.0025405
16 | 0.97228 | -0.53497 | 0.0040577 | 0.0010169
17 | 0.97233 | -0.53402 | 0 | 0
18 | 0.97403 | -0.50043 | 0.0043855 | 0.0010991
19 | 0.9748 | -0.48548 | 0.0024383 | 0.00061109
20 | 0.97792 | -0.42426 | 0 | 0
21 | 0.97208 | -0.53898 | 0 | 0
22 | 0.97217 | -0.53717 | 0.012182 | 0.0030532
23 | 0.97207 | -0.53923 | 0.0039084 | 0.00097953
24 | 0.99645 | -0.067345 | 0.012064 | 0.0030236
25 | 0.99851 | -0.028256 | 0 | 0
26 | 0.99845 | -0.029396 | 0 | 0
27 | 0.99523 | -0.090777 | 0.0072823 | 0.0018251
28 | 1 | 0 | -0.60302 | -0.15341
29 | 0.99126 | -0.16652 | 0 | 0
30 | 0.99263 | -0.14027 | 0 | 0
31 | 0.99117 | -0.16829 | 0.0076127 | 0.0019079
32 | 0.99078 | -0.17567 | 0 | 0
33 | 0.985 | -0.28824 | 0.0074522 | 0.0018677
34 | 0.99037 | -0.18349 | 0 | 0
35 | 0.99059 | -0.17931 | 0.0043697 | 0.0010951
36 | 0.98996 | -0.19145 | 0 | 0
37 | 0.9901 | -0.1887 | 0.0154 | 0.0038595
38 | 0.98817 | -0.22566 | 0 | 0
39 | 0.98981 | -0.19432 | 0.0026134 | 0.00065497
40 | 0.99201 | -0.15225 | 0.0044259 | 0.0011092
41 | 0.9938 | -0.11795 | 0.0092202 | 0.0023108
42 | 0.99737 | -0.050247 | 0.016172 | 0.004053
43 | 0.98749 | -0.23891 | 0.0051703 | 0.0012958
44 | 0.97159 | -0.54869 | 0 | 0
45 | 0.97169 | -0.54661 | 0.0043849 | 0.001099
46 | 0.97158 | -0.54884 | 0.0033488 | 0.00083929
47 | 0.97038 | -0.57265 | 0 | 0
48 | 0.97039 | -0.57249 | 0 | 0
49 | 0.97029 | -0.57433 | 0.0047044 | 0.001179
50 | 0.97859 | -0.41108 | 0.0025274 | 0.00063344
51 | 0.97785 | -0.42564 | 0.002962 | 0.00074235
52 | 0.99376 | -0.11883 | 0.0072852 | 0.0018258
53 | 0.98953 | -0.20029 | 0.0028196 | 0.00070667
54 | 0.98956 | -0.19985 | 0.0028217 | 0.0007072
55 | 0.97075 | -0.56526 | 0.0091873 | 0.0023025
56 | 0.97202 | -0.54021 | 0.0042759 | 0.0010716
57 | 0.99521 | -0.09224 | 0.0091412 | 0.002291
58 | 0.99538 | -0.088938 | 0.012257 | 0.0030719
59 | 0.98235 | -0.34003 | 0.0089725 | 0.0022487
60 | 0.98235 | -0.34002 | 0.011573 | 0.0029004
61 | 0.97443 | -0.49278 | 0 | 0
62 | 0.98438 | -0.30033 | 0.0079985 | 0.0020046
63 | 0.98371 | -0.31334 | 0.00987 | 0.0024736
64 | 0.98318 | -0.32371 | 0.0050347 | 0.0012618
65 | 0.98292 | -0.32884 | 0.0054018 | 0.0013538
66 | 0.97987 | -0.38617 | 0.0015004 | 0.00037603
67 | 0.97155 | -0.54938 | 0.00404 | 0.0010125
68 | 0.97036 | -0.57299 | 0 | 0
69 | 0.9703 | -0.57415 | 0.0032919 | 0.00082502
70 | 0.97046 | -0.57105 | 0.0092053 | 0.0023071
71 | 0.98252 | -0.33477 | 0.0077591 | 0.0019446
72 | 0.98265 | -0.33233 | 0 | 0
73 | 0.9812 | -0.36029 | 0.002218 | 0.00055589
74 | 0.98278 | -0.32966 | 0.0049289 | 0.0012353
75 | 0.98438 | -0.29882 | 0 | 0
76 | 0.98377 | -0.31081 | 0 | 0
77 | 0.98465 | -0.29369 | 0 | 0
78 | 0.99593 | -0.07821 | 0.0054051 | 0.0013546
79 | 0.99599 | -0.077043 | 0.0055556 | 0.0013924
80 | 0.99603 | -0.076268 | 0.0045267 | 0.0011345
81 | 0.99 | -0.19076 | 0.0059088 | 0.0014809
82 | 0.9901 | -0.18899 | 0.0041414 | 0.0010379
83 | 0.99018 | -0.18736 | 0.0048777 | 0.0012225
84 | 0.99031 | -0.18487 | 0.0051159 | 0.0012822
85 | 0.99663 | -0.064732 | 0.0089055 | 0.0022319
86 | 0.99722 | -0.053359 | 0.026104 | 0.0065422
87 | 0.99747 | -0.048676 | 0.0082792 | 0.002075
88 | 0.99839 | -0.030822 | 0.010723 | 0.0026874
89 | 0.99111 | -0.16943 | 0.0053015 | 0.0013287
90 | 0.99155 | -0.16108 | 0.0040604 | 0.0010176
91 | 0.99511 | -0.092931 | 0.012606 | 0.0031594
92 | 0.99527 | -0.089935 | 0.004843 | 0.0012138
93 | 0.98689 | -0.25045 | 0 | 0
94 | 0.9897 | -0.19706 | 0.013941 | 0.0034939
95 | 0.98964 | -0.1982 | 0.0044568 | 0.001117
96 | 0.9899 | -0.1931 | 0.0063595 | 0.0015938
97 | 0.98963 | -0.19832 | 0.0024885 | 0.00062368
98 | 0.98993 | -0.19263 | 0.0027051 | 0.00067796
99 | 0.99037 | -0.18405 | 0.0081908 | 0.0020528
100 | 0.99066 | -0.1784 | 0.0047172 | 0.0011822
101 | 0.99067 | -0.17827 | 0.0071996 | 0.0018044
102 | 0.9852 | -0.283 | 0.0045754 | 0.0011467
103 | 0.98577 | -0.27196 | 0.0052197 | 0.0013082
104 | 0.98631 | -0.26149 | 0.0052894 | 0.0013257
105 | 0.98463 | -0.29395 | 0 | 0
106 | 0.98461 | -0.29447 | 0.0014142 | 0.00035442
107 | 0.98331 | -0.31979 | 0 | 0
108 | 0.98372 | -0.31165 | 0.0033169 | 0.00083128
109 | 0.98284 | -0.32881 | 0.005219 | 0.001308
110 | 0.98303 | -0.32524 | 0.0023847 | 0.00059765
111 | 0.98272 | -0.33122 | 0.0052939 | 0.0013268
112 | 0.98303 | -0.32518 | 0.0045611 | 0.0011431
113 | 0.98269 | -0.33179 | 0.002216 | 0.00055539
114 | 0.98324 | -0.321 | 0.0045085 | 0.0011299
115 | 0.97422 | -0.4969 | 0.0068515 | 0.0017171
116 | 0.97429 | -0.49538 | 0.0029094 | 0.00072917
117 | 0.98318 | -0.32218 | 0 | 0
118 | 0.98318 | -0.32232 | 0.0046456 | 0.0011643
119 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.050747 | -0.012719 | 0.05078 | 0.012739 | 3.2069e-05 | 2.0338e-05 | 0.076586 | 0.076586 | 0.076586 | 0.98599 | -0.26896 | 0.98667 | -0.25571 | 21.0401
1 | -0.05078 | -0.012739 | 0.050788 | 0.012744 | 8.0041e-06 | 5.0761e-06 | 0.076586 | 0.076586 | 0.076586 | 0.98667 | -0.25571 | 0.98684 | -0.2524 | 21.0401
2 | -0.0047748 | -0.0011967 | 0.004775 | 0.0011967 | 1.697e-07 | -7.804e-09 | 0.0071233 | 0.0071232 | 0.0071233 | 0.99744 | -0.048645 | 0.99748 | -0.047899 | 1.9569
3 | -0.021861 | -0.005479 | 0.02187 | 0.0054843 | 8.7327e-06 | 5.303e-06 | 0.032612 | 0.032612 | 0.032612 | 0.99748 | -0.047899 | 0.99792 | -0.039517 | 8.9595
4 | -0.11747 | -0.02953 | 0.11758 | 0.029602 | 0.00011217 | 7.1665e-05 | 0.17716 | 0.17716 | 0.17716 | 0.98684 | -0.2524 | 0.98787 | -0.23243 | 48.6714
5 | 0.066685 | 0.016786 | -0.066621 | -0.016745 | 6.4514e-05 | 4.1072e-05 | 0.10058 | 0.10058 | 0.10058 | 0.98684 | -0.2524 | 0.9858 | -0.27266 | 27.6313
6 | 0.33045 | 0.084431 | -0.33001 | -0.084148 | 0.00044401 | 0.00028315 | 0.49332 | 0.49332 | 0.49332 | 0.99792 | -0.039517 | 0.99645 | -0.067345 | 33.8818
7 | -0.35232 | -0.089915 | 0.35252 | 0.090037 | 0.0001918 | 0.00012236 | 0.52593 | 0.52593 | 0.52593 | 0.99792 | -0.039517 | 0.99851 | -0.028256 | 36.1216
8 | -0.11758 | -0.029602 | 0.11797 | 0.029848 | 0.00038505 | 0.00024601 | 0.17716 | 0.17716 | 0.17716 | 0.98787 | -0.23243 | 0.9914 | -0.16417 | 48.6714
9 | 0.05643 | 0.014191 | -0.056389 | -0.014165 | 4.194e-05 | 2.6645e-05 | 0.085196 | 0.085197 | 0.085197 | 0.9858 | -0.27266 | 0.985 | -0.28824 | 23.4056
10 | -0.12534 | -0.031696 | 0.12562 | 0.031871 | 0.00027325 | 0.00017461 | 0.18823 | 0.18823 | 0.18823 | 0.9914 | -0.16417 | 0.99376 | -0.11883 | 51.7124
11 | -0.0029607 | -0.00074181 | 0.0029609 | 0.00074167 | 1.3427e-07 | -1.3276e-07 | 0.0045187 | 0.0045186 | 0.0045187 | 0.97495 | -0.4824 | 0.975 | -0.48145 | 1.2414
12 | 0.0029607 | 0.00074181 | -0.0029605 | -0.00074198 | 1.7783e-07 | -1.7577e-07 | 0.0045187 | 0.0045188 | 0.0045188 | 0.97495 | -0.4824 | 0.97489 | -0.48366 | 1.2414
13 | 0.012207 | 0.0030604 | -0.012204 | -0.0030591 | 2.3433e-06 | 1.2752e-06 | 0.01863 | 0.01863 | 0.01863 | 0.975 | -0.48145 | 0.9748 | -0.48548 | 5.1181
14 | -0.092534 | -0.023287 | 0.092788 | 0.023449 | 0.00025365 | 0.00016191 | 0.14126 | 0.14126 | 0.14126 | 0.975 | -0.48145 | 0.97792 | -0.42426 | 38.8069
15 | 0.077366 | 0.019485 | -0.077296 | -0.01944 | 7.0162e-05 | 4.4737e-05 | 0.11811 | 0.11811 | 0.11811 | 0.975 | -0.48145 | 0.97403 | -0.50043 | 32.4475
16 | -0.036543 | -0.0091638 | 0.036603 | 0.0092017 | 6.0213e-05 | 3.7902e-05 | 0.055994 | 0.055994 | 0.055994 | 0.97114 | -0.55764 | 0.97288 | -0.52313 | 15.3831
17 | 0.026404 | 0.0066225 | -0.026401 | -0.0066204 | 3.4297e-06 | 2.1259e-06 | 0.04046 | 0.04046 | 0.04046 | 0.97114 | -0.55764 | 0.971 | -0.56037 | 11.1153
18 | 0.010138 | 0.0025413 | -0.010137 | -0.0025405 | 1.5447e-06 | 7.7745e-07 | 0.015535 | 0.015535 | 0.015535 | 0.97114 | -0.55764 | 0.97097 | -0.56084 | 4.2678
19 | 0.020127 | 0.0050508 | -0.020116 | -0.0050439 | 1.1353e-05 | 6.8693e-06 | 0.030787 | 0.030787 | 0.030787 | 0.97288 | -0.52313 | 0.97228 | -0.53497 | 8.4579
20 | 0.016102 | 0.0040383 | -0.016093 | -0.0040334 | 8.3521e-06 | 4.8897e-06 | 0.024629 | 0.024629 | 0.024629 | 0.97288 | -0.52313 | 0.97233 | -0.53402 | 6.7661
21 | -0.072832 | -0.018291 | 0.072911 | 0.018341 | 7.8983e-05 | 5.0338e-05 | 0.11141 | 0.11141 | 0.11141 | 0.97288 | -0.52313 | 0.97403 | -0.50043 | 30.6069
22 | 0.026401 | 0.0066204 | -0.026395 | -0.0066165 | 6.1564e-06 | 3.8161e-06 | 0.04046 | 0.04046 | 0.04046 | 0.971 | -0.56037 | 0.97075 | -0.56526 | 11.1153
23 | 0.016058 | 0.004027 | -0.016054 | -0.0040246 | 4.0127e-06 | 2.3485e-06 | 0.024577 | 0.024577 | 0.024577 | 0.97228 | -0.53497 | 0.97202 | -0.54021 | 6.7519
24 | 0.0039093 | 0.00097925 | -0.0039084 | -0.00097952 | 9.2276e-07 | -2.6194e-07 | 0.0059825 | 0.0059828 | 0.0059828 | 0.97233 | -0.53402 | 0.97208 | -0.53898 | 1.6436
25 | 0.012184 | 0.0030542 | -0.012182 | -0.0030532 | 1.8299e-06 | 9.9708e-07 | 0.018646 | 0.018646 | 0.018646 | 0.97233 | -0.53402 | 0.97217 | -0.53717 | 5.1226
26 | 0.009766 | 0.002448 | -0.0097626 | -0.0024464 | 3.3968e-06 | 1.6661e-06 | 0.014908 | 0.014908 | 0.014908 | 0.9748 | -0.48548 | 0.97443 | -0.49278 | 4.0956
27 | -0.09575 | -0.024191 | 0.09581 | 0.02423 | 6.0544e-05 | 3.8653e-05 | 0.14576 | 0.14576 | 0.14576 | 0.97792 | -0.42426 | 0.97859 | -0.41108 | 40.0451
28 | 0.0029622 | 0.00074216 | -0.002962 | -0.00074235 | 1.9419e-07 | -1.9549e-07 | 0.0045073 | 0.0045074 | 0.0045074 | 0.97792 | -0.42426 | 0.97785 | -0.42564 | 1.2383
29 | 0.0039084 | 0.00097952 | -0.0039084 | -0.00097953 | 4.6698e-08 | -1.3242e-08 | 0.0059828 | 0.0059828 | 0.0059828 | 0.97208 | -0.53898 | 0.97207 | -0.53923 | 1.6436
30 | 0.31795 | 0.081124 | -0.3176 | -0.080903 | 0.00034653 | 0.00022093 | 0.4753 | 0.4753 | 0.4753 | 0.99645 | -0.067345 | 0.99527 | -0.089935 | 32.6445
31 | 0.016189 | 0.0040628 | -0.016188 | -0.0040623 | 8.8011e-07 | 5.1054e-07 | 0.024127 | 0.024127 | 0.024127 | 0.99851 | -0.028256 | 0.99845 | -0.029396 | 6.6283
32 | 0.14079 | 0.035907 | -0.14037 | -0.035637 | 0.00042364 | 0.0002708 | 0.21003 | 0.21003 | 0.21003 | 0.99851 | -0.028256 | 0.99523 | -0.090777 | 57.7004
33 | -0.50949 | -0.13001 | 0.51019 | 0.13045 | 0.00069647 | 0.00044506 | 0.76009 | 0.76009 | 0.76009 | 0.99851 | -0.028256 | 1 | 0 | 52.2038
34 | 0.016188 | 0.0040623 | -0.016172 | -0.004053 | 1.6079e-05 | 9.3285e-06 | 0.024127 | 0.024127 | 0.024127 | 0.99845 | -0.029396 | 0.99737 | -0.050247 | 6.6284
35 | 0.13308 | 0.033811 | -0.1329 | -0.033697 | 0.00017946 | 0.0001147 | 0.19914 | 0.19914 | 0.19914 | 0.99523 | -0.090777 | 0.99376 | -0.11883 | 54.7092
36 | 0.091176 | 0.022958 | -0.091041 | -0.022872 | 0.00013414 | 8.5595e-05 | 0.13571 | 0.13571 | 0.13571 | 1 | 0 | 0.99839 | -0.030822 | 37.2825
37 | -0.2256 | -0.057403 | 0.22588 | 0.057585 | 0.00028578 | 0.00018153 | 0.33896 | 0.33896 | 0.33896 | 0.99126 | -0.16652 | 0.99263 | -0.14027 | 23.2802
38 | 0.012916 | 0.0032372 | -0.012914 | -0.0032366 | 1.0941e-06 | 6.0018e-07 | 0.019388 | 0.019388 | 0.019388 | 0.99126 | -0.16652 | 0.99117 | -0.16829 | 5.3264
39 | 0.21268 | 0.054166 | -0.21259 | -0.054107 | 9.3885e-05 | 5.9581e-05 | 0.31957 | 0.31957 | 0.31957 | 0.99126 | -0.16652 | 0.99078 | -0.17567 | 21.9486
40 | 0.064327 | 0.016176 | -0.06429 | -0.016152 | 3.6788e-05 | 2.3408e-05 | 0.09645 | 0.09645 | 0.09645 | 0.99263 | -0.14027 | 0.99201 | -0.15225 | 26.4971
41 | -0.29021 | -0.073761 | 0.29052 | 0.07396 | 0.00031236 | 0.000199 | 0.43541 | 0.43541 | 0.43541 | 0.99263 | -0.14027 | 0.9938 | -0.11795 | 29.9044
42 | 0.0053018 | 0.0013287 | -0.0053015 | -0.0013287 | 2.8633e-07 | 2.7923e-08 | 0.0079594 | 0.0079595 | 0.0079595 | 0.99117 | -0.16829 | 0.99111 | -0.16943 | 2.1867
43 | 0.18816 | 0.047981 | -0.18809 | -0.047936 | 7.1024e-05 | 4.4968e-05 | 0.28289 | 0.28289 | 0.28289 | 0.99078 | -0.17567 | 0.99037 | -0.18349 | 19.429
44 | 0.024426 | 0.0061259 | -0.024422 | -0.0061233 | 4.2344e-06 | 2.602e-06 | 0.036686 | 0.036686 | 0.036686 | 0.99078 | -0.17567 | 0.99059 | -0.17931 | 10.0786
45 | 0.048936 | 0.012297 | -0.048908 | -0.012279 | 2.823e-05 | 1.7892e-05 | 0.073939 | 0.073939 | 0.073939 | 0.985 | -0.28824 | 0.98438 | -0.30033 | 20.3128
46 | 0.17269 | 0.044074 | -0.17262 | -0.044032 | 6.6399e-05 | 4.1956e-05 | 0.25974 | 0.25974 | 0.25974 | 0.99037 | -0.18349 | 0.98996 | -0.19145 | 17.8395
47 | 0.015403 | 0.0038617 | -0.0154 | -0.0038595 | 3.8193e-06 | 2.1997e-06 | 0.023144 | 0.023144 | 0.023144 | 0.99037 | -0.18349 | 0.9901 | -0.1887 | 6.3582
48 | 0.020052 | 0.0050282 | -0.020047 | -0.005025 | 5.3143e-06 | 3.2001e-06 | 0.030122 | 0.030122 | 0.030122 | 0.99059 | -0.17931 | 0.99031 | -0.18487 | 8.2754
49 | 0.17001 | 0.043378 | -0.16973 | -0.0432 | 0.00028042 | 0.00017712 | 0.25581 | 0.25582 | 0.25582 | 0.98996 | -0.19145 | 0.98817 | -0.22566 | 17.5697
50 | 0.0026137 | 0.0006544 | -0.0026134 | -0.00065497 | 3.5623e-07 | -5.6324e-07 | 0.0039285 | 0.0039287 | 0.0039287 | 0.98996 | -0.19145 | 0.98981 | -0.19432 | 1.0793
51 | 0.16973 | 0.0432 | -0.16962 | -0.043132 | 0.00010833 | 6.8424e-05 | 0.25582 | 0.25582 | 0.25582 | 0.98817 | -0.22566 | 0.98749 | -0.23891 | 17.5697
52 | 0.059864 | 0.015043 | -0.059839 | -0.015027 | 2.5219e-05 | 1.6032e-05 | 0.089811 | 0.089811 | 0.089811 | 0.99201 | -0.15225 | 0.99155 | -0.16108 | 24.6733
53 | -0.29974 | -0.07627 | 0.3001 | 0.076501 | 0.00036188 | 0.00023061 | 0.44921 | 0.44921 | 0.44921 | 0.9938 | -0.11795 | 0.99511 | -0.092931 | 30.8526
54 | 0.16445 | 0.041836 | -0.16436 | -0.041779 | 9.1436e-05 | 5.7708e-05 | 0.24802 | 0.24802 | 0.24802 | 0.98749 | -0.23891 | 0.98689 | -0.25045 | 17.0347
55 | -0.0073889 | -0.0018518 | 0.0073896 | 0.0018521 | 7.3282e-07 | 2.7999e-07 | 0.011316 | 0.011316 | 0.011316 | 0.97159 | -0.54869 | 0.97169 | -0.54661 | 3.1089
56 | 0.0073889 | 0.0018518 | -0.0073888 | -0.0018518 | 5.4537e-08 | 2.0839e-08 | 0.011316 | 0.011316 | 0.011316 | 0.97159 | -0.54869 | 0.97158 | -0.54884 | 3.1089
57 | -0.011775 | -0.002951 | 0.011778 | 0.002953 | 3.5873e-06 | 1.9313e-06 | 0.018031 | 0.018031 | 0.018031 | 0.97169 | -0.54661 | 0.97202 | -0.54021 | 4.9536
58 | 0.0040401 | 0.0010125 | -0.00404 | -0.0010125 | 1.032e-07 | -2.2969e-08 | 0.0061875 | 0.0061875 | 0.0061875 | 0.97158 | -0.54884 | 0.97155 | -0.54938 | 1.6999
59 | -0.0047048 | -0.001179 | 0.0047048 | 0.001179 | 3.6538e-08 | 2.5833e-10 | 0.0072145 | 0.0072145 | 0.0072145 | 0.97038 | -0.57265 | 0.97039 | -0.57249 | 1.982
60 | 0.0047048 | 0.001179 | -0.0047044 | -0.001179 | 3.7576e-07 | 2.6824e-09 | 0.0072145 | 0.0072146 | 0.0072146 | 0.97038 | -0.57265 | 0.97029 | -0.57433 | 1.982
61 | -0.0079969 | -0.0020039 | 0.0079975 | 0.0020041 | 5.4732e-07 | 2.3037e-07 | 0.012263 | 0.012263 | 0.012263 | 0.97039 | -0.57249 | 0.97046 | -0.57105 | 3.3689
62 | 0.0032921 | 0.00082485 | -0.0032921 | -0.0008249 | 7.823e-08 | -5.1058e-08 | 0.0050482 | 0.0050482 | 0.0050482 | 0.97039 | -0.57249 | 0.97036 | -0.57299 | 1.3869
63 | -0.098338 | -0.024863 | 0.098455 | 0.024938 | 0.00011763 | 7.511e-05 | 0.14961 | 0.14961 | 0.14961 | 0.97859 | -0.41108 | 0.97987 | -0.38617 | 41.1009
64 | -0.0028196 | -0.00070667 | 0.0028197 | 0.0007066 | 5.8318e-08 | -7.3801e-08 | 0.0042401 | 0.00424 | 0.0042401 | 0.98953 | -0.20029 | 0.98956 | -0.19985 | 1.1649
65 | -0.0056415 | -0.0014138 | 0.0056419 | 0.0014139 | 4.1113e-07 | 6.7391e-08 | 0.0084831 | 0.0084831 | 0.0084831 | 0.98956 | -0.19985 | 0.98963 | -0.19832 | 2.3305
66 | 0.017208 | 0.004314 | -0.017203 | -0.0043112 | 4.7467e-06 | 2.813e-06 | 0.026377 | 0.026377 | 0.026377 | 0.97075 | -0.56526 | 0.97046 | -0.57105 | 7.2465
67 | -0.0091412 | -0.002291 | 0.0091426 | 0.0022916 | 1.4384e-06 | 6.5373e-07 | 0.013668 | 0.013668 | 0.013668 | 0.99521 | -0.09224 | 0.99538 | -0.088938 | 3.7549
68 | -0.0214 | -0.0053635 | 0.02141 | 0.0053702 | 1.0942e-05 | 6.6322e-06 | 0.031991 | 0.031991 | 0.031991 | 0.99538 | -0.088938 | 0.99593 | -0.07821 | 8.7887
69 | -0.0089725 | -0.0022487 | 0.0089725 | 0.0022487 | 5.7648e-09 | 2.6364e-09 | 0.013591 | 0.013591 | 0.013591 | 0.98235 | -0.34003 | 0.98235 | -0.34002 | 3.7338
70 | -0.020545 | -0.0051491 | 0.020556 | 0.0051557 | 1.0939e-05 | 6.6197e-06 | 0.031121 | 0.031121 | 0.031121 | 0.98235 | -0.34002 | 0.98292 | -0.32884 | 8.5497
71 | 0.0029098 | 0.00072879 | -0.0029094 | -0.00072917 | 3.608e-07 | -3.7604e-07 | 0.0044433 | 0.0044435 | 0.0044435 | 0.97443 | -0.49278 | 0.97429 | -0.49538 | 1.2207
72 | 0.0068528 | 0.0017176 | -0.0068515 | -0.0017171 | 1.3446e-06 | 4.5277e-07 | 0.010465 | 0.010465 | 0.010465 | 0.97443 | -0.49278 | 0.97422 | -0.4969 | 2.875
73 | 0.04091 | 0.010275 | -0.040884 | -0.010258 | 2.5386e-05 | 1.6022e-05 | 0.061848 | 0.061848 | 0.061848 | 0.98438 | -0.30033 | 0.98371 | -0.31334 | 16.9912
74 | 0.031014 | 0.0077848 | -0.030999 | -0.0077753 | 1.5327e-05 | 9.5734e-06 | 0.046918 | 0.046918 | 0.046918 | 0.98371 | -0.31334 | 0.98318 | -0.32371 | 12.8896
75 | 0.025964 | 0.0065134 | -0.025958 | -0.0065095 | 6.3555e-06 | 3.9284e-06 | 0.039298 | 0.039298 | 0.039298 | 0.98318 | -0.32371 | 0.98292 | -0.32884 | 10.7962
76 | -0.099956 | -0.025314 | 0.10008 | 0.025394 | 0.0001244 | 7.9432e-05 | 0.15189 | 0.15189 | 0.15189 | 0.97987 | -0.38617 | 0.9812 | -0.36029 | 41.7268
77 | 0.0032921 | 0.0008249 | -0.0032919 | -0.00082502 | 1.8235e-07 | -1.1899e-07 | 0.0050482 | 0.0050483 | 0.0050483 | 0.97036 | -0.57299 | 0.9703 | -0.57415 | 1.3869
78 | -0.0077591 | -0.0019446 | 0.00776 | 0.001945 | 9.0049e-07 | 3.5605e-07 | 0.011751 | 0.011751 | 0.011751 | 0.98252 | -0.33477 | 0.98265 | -0.33233 | 3.2283
79 | 0.10244 | 0.026038 | -0.1023 | -0.02595 | 0.00013773 | 8.7952e-05 | 0.15525 | 0.15525 | 0.15525 | 0.98265 | -0.33233 | 0.9812 | -0.36029 | 42.6509
80 | -0.1102 | -0.027983 | 0.11021 | 0.027992 | 1.414e-05 | 8.9808e-06 | 0.167 | 0.167 | 0.167 | 0.98265 | -0.33233 | 0.98278 | -0.32966 | 22.9396
81 | -0.11514 | -0.029227 | 0.11531 | 0.029336 | 0.00017112 | 0.00010876 | 0.17446 | 0.17446 | 0.17446 | 0.98278 | -0.32966 | 0.98438 | -0.29882 | 23.9647
82 | 0.032185 | 0.0080802 | -0.032167 | -0.0080687 | 1.8402e-05 | 1.1514e-05 | 0.048657 | 0.048657 | 0.048657 | 0.98438 | -0.29882 | 0.98377 | -0.31081 | 13.3674
83 | -0.1475 | -0.037416 | 0.14753 | 0.037439 | 3.6399e-05 | 2.2898e-05 | 0.22312 | 0.22312 | 0.22312 | 0.98438 | -0.29882 | 0.98465 | -0.29369 | 15.3242
84 | 0.02885 | 0.0072375 | -0.028838 | -0.0072298 | 1.2335e-05 | 7.675e-06 | 0.04364 | 0.04364 | 0.04364 | 0.98377 | -0.31081 | 0.98331 | -0.31979 | 11.9891
85 | 0.003317 | 0.00083119 | -0.0033169 | -0.00083128 | 1.3168e-07 | -9.2833e-08 | 0.0050172 | 0.0050172 | 0.0050172 | 0.98377 | -0.31081 | 0.98372 | -0.31165 | 1.3784
86 | 0.0014142 | 0.00035407 | -0.0014142 | -0.00035419 | 1.7445e-08 | -1.1839e-07 | 0.0021371 | 0.0021371 | 0.0021371 | 0.98465 | -0.29369 | 0.98463 | -0.29395 | 0.58712
87 | -0.14895 | -0.037793 | 0.14902 | 0.037841 | 7.665e-05 | 4.8236e-05 | 0.22526 | 0.22526 | 0.22526 | 0.98465 | -0.29369 | 0.9852 | -0.283 | 15.4709
88 | -0.026816 | -0.0067248 | 0.026817 | 0.0067257 | 1.4915e-06 | 9.2233e-07 | 0.040066 | 0.040066 | 0.040066 | 0.99593 | -0.07821 | 0.99599 | -0.077043 | 11.0072
89 | -0.032373 | -0.0081181 | 0.032374 | 0.0081188 | 1.197e-06 | 7.4832e-07 | 0.048366 | 0.048366 | 0.048366 | 0.99599 | -0.077043 | 0.99603 | -0.076268 | 13.2875
90 | -0.036901 | -0.0092533 | 0.036921 | 0.0092661 | 2.03e-05 | 1.276e-05 | 0.055129 | 0.055129 | 0.055129 | 0.99603 | -0.076268 | 0.99663 | -0.064732 | 15.1454
91 | -0.0059088 | -0.0014809 | 0.0059093 | 0.001481 | 4.9588e-07 | 1.0177e-07 | 0.0088812 | 0.0088811 | 0.0088812 | 0.99 | -0.19076 | 0.9901 | -0.18899 | 2.4399
92 | -0.010051 | -0.0025189 | 0.010052 | 0.0025193 | 7.8175e-07 | 3.8281e-07 | 0.015105 | 0.015105 | 0.015105 | 0.9901 | -0.18899 | 0.99018 | -0.18736 | 4.1498
93 | -0.014929 | -0.0037418 | 0.014931 | 0.0037428 | 1.7707e-06 | 1.0126e-06 | 0.022435 | 0.022435 | 0.022435 | 0.99018 | -0.18736 | 0.99031 | -0.18487 | 6.1635
94 | -0.045826 | -0.011498 | 0.045851 | 0.011514 | 2.4865e-05 | 1.5729e-05 | 0.068425 | 0.068425 | 0.068425 | 0.99663 | -0.064732 | 0.99722 | -0.053359 | 18.7982
95 | -0.071955 | -0.018056 | 0.071971 | 0.018066 | 1.6071e-05 | 1.0237e-05 | 0.10738 | 0.10738 | 0.10738 | 0.99722 | -0.053359 | 0.99747 | -0.048676 | 29.499
96 | -0.08025 | -0.020141 | 0.080319 | 0.020185 | 6.8394e-05 | 4.3606e-05 | 0.11973 | 0.11973 | 0.11973 | 0.99747 | -0.048676 | 0.99839 | -0.030822 | 32.8921
97 | 0.055779 | 0.014009 | -0.055733 | -0.01398 | 4.5704e-05 | 2.9026e-05 | 0.083717 | 0.083717 | 0.083717 | 0.99155 | -0.16108 | 0.99067 | -0.17827 | 22.9993
98 | -0.31271 | -0.07966 | 0.31276 | 0.079689 | 4.5193e-05 | 2.8809e-05 | 0.46806 | 0.46806 | 0.46806 | 0.99511 | -0.092931 | 0.99527 | -0.089935 | 32.1472
99 | 0.16436 | 0.041779 | -0.16427 | -0.041723 | 8.7273e-05 | 5.5081e-05 | 0.24802 | 0.24803 | 0.24803 | 0.98689 | -0.25045 | 0.98631 | -0.26149 | 17.0347
100 | 0.012588 | 0.0031549 | -0.012587 | -0.0031545 | 6.8086e-07 | 3.7062e-07 | 0.018926 | 0.018926 | 0.018926 | 0.9897 | -0.19706 | 0.98964 | -0.1982 | 5.1994
101 | -0.026528 | -0.0066487 | 0.026533 | 0.0066518 | 5.0102e-06 | 3.0986e-06 | 0.039886 | 0.039886 | 0.039886 | 0.9897 | -0.19706 | 0.9899 | -0.1931 | 10.9576
102 | 0.0081304 | 0.0020376 | -0.0081304 | -0.0020375 | 4.8531e-08 | 1.9933e-08 | 0.012225 | 0.012225 | 0.012225 | 0.98964 | -0.1982 | 0.98963 | -0.19832 | 3.3585
103 | -0.032893 | -0.0082457 | 0.032894 | 0.0082461 | 7.3858e-07 | 4.6234e-07 | 0.049445 | 0.049445 | 0.049445 | 0.9899 | -0.1931 | 0.98993 | -0.19263 | 13.5838
104 | -0.035599 | -0.0089241 | 0.035613 | 0.0089332 | 1.4554e-05 | 9.1401e-06 | 0.053511 | 0.053511 | 0.053511 | 0.98993 | -0.19263 | 0.99037 | -0.18405 | 14.7009
105 | -0.043804 | -0.010986 | 0.043816 | 0.010994 | 1.1807e-05 | 7.463e-06 | 0.065818 | 0.065818 | 0.065818 | 0.99037 | -0.18405 | 0.99066 | -0.1784 | 18.0819
106 | -0.048533 | -0.012176 | 0.048533 | 0.012176 | 3.0546e-07 | 1.9352e-07 | 0.072903 | 0.072903 | 0.072903 | 0.99066 | -0.1784 | 0.99067 | -0.17827 | 20.0284
107 | -0.1536 | -0.038988 | 0.15368 | 0.039039 | 8.1618e-05 | 5.1412e-05 | 0.23217 | 0.23217 | 0.23217 | 0.9852 | -0.283 | 0.98577 | -0.27196 | 15.9455
108 | -0.1589 | -0.040347 | 0.15898 | 0.040398 | 8.0108e-05 | 5.0513e-05 | 0.24005 | 0.24005 | 0.24005 | 0.98577 | -0.27196 | 0.98631 | -0.26149 | 16.4866
109 | 0.0014142 | 0.00035419 | -0.0014142 | -0.00035442 | 3.5081e-08 | -2.3805e-07 | 0.0021371 | 0.0021372 | 0.0021372 | 0.98463 | -0.29395 | 0.98461 | -0.29447 | 0.58715
110 | 0.0091549 | 0.0022945 | -0.0091544 | -0.0022942 | 5.2826e-07 | 2.4499e-07 | 0.013854 | 0.013854 | 0.013854 | 0.98331 | -0.31979 | 0.98324 | -0.321 | 3.806
111 | 0.019683 | 0.0049354 | -0.019678 | -0.0049323 | 5.0597e-06 | 3.0453e-06 | 0.029786 | 0.029787 | 0.029787 | 0.98331 | -0.31979 | 0.98303 | -0.32518 | 8.1831
112 | -0.01273 | -0.0031904 | 0.012732 | 0.0031915 | 2.1677e-06 | 1.1901e-06 | 0.019273 | 0.019273 | 0.019273 | 0.98284 | -0.32881 | 0.98303 | -0.32524 | 5.2947
113 | 0.0075108 | 0.0018823 | -0.00751 | -0.001882 | 8.6211e-07 | 3.2646e-07 | 0.011371 | 0.011371 | 0.011371 | 0.98284 | -0.32881 | 0.98272 | -0.33122 | 3.124
114 | -0.015117 | -0.0037892 | 0.015117 | 0.0037892 | 3.8583e-08 | 2.2202e-08 | 0.022882 | 0.022882 | 0.022882 | 0.98303 | -0.32524 | 0.98303 | -0.32518 | 6.2864
115 | 0.0022161 | 0.00055525 | -0.002216 | -0.00055539 | 6.0275e-08 | -1.4228e-07 | 0.0033555 | 0.0033556 | 0.0033556 | 0.98272 | -0.33122 | 0.98269 | -0.33179 | 0.92186
116 | 0.0046459 | 0.0011643 | -0.0046456 | -0.0011643 | 2.6208e-07 | -1.1571e-08 | 0.0070309 | 0.0070309 | 0.0070309 | 0.98324 | -0.321 | 0.98318 | -0.32218 | 1.9316
117 | 0.0046456 | 0.0011643 | -0.0046456 | -0.0011643 | 3.1291e-08 | -1.3799e-09 | 0.0070309 | 0.0070309 | 0.0070309 | 0.98318 | -0.32218 | 0.98318 | -0.32232 | 1.9316

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.61179 | 0.15561

## res_load
| p_mw | q_mvar
0 | 0.050747 | 0.012719
1 | 0.0047748 | 0.0011967
2 | 0.017086 | 0.0042823
3 | 0.01019 | 0.0025539
4 | 0.0073751 | 0.0018484
5 | 0.0029605 | 0.00074198
6 | 0.010137 | 0.0025405
7 | 0.0040577 | 0.0010169
8 | 0.0043855 | 0.0010991
9 | 0.0024383 | 0.00061109
10 | 0.012182 | 0.0030532
11 | 0.0039084 | 0.00097953
12 | 0.012064 | 0.0030236
13 | 0.0072823 | 0.0018251
14 | 0.0087788 | 0.0022002
15 | 0.0076127 | 0.0019079
16 | 0.0074522 | 0.0018677
17 | 0.0043697 | 0.0010951
18 | 0.0154 | 0.0038595
19 | 0.0026134 | 0.00065497
20 | 0.0044259 | 0.0011092
21 | 0.0092202 | 0.0023108
22 | 0.016172 | 0.004053
23 | 0.0051703 | 0.0012958
24 | 0.0043849 | 0.001099
25 | 0.0033488 | 0.00083929
26 | 0.0047044 | 0.001179
27 | 0.0025274 | 0.00063344
28 | 0.002962 | 0.00074235
29 | 0.0072852 | 0.0018258
30 | 0.0028196 | 0.00070667
31 | 0.0028217 | 0.0007072
32 | 0.0091873 | 0.0023025
33 | 0.0042759 | 0.0010716
34 | 0.0091412 | 0.002291
35 | 0.012257 | 0.0030719
36 | 0.0089725 | 0.0022487
37 | 0.011573 | 0.0029004
38 | 0.0079985 | 0.0020046
39 | 0.00987 | 0.0024736
40 | 0.0050347 | 0.0012618
41 | 0.0054018 | 0.0013538
42 | 0.0015004 | 0.00037603
43 | 0.00404 | 0.0010125
44 | 0.0032919 | 0.00082502
45 | 0.0092053 | 0.0023071
46 | 0.0077591 | 0.0019446
47 | 0.002218 | 0.00055589
48 | 0.0049289 | 0.0012353
49 | 0.0054051 | 0.0013546
50 | 0.0055556 | 0.0013924
51 | 0.0045267 | 0.0011345
52 | 0.0059088 | 0.0014809
53 | 0.0041414 | 0.0010379
54 | 0.0048777 | 0.0012225
55 | 0.0051159 | 0.0012822
56 | 0.0089055 | 0.0022319
57 | 0.026104 | 0.0065422
58 | 0.0082792 | 0.002075
59 | 0.010723 | 0.0026874
60 | 0.0053015 | 0.0013287
61 | 0.0040604 | 0.0010176
62 | 0.012606 | 0.0031594
63 | 0.004843 | 0.0012138
64 | 0.013941 | 0.0034939
65 | 0.0044568 | 0.001117
66 | 0.0063595 | 0.0015938
67 | 0.0024885 | 0.00062368
68 | 0.0027051 | 0.00067796
69 | 0.0081908 | 0.0020528
70 | 0.0047172 | 0.0011822
71 | 0.0071996 | 0.0018044
72 | 0.0045754 | 0.0011467
73 | 0.0052197 | 0.0013082
74 | 0.0052894 | 0.0013257
75 | 0.0014142 | 0.00035442
76 | 0.0033169 | 0.00083128
77 | 0.005219 | 0.001308
78 | 0.0023847 | 0.00059765
79 | 0.0052939 | 0.0013268
80 | 0.0045611 | 0.0011431
81 | 0.002216 | 0.00055539
82 | 0.0045085 | 0.0011299
83 | 0.0068515 | 0.0017171
84 | 0.0029094 | 0.00072917
85 | 0.0046456 | 0.0011643

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1