## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-709_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-709_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-709_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_261-709_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_261-709_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_261-709_0_3_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_261-709_0_3_node_52 | 0.4 | n |  | TRUE
7 | bus_LV_261-709_0_3_node_11 | 0.4 | n |  | TRUE
8 | bus_LV_261-709_0_3_node_38 | 0.4 | n |  | TRUE
9 | bus_LV_261-709_0_3_node_6 | 0.4 | n |  | TRUE
10 | bus_LV_261-709_0_3_node_47 | 0.4 | n |  | TRUE
11 | bus_LV_261-709_0_3_node_22 | 0.4 | n |  | TRUE
12 | bus_LV_261-709_0_3_node_50 | 0.4 | n |  | TRUE
13 | bus_LV_261-709_0_3_node_7 | 0.4 | n |  | TRUE
14 | bus_LV_261-709_0_3_node_48 | 0.4 | n |  | TRUE
15 | bus_LV_261-709_0_3_node_8 | 0.4 | n |  | TRUE
16 | bus_LV_261-709_0_3_node_21 | 0.4 | n |  | TRUE
17 | bus_LV_261-709_0_3_node_39 | 0.4 | n |  | TRUE
18 | bus_LV_261-709_0_3_node_34 | 0.4 | n |  | TRUE
19 | bus_LV_261-709_0_3_node_12 | 0.4 | n |  | TRUE
20 | bus_LV_261-709_0_3_node_13 | 0.4 | n |  | TRUE
21 | bus_LV_261-709_0_3_node_16 | 0.4 | n |  | TRUE
22 | bus_LV_261-709_0_3_node_28 | 0.4 | n |  | TRUE
23 | bus_LV_261-709_0_3_node_18 | 0.4 | n |  | TRUE
24 | bus_LV_261-709_0_3_node_14 | 0.4 | n |  | TRUE
25 | bus_LV_261-709_0_3_node_36 | 0.4 | n |  | TRUE
26 | bus_LV_261-709_0_3_node_35 | 0.4 | n |  | TRUE
27 | bus_LV_261-709_0_3_node_27 | 0.4 | n |  | TRUE
28 | bus_LV_261-709_0_3_node_44 | 0.4 | n |  | TRUE
29 | bus_LV_261-709_0_3_node_23 | 0.4 | n |  | TRUE
30 | bus_LV_261-709_0_3_node_49 | 0.4 | n |  | TRUE
31 | bus_LV_261-709_0_3_node_24 | 0.4 | n |  | TRUE
32 | bus_LV_261-709_0_3_node_54 | 0.4 | n |  | TRUE
33 | bus_LV_261-709_0_3_node_53 | 0.4 | n |  | TRUE
34 | bus_LV_261-709_0_3_node_37 | 0.4 | n |  | TRUE
35 | bus_LV_261-709_0_3_node_43 | 0.4 | n |  | TRUE
36 | bus_LV_261-709_0_3_node_33 | 0.4 | n |  | TRUE
37 | bus_LV_261-709_0_3_node_40 | 0.4 | n |  | TRUE
38 | bus_LV_261-709_0_3_node_42 | 0.4 | n |  | TRUE
39 | bus_LV_261-709_0_3_node_41 | 0.4 | n |  | TRUE
40 | bus_LV_261-709_0_3_node_30 | 0.4 | n |  | TRUE
41 | bus_LV_261-709_0_3_node_29 | 0.4 | n |  | TRUE
42 | bus_LV_261-709_0_3_node_45 | 0.4 | n |  | TRUE
43 | bus_LV_261-709_0_3_node_51 | 0.4 | n |  | TRUE
44 | bus_LV_261-709_0_3_node_46 | 0.4 | n |  | TRUE
45 | bus_LV_261-709_0_3_node_31 | 0.4 | n |  | TRUE
46 | bus_LV_261-709_0_3_node_32 | 0.4 | n |  | TRUE
47 | bus_MV_548_0_node_42 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-709_0_3_load_0 | 0 | 0.01222 | 0.0030625 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-709_0_3_load_1 | 1 | 0.018675 | 0.0046804 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-709_0_3_load_3 | 3 | 0.012986 | 0.0032546 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-709_0_3_load_52 | 6 | 0.018191 | 0.0045592 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-709_0_3_load_38 | 8 | 0.0022523 | 0.00056449 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-709_0_3_load_47 | 10 | 0.012882 | 0.0032286 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-709_0_3_load_50 | 12 | 0.0068741 | 0.0017228 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-709_0_3_load_48 | 14 | 0.0035746 | 0.00089587 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-709_0_3_load_39 | 17 | 0.011733 | 0.0029405 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-709_0_3_load_34 | 18 | 0.0048049 | 0.0012042 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-709_0_3_load_28 | 22 | 0.010087 | 0.002528 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-709_0_3_load_36 | 25 | 0.0054838 | 0.0013744 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-709_0_3_load_35 | 26 | 0.0073203 | 0.0018346 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-709_0_3_load_27 | 27 | 0.0082917 | 0.0020781 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-709_0_3_load_44 | 28 | 0.0087542 | 0.002194 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-709_0_3_load_49 | 30 | 0.0072025 | 0.0018051 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-709_0_3_load_24 | 31 | 0.019834 | 0.004971 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_261-709_0_3_load_54 | 32 | 0.017448 | 0.0043728 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_261-709_0_3_load_53 | 33 | 0.015841 | 0.00397 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_261-709_0_3_load_37 | 34 | 0.010599 | 0.0026564 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_261-709_0_3_load_43 | 35 | 0.015311 | 0.0038373 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_261-709_0_3_load_33 | 36 | 0.0065507 | 0.0016418 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_261-709_0_3_load_40 | 37 | 0.0086344 | 0.002164 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_261-709_0_3_load_42 | 38 | 0.012834 | 0.0032165 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_261-709_0_3_load_41 | 39 | 0.016696 | 0.0041845 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_261-709_0_3_load_30 | 40 | 0.0031287 | 0.00078412 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_261-709_0_3_load_29 | 41 | 0.0091334 | 0.0022891 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_261-709_0_3_load_45 | 42 | 0.0056299 | 0.001411 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_261-709_0_3_load_51 | 43 | 0.017194 | 0.0043093 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_261-709_0_3_load_46 | 44 | 0.015166 | 0.003801 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_261-709_0_3_load_31 | 45 | 0.0037599 | 0.00094231 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_261-709_0_3_load_32 | 46 | 0.004915 | 0.0012318 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 0 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-709_0_3_line_0 |  | 0 | 1 | 0.024599 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-709_0_3_line_1 |  | 0 | 2 | 0.020763 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
2 | LV_261-709_0_3_line_2 |  | 1 | 3 | 0.00086304 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-709_0_3_line_3 |  | 2 | 4 | 0.003829 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-709_0_3_line_4 |  | 2 | 5 | 0.0082547 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_261-709_0_3_line_5 |  | 3 | 6 | 0.0089489 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_261-709_0_3_line_6 |  | 4 | 7 | 0.009201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_261-709_0_3_line_7 |  | 4 | 8 | 0.0055385 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_261-709_0_3_line_8 |  | 5 | 9 | 0.004359 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_261-709_0_3_line_9 |  | 5 | 10 | 0.034695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_261-709_0_3_line_10 |  | 6 | 33 | 0.00093934 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_261-709_0_3_line_11 |  | 7 | 18 | 0.0047686 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_261-709_0_3_line_12 |  | 7 | 13 | 0.008582 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-709_0_3_line_13 |  | 8 | 34 | 0.022317 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_261-709_0_3_line_14 |  | 9 | 11 | 0.022783 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_261-709_0_3_line_15 |  | 9 | 12 | 0.007136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_261-709_0_3_line_16 |  | 10 | 35 | 0.030504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_261-709_0_3_line_17 |  | 11 | 31 | 0.015133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_261-709_0_3_line_18 |  | 12 | 30 | 0.014472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_261-709_0_3_line_19 |  | 13 | 14 | 0.015271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_261-709_0_3_line_20 |  | 14 | 36 | 0.0086296 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_261-709_0_3_line_21 |  | 15 | 16 | 0.011193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_261-709_0_3_line_22 |  | 15 | 17 | 0.0070909 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_261-709_0_3_line_23 |  | 16 | 29 | 0.044643 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_261-709_0_3_line_24 |  | 16 | 30 | 0.030112 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_261-709_0_3_line_25 |  | 17 | 37 | 0.024045 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_261-709_0_3_line_26 |  | 18 | 40 | 0.0089307 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_261-709_0_3_line_27 |  | 19 | 20 | 0.0091496 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_261-709_0_3_line_28 |  | 19 | 21 | 0.007136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_261-709_0_3_line_29 |  | 19 | 22 | 0.0086941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_261-709_0_3_line_30 |  | 20 | 23 | 0.00396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_261-709_0_3_line_31 |  | 21 | 27 | 0.019891 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_261-709_0_3_line_32 |  | 22 | 41 | 0.018398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_261-709_0_3_line_33 |  | 23 | 28 | 0.01325 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_261-709_0_3_line_34 |  | 23 | 24 | 0.007111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_261-709_0_3_line_35 |  | 24 | 25 | 0.03557 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_261-709_0_3_line_36 |  | 24 | 26 | 0.017184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_261-709_0_3_line_37 |  | 28 | 42 | 0.02256 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_261-709_0_3_line_38 |  | 29 | 32 | 0.024544 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_261-709_0_3_line_39 |  | 36 | 46 | 0.0084622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_261-709_0_3_line_40 |  | 37 | 39 | 0.024165 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_261-709_0_3_line_41 |  | 38 | 39 | 0.022728 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_261-709_0_3_line_42 |  | 40 | 41 | 0.017099 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_261-709_0_3_line_43 |  | 42 | 44 | 0.0091326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_261-709_0_3_line_44 |  | 43 | 44 | 0.0078331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_261-709_0_3_line_45 |  | 45 | 46 | 0.0007805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-709_0_3_trafo_0 | 0.63 MVA 20/0.4 kV | 47 | 0 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2684463.8045 | 1246776.9597 | 2684448.2685 | 1246796.0316
1 | 2684476.9181 | 1246760.8615 | 2684463.8045 | 1246776.9597
2 | 2684448.2685 | 1246796.0316 | 2684447.7234 | 1246796.7008
3 | 2684480.0982 | 1246763.0083 | 2684476.9181 | 1246760.8615
4 | 2684470.0869 | 1246756.2274 | 2684473.6707 | 1246758.6691 | 2684476.9181 | 1246760.8615
5 | 2684442.0715 | 1246803.639 | 2684447.7234 | 1246796.7008
6 | 2684480.0982 | 1246763.0083 | 2684480.691 | 1246762.2273 | 2684482.701 | 1246759.5429 | 2684483.0244 | 1246759.1138 | 2684483.7021 | 1246758.2117 | 2684485.5119 | 1246755.7912 | 2684485.6197 | 1246755.6482
7 | 2684480.0982 | 1246763.0083 | 2684484.6892 | 1246766.1063
8 | 2684466.4808 | 1246753.7631 | 2684470.0869 | 1246756.2274
9 | 2684470.0869 | 1246756.2274 | 2684448.1468 | 1246783.1043
10 | 2684442.0715 | 1246803.639 | 2684441.4782 | 1246804.3673
11 | 2684485.6197 | 1246755.6482 | 2684489.5705 | 1246758.3186
12 | 2684485.6197 | 1246755.6482 | 2684484.5398 | 1246754.0316 | 2684484.1552 | 1246752.9254 | 2684484.0342 | 1246751.3447 | 2684484.0723 | 1246750.2555 | 2684483.6308 | 1246749.9601 | 2684481.7374 | 1246748.71
13 | 2684484.6892 | 1246766.1063 | 2684503.1883 | 1246778.5895
14 | 2684466.4808 | 1246753.7631 | 2684467.1041 | 1246752.9603 | 2684469.4742 | 1246749.9252 | 2684472.106 | 1246746.549 | 2684472.6753 | 1246745.8233 | 2684462.0936 | 1246738.7785
15 | 2684466.4808 | 1246753.7631 | 2684460.5863 | 1246749.7409
16 | 2684428.8567 | 1246806.7348 | 2684448.1468 | 1246783.1043
17 | 2684462.0936 | 1246738.7785 | 2684463.3476 | 1246736.6615 | 2684464.9308 | 1246724.0883
18 | 2684448.6326 | 1246741.5839 | 2684460.5863 | 1246749.7409
19 | 2684481.7374 | 1246748.71 | 2684490.4804 | 1246736.1899
20 | 2684490.4804 | 1246736.1899 | 2684495.4212 | 1246729.1147
21 | 2684423.7598 | 1246724.6112 | 2684421.0295 | 1246723.238 | 2684419.0053 | 1246723.2092 | 2684416.907 | 1246723.6129 | 2684415.1419 | 1246724.4884 | 2684413.6937 | 1246725.9133
22 | 2684413.6937 | 1246725.9133 | 2684409.618 | 1246731.7158
23 | 2684423.7598 | 1246724.6112 | 2684425.9953 | 1246721.474 | 2684429.2484 | 1246716.9059 | 2684425.7357 | 1246714.2428 | 2684424.9193 | 1246712.6856 | 2684424.7351 | 1246711.3042 | 2684425.7415 | 1246709.595 | 2684422.1087 | 1246706.8746 | 2684425.7222 | 1246701.9335 | 2684434.5297 | 1246689.8166
24 | 2684423.7598 | 1246724.6112 | 2684448.6326 | 1246741.5839
25 | 2684409.618 | 1246731.7158 | 2684395.7971 | 1246751.3918
26 | 2684489.5705 | 1246758.3186 | 2684496.9696 | 1246763.3198
27 | 2684528.2255 | 1246795.4846 | 2684531.0462 | 1246791.5775 | 2684533.5817 | 1246788.0666
28 | 2684539.5617 | 1246791.9881 | 2684533.5817 | 1246788.0666
29 | 2684533.5817 | 1246788.0666 | 2684526.3787 | 1246783.198
30 | 2684528.2255 | 1246795.4846 | 2684531.4485 | 1246797.7989
31 | 2684539.5617 | 1246791.9881 | 2684556.2904 | 1246802.7494
32 | 2684526.3787 | 1246783.198 | 2684511.1361 | 1246772.8952
33 | 2684531.4485 | 1246797.7989 | 2684523.0884 | 1246808.0785
34 | 2684531.4485 | 1246797.7989 | 2684534.7237 | 1246800.1585 | 2684537.2676 | 1246801.8849
35 | 2684537.2676 | 1246801.8849 | 2684514.8509 | 1246829.5028
36 | 2684537.2676 | 1246801.8849 | 2684551.4592 | 1246811.5746
37 | 2684523.0884 | 1246808.0785 | 2684508.8538 | 1246825.5813
38 | 2684434.5297 | 1246689.8166 | 2684454.6037 | 1246704.024
39 | 2684495.4212 | 1246729.1147 | 2684500.2661 | 1246722.1767
40 | 2684381.9071 | 1246771.1663 | 2684395.7971 | 1246751.3918
41 | 2684381.9071 | 1246771.1663 | 2684368.8431 | 1246789.7648
42 | 2684496.9696 | 1246763.3198 | 2684511.1361 | 1246772.8952
43 | 2684503.0915 | 1246832.6665 | 2684508.8538 | 1246825.5813
44 | 2684498.1492 | 1246838.7436 | 2684503.0915 | 1246832.6665
45 | 2684500.7129 | 1246721.5368 | 2684500.2661 | 1246722.1767

## bus_geodata
| x | y | coords
0 | 2684463.8045 | 1246776.9597
1 | 2684448.2685 | 1246796.0316
2 | 2684476.9181 | 1246760.8615
3 | 2684447.7234 | 1246796.7008
4 | 2684480.0982 | 1246763.0083
5 | 2684470.0869 | 1246756.2274
6 | 2684442.0715 | 1246803.639
7 | 2684485.6197 | 1246755.6482
8 | 2684484.6892 | 1246766.1063
9 | 2684466.4808 | 1246753.7631
10 | 2684448.1468 | 1246783.1043
11 | 2684462.0936 | 1246738.7785
12 | 2684460.5863 | 1246749.7409
13 | 2684481.7374 | 1246748.71
14 | 2684490.4804 | 1246736.1899
15 | 2684413.6937 | 1246725.9133
16 | 2684423.7598 | 1246724.6112
17 | 2684409.618 | 1246731.7158
18 | 2684489.5705 | 1246758.3186
19 | 2684533.5817 | 1246788.0666
20 | 2684528.2255 | 1246795.4846
21 | 2684539.5618 | 1246791.9881
22 | 2684526.3787 | 1246783.198
23 | 2684531.4485 | 1246797.7989
24 | 2684537.2676 | 1246801.8849
25 | 2684514.8509 | 1246829.5028
26 | 2684551.4592 | 1246811.5746
27 | 2684556.2904 | 1246802.7494
28 | 2684523.0884 | 1246808.0785
29 | 2684434.5297 | 1246689.8166
30 | 2684448.6326 | 1246741.5839
31 | 2684464.9308 | 1246724.0883
32 | 2684454.6037 | 1246704.024
33 | 2684441.4782 | 1246804.3673
34 | 2684503.1883 | 1246778.5895
35 | 2684428.8567 | 1246806.7348
36 | 2684495.4212 | 1246729.1147
37 | 2684395.7971 | 1246751.3918
38 | 2684368.8431 | 1246789.7648
39 | 2684381.9071 | 1246771.1663
40 | 2684496.9696 | 1246763.3198
41 | 2684511.1361 | 1246772.8952
42 | 2684508.8538 | 1246825.5813
43 | 2684498.1492 | 1246838.7436
44 | 2684503.0915 | 1246832.6665
45 | 2684500.7129 | 1246721.5368
46 | 2684500.2661 | 1246722.1767
47 | 2684476.9181 | 1246760.8615

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 1 | 0 | -0.32524 | -0.081794
1 | 0.99853 | -0.028207 | 0.018675 | 0.0046804
2 | 0.99757 | -0.046456 | 0 | 0
3 | 0.9985 | -0.028917 | 0.012986 | 0.0032546
4 | 0.99713 | -0.054954 | 0 | 0
5 | 0.99659 | -0.065192 | 0 | 0
6 | 0.99822 | -0.034242 | 0.018191 | 0.0045592
7 | 0.99617 | -0.073327 | 0 | 0
8 | 0.99706 | -0.056202 | 0.0022523 | 0.00056449
9 | 0.99619 | -0.072941 | 0 | 0
10 | 0.9957 | -0.082374 | 0.012882 | 0.0032286
11 | 0.99578 | -0.080881 | 0 | 0
12 | 0.99566 | -0.083152 | 0.0068741 | 0.0017228
13 | 0.99602 | -0.076162 | 0 | 0
14 | 0.99576 | -0.081207 | 0.0035746 | 0.00089587
15 | 0.99231 | -0.14782 | 0 | 0
16 | 0.99282 | -0.13793 | 0 | 0
17 | 0.99198 | -0.15408 | 0.011733 | 0.0029405
18 | 0.99576 | -0.081287 | 0.0048049 | 0.0012042
19 | 0.9918 | -0.15749 | 0 | 0
20 | 0.9913 | -0.16715 | 0 | 0
21 | 0.99175 | -0.15854 | 0 | 0
22 | 0.99234 | -0.14705 | 0.010087 | 0.002528
23 | 0.99109 | -0.17133 | 0 | 0
24 | 0.991 | -0.17295 | 0 | 0
25 | 0.99083 | -0.17641 | 0.0054838 | 0.0013744
26 | 0.99089 | -0.17518 | 0.0073203 | 0.0018346
27 | 0.9916 | -0.16146 | 0.0082917 | 0.0020781
28 | 0.99052 | -0.18233 | 0.0087542 | 0.002194
29 | 0.99211 | -0.15172 | 0 | 0
30 | 0.99467 | -0.10214 | 0.0072025 | 0.0018051
31 | 0.99551 | -0.086158 | 0.019834 | 0.004971
32 | 0.99171 | -0.15931 | 0.017448 | 0.0043728
33 | 0.99821 | -0.034502 | 0.015841 | 0.00397
34 | 0.99685 | -0.06035 | 0.010599 | 0.0026564
35 | 0.99528 | -0.090588 | 0.015311 | 0.0038373
36 | 0.99564 | -0.083517 | 0.0065507 | 0.0016418
37 | 0.99114 | -0.17035 | 0.0086344 | 0.002164
38 | 0.99022 | -0.1882 | 0.012834 | 0.0032165
39 | 0.99049 | -0.18302 | 0.016696 | 0.0041845
40 | 0.99502 | -0.095458 | 0.0031287 | 0.00078412
41 | 0.99366 | -0.1217 | 0.0091334 | 0.0022891
42 | 0.98973 | -0.19757 | 0.0056299 | 0.001411
43 | 0.98934 | -0.20523 | 0.017194 | 0.0043093
44 | 0.98946 | -0.20283 | 0.015166 | 0.003801
45 | 0.99557 | -0.084859 | 0.0037599 | 0.00094231
46 | 0.99558 | -0.084808 | 0.004915 | 0.0012318
47 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.065792 | 0.016527 | -0.065703 | -0.016471 | 8.8435e-05 | 5.6276e-05 | 0.097913 | 0.097913 | 0.097913 | 1 | 0 | 0.99853 | -0.028207 | 26.8991
1 | 0.2578 | 0.065267 | -0.25723 | -0.0649 | 0.0005736 | 0.00036656 | 0.38384 | 0.38384 | 0.38384 | 1 | 0 | 0.99757 | -0.046456 | 52.7258
2 | 0.047028 | 0.01179 | -0.047027 | -0.011789 | 1.5896e-06 | 1.0061e-06 | 0.070083 | 0.070083 | 0.070083 | 0.99853 | -0.028207 | 0.9985 | -0.028917 | 19.2536
3 | 0.12725 | 0.032125 | -0.1272 | -0.032092 | 5.1779e-05 | 3.3088e-05 | 0.1899 | 0.1899 | 0.1899 | 0.99757 | -0.046456 | 0.99713 | -0.054954 | 52.1693
4 | 0.12998 | 0.032776 | -0.12986 | -0.032701 | 0.00011644 | 7.4414e-05 | 0.19395 | 0.19395 | 0.19395 | 0.99757 | -0.046456 | 0.99659 | -0.065192 | 53.2823
5 | 0.034041 | 0.0085347 | -0.034032 | -0.0085293 | 8.6366e-06 | 5.4104e-06 | 0.050731 | 0.050731 | 0.050731 | 0.9985 | -0.028917 | 0.99822 | -0.034242 | 13.937
6 | 0.11435 | 0.028869 | -0.11425 | -0.028805 | 0.00010055 | 6.4235e-05 | 0.17071 | 0.17071 | 0.17071 | 0.99713 | -0.054954 | 0.99617 | -0.073327 | 46.8993
7 | 0.012854 | 0.0032224 | -0.012854 | -0.003222 | 7.6428e-07 | 4.169e-07 | 0.019183 | 0.019183 | 0.019183 | 0.99713 | -0.054954 | 0.99706 | -0.056202 | 5.2701
8 | 0.10164 | 0.025617 | -0.1016 | -0.025593 | 3.7669e-05 | 2.4052e-05 | 0.1518 | 0.1518 | 0.1518 | 0.99659 | -0.065192 | 0.99619 | -0.072941 | 41.7046
9 | 0.028223 | 0.0070837 | -0.0282 | -0.0070694 | 2.3107e-05 | 1.4337e-05 | 0.042143 | 0.042143 | 0.042143 | 0.99659 | -0.065192 | 0.9957 | -0.082374 | 11.5778
10 | 0.015841 | 0.0039701 | -0.015841 | -0.00397 | 1.9641e-07 | 1.1342e-07 | 0.023613 | 0.023613 | 0.023613 | 0.99822 | -0.034242 | 0.99821 | -0.034502 | 6.4872
11 | 0.095436 | 0.024088 | -0.0954 | -0.024065 | 3.6372e-05 | 2.3216e-05 | 0.14262 | 0.14262 | 0.14262 | 0.99617 | -0.073327 | 0.99576 | -0.081287 | 39.1802
12 | 0.018809 | 0.0047172 | -0.018807 | -0.0047156 | 2.5407e-06 | 1.5143e-06 | 0.028097 | 0.028097 | 0.028097 | 0.99617 | -0.073327 | 0.99602 | -0.076162 | 7.7191
13 | 0.010601 | 0.0026575 | -0.010599 | -0.0026564 | 2.0949e-06 | 1.0498e-06 | 0.015822 | 0.015822 | 0.015822 | 0.99706 | -0.056202 | 0.99685 | -0.06035 | 4.3466
14 | 0.019847 | 0.0049785 | -0.019839 | -0.004974 | 7.5093e-06 | 4.5095e-06 | 0.029647 | 0.029647 | 0.029647 | 0.99619 | -0.072941 | 0.99578 | -0.080881 | 8.1448
15 | 0.081752 | 0.020615 | -0.081712 | -0.020589 | 3.9933e-05 | 2.5464e-05 | 0.12216 | 0.12216 | 0.12216 | 0.99619 | -0.072941 | 0.99566 | -0.083152 | 33.5598
16 | 0.015317 | 0.0038408 | -0.015311 | -0.0038373 | 5.9942e-06 | 3.4397e-06 | 0.022891 | 0.022891 | 0.022891 | 0.9957 | -0.082374 | 0.99528 | -0.090588 | 6.2888
17 | 0.019839 | 0.004974 | -0.019834 | -0.004971 | 4.9879e-06 | 2.9955e-06 | 0.029647 | 0.029647 | 0.029647 | 0.99578 | -0.080881 | 0.99551 | -0.086158 | 8.1448
18 | 0.074838 | 0.018867 | -0.07477 | -0.018823 | 6.7935e-05 | 4.329e-05 | 0.11188 | 0.11188 | 0.11188 | 0.99566 | -0.083152 | 0.99467 | -0.10214 | 30.7375
19 | 0.018807 | 0.0047156 | -0.018802 | -0.004713 | 4.5209e-06 | 2.6947e-06 | 0.028097 | 0.028098 | 0.028098 | 0.99602 | -0.076162 | 0.99576 | -0.081207 | 7.7191
20 | 0.015228 | 0.0038171 | -0.015226 | -0.0038161 | 1.6758e-06 | 9.6024e-07 | 0.022756 | 0.022756 | 0.022756 | 0.99576 | -0.081207 | 0.99564 | -0.083517 | 6.2516
21 | -0.049963 | -0.012546 | 0.049987 | 0.012561 | 2.3567e-05 | 1.4938e-05 | 0.074931 | 0.074931 | 0.074931 | 0.99231 | -0.14782 | 0.99282 | -0.13793 | 20.5854
22 | 0.049963 | 0.012546 | -0.049948 | -0.012537 | 1.493e-05 | 9.4634e-06 | 0.074931 | 0.074931 | 0.074931 | 0.99231 | -0.14782 | 0.99198 | -0.15408 | 20.5854
23 | 0.017466 | 0.0043833 | -0.017454 | -0.0043766 | 1.1474e-05 | 6.7663e-06 | 0.026179 | 0.026179 | 0.026179 | 0.99282 | -0.13793 | 0.99211 | -0.15172 | 7.1921
24 | -0.067452 | -0.016945 | 0.067568 | 0.017018 | 0.00011544 | 7.3491e-05 | 0.10111 | 0.10111 | 0.10111 | 0.99282 | -0.13793 | 0.99467 | -0.10214 | 27.7774
25 | 0.038215 | 0.0095965 | -0.038186 | -0.0095778 | 2.9637e-05 | 1.8658e-05 | 0.057331 | 0.057331 | 0.057331 | 0.99198 | -0.15408 | 0.99114 | -0.17035 | 15.7504
26 | 0.090595 | 0.02286 | -0.090533 | -0.022821 | 6.1431e-05 | 3.92e-05 | 0.13544 | 0.13544 | 0.13544 | 0.99576 | -0.081287 | 0.99502 | -0.095458 | 37.2076
27 | 0.059653 | 0.014989 | -0.059625 | -0.014972 | 2.7491e-05 | 1.7476e-05 | 0.089512 | 0.089512 | 0.089512 | 0.9918 | -0.15749 | 0.9913 | -0.16715 | 24.5912
28 | 0.0082933 | 0.0020787 | -0.0082928 | -0.0020786 | 4.1429e-07 | 1.7306e-07 | 0.012443 | 0.012443 | 0.012443 | 0.9918 | -0.15749 | 0.99175 | -0.15854 | 3.4183
29 | -0.067946 | -0.017068 | 0.06798 | 0.01709 | 3.389e-05 | 2.1577e-05 | 0.10195 | 0.10195 | 0.10195 | 0.9918 | -0.15749 | 0.99234 | -0.14705 | 28.0095
30 | 0.059625 | 0.014972 | -0.059613 | -0.014964 | 1.1898e-05 | 7.5639e-06 | 0.089512 | 0.089512 | 0.089512 | 0.9913 | -0.16715 | 0.99109 | -0.17133 | 24.5912
31 | 0.0082928 | 0.0020786 | -0.0082917 | -0.0020781 | 1.1548e-06 | 4.8246e-07 | 0.012443 | 0.012443 | 0.012443 | 0.99175 | -0.15854 | 0.9916 | -0.16146 | 3.4183
32 | -0.078067 | -0.019618 | 0.078161 | 0.019678 | 9.4572e-05 | 6.0288e-05 | 0.11708 | 0.11708 | 0.11708 | 0.99234 | -0.14705 | 0.99366 | -0.1217 | 32.1647
33 | 0.046807 | 0.011754 | -0.046782 | -0.011739 | 2.4545e-05 | 1.5538e-05 | 0.070284 | 0.070284 | 0.070284 | 0.99109 | -0.17133 | 0.99052 | -0.18233 | 19.3088
34 | 0.012807 | 0.0032099 | -0.012806 | -0.0032094 | 9.8591e-07 | 5.3935e-07 | 0.019228 | 0.019228 | 0.019228 | 0.99109 | -0.17133 | 0.991 | -0.17295 | 5.2825
35 | 0.0054847 | 0.0013745 | -0.0054838 | -0.0013744 | 9.0468e-07 | 1.2078e-07 | 0.0082354 | 0.0082355 | 0.0082355 | 0.991 | -0.17295 | 0.99083 | -0.17641 | 2.2625
36 | 0.007321 | 0.0018349 | -0.0073203 | -0.0018346 | 7.7871e-07 | 2.7699e-07 | 0.010993 | 0.010993 | 0.010993 | 0.991 | -0.17295 | 0.99089 | -0.17518 | 3.02
37 | 0.038028 | 0.0095449 | -0.038 | -0.0095275 | 2.7615e-05 | 1.7384e-05 | 0.057133 | 0.057133 | 0.057133 | 0.99052 | -0.18233 | 0.98973 | -0.19757 | 15.6959
38 | 0.017454 | 0.0043766 | -0.017448 | -0.0043728 | 6.3081e-06 | 3.7204e-06 | 0.026179 | 0.02618 | 0.02618 | 0.99211 | -0.15172 | 0.99171 | -0.15931 | 7.1922
39 | 0.0086755 | 0.0021744 | -0.0086749 | -0.0021741 | 5.3347e-07 | 2.3138e-07 | 0.012966 | 0.012966 | 0.012966 | 0.99564 | -0.083517 | 0.99558 | -0.084808 | 3.562
40 | 0.029551 | 0.0074138 | -0.029533 | -0.0074027 | 1.7839e-05 | 1.1106e-05 | 0.044368 | 0.044369 | 0.044369 | 0.99114 | -0.17035 | 0.99049 | -0.18302 | 12.1892
41 | -0.012834 | -0.0032165 | 0.012837 | 0.0032182 | 3.1701e-06 | 1.7364e-06 | 0.019286 | 0.019286 | 0.019286 | 0.99022 | -0.1882 | 0.99049 | -0.18302 | 5.2983
42 | 0.087405 | 0.022037 | -0.087295 | -0.021967 | 0.00010963 | 6.9942e-05 | 0.13076 | 0.13076 | 0.13076 | 0.99502 | -0.095458 | 0.99366 | -0.1217 | 35.9223
43 | 0.03237 | 0.0081165 | -0.032362 | -0.0081114 | 8.1119e-06 | 5.0743e-06 | 0.048669 | 0.048669 | 0.048669 | 0.98973 | -0.19757 | 0.98946 | -0.20283 | 13.3705
44 | -0.017194 | -0.0043093 | 0.017196 | 0.0043105 | 1.9645e-06 | 1.1567e-06 | 0.025861 | 0.025861 | 0.025861 | 0.98934 | -0.20523 | 0.98946 | -0.20283 | 7.1047
45 | -0.0037599 | -0.00094231 | 0.0037599 | 0.00094231 | 9.2433e-09 | -4.2333e-09 | 0.0056196 | 0.0056196 | 0.0056196 | 0.99557 | -0.084859 | 0.99558 | -0.084808 | 1.5439

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.33746 | 0.084856

## res_load
| p_mw | q_mvar
0 | 0.01222 | 0.0030625
1 | 0.018675 | 0.0046804
2 | 0.012986 | 0.0032546
3 | 0.018191 | 0.0045592
4 | 0.0022523 | 0.00056449
5 | 0.012882 | 0.0032286
6 | 0.0068741 | 0.0017228
7 | 0.0035746 | 0.00089587
8 | 0.011733 | 0.0029405
9 | 0.0048049 | 0.0012042
10 | 0.010087 | 0.002528
11 | 0.0054838 | 0.0013744
12 | 0.0073203 | 0.0018346
13 | 0.0082917 | 0.0020781
14 | 0.0087542 | 0.002194
15 | 0.0072025 | 0.0018051
16 | 0.019834 | 0.004971
17 | 0.017448 | 0.0043728
18 | 0.015841 | 0.00397
19 | 0.010599 | 0.0026564
20 | 0.015311 | 0.0038373
21 | 0.0065507 | 0.0016418
22 | 0.0086344 | 0.002164
23 | 0.012834 | 0.0032165
24 | 0.016696 | 0.0041845
25 | 0.0031287 | 0.00078412
26 | 0.0091334 | 0.0022891
27 | 0.0056299 | 0.001411
28 | 0.017194 | 0.0043093
29 | 0.015166 | 0.003801
30 | 0.0037599 | 0.00094231
31 | 0.004915 | 0.0012318

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1