## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-722_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-722_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-722_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_261-722_0_3_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_261-722_0_3_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_261-722_0_3_node_3 | 0.4 | n |  | TRUE
6 | bus_LV_261-722_0_3_node_7 | 0.4 | n |  | TRUE
7 | bus_LV_261-722_0_3_node_27 | 0.4 | n |  | TRUE
8 | bus_LV_261-722_0_3_node_16 | 0.4 | n |  | TRUE
9 | bus_LV_261-722_0_3_node_42 | 0.4 | n |  | TRUE
10 | bus_LV_261-722_0_3_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_261-722_0_3_node_19 | 0.4 | n |  | TRUE
12 | bus_LV_261-722_0_3_node_25 | 0.4 | n |  | TRUE
13 | bus_LV_261-722_0_3_node_10 | 0.4 | n |  | TRUE
14 | bus_LV_261-722_0_3_node_14 | 0.4 | n |  | TRUE
15 | bus_LV_261-722_0_3_node_13 | 0.4 | n |  | TRUE
16 | bus_LV_261-722_0_3_node_23 | 0.4 | n |  | TRUE
17 | bus_LV_261-722_0_3_node_12 | 0.4 | n |  | TRUE
18 | bus_LV_261-722_0_3_node_15 | 0.4 | n |  | TRUE
19 | bus_LV_261-722_0_3_node_52 | 0.4 | n |  | TRUE
20 | bus_LV_261-722_0_3_node_29 | 0.4 | n |  | TRUE
21 | bus_LV_261-722_0_3_node_26 | 0.4 | n |  | TRUE
22 | bus_LV_261-722_0_3_node_40 | 0.4 | n |  | TRUE
23 | bus_LV_261-722_0_3_node_37 | 0.4 | n |  | TRUE
24 | bus_LV_261-722_0_3_node_17 | 0.4 | n |  | TRUE
25 | bus_LV_261-722_0_3_node_46 | 0.4 | n |  | TRUE
26 | bus_LV_261-722_0_3_node_39 | 0.4 | n |  | TRUE
27 | bus_LV_261-722_0_3_node_43 | 0.4 | n |  | TRUE
28 | bus_LV_261-722_0_3_node_18 | 0.4 | n |  | TRUE
29 | bus_LV_261-722_0_3_node_28 | 0.4 | n |  | TRUE
30 | bus_LV_261-722_0_3_node_21 | 0.4 | n |  | TRUE
31 | bus_LV_261-722_0_3_node_36 | 0.4 | n |  | TRUE
32 | bus_LV_261-722_0_3_node_35 | 0.4 | n |  | TRUE
33 | bus_LV_261-722_0_3_node_50 | 0.4 | n |  | TRUE
34 | bus_LV_261-722_0_3_node_51 | 0.4 | n |  | TRUE
35 | bus_LV_261-722_0_3_node_38 | 0.4 | n |  | TRUE
36 | bus_LV_261-722_0_3_node_20 | 0.4 | n |  | TRUE
37 | bus_LV_261-722_0_3_node_22 | 0.4 | n |  | TRUE
38 | bus_LV_261-722_0_3_node_24 | 0.4 | n |  | TRUE
39 | bus_LV_261-722_0_3_node_33 | 0.4 | n |  | TRUE
40 | bus_LV_261-722_0_3_node_31 | 0.4 | n |  | TRUE
41 | bus_LV_261-722_0_3_node_30 | 0.4 | n |  | TRUE
42 | bus_LV_261-722_0_3_node_32 | 0.4 | n |  | TRUE
43 | bus_LV_261-722_0_3_node_34 | 0.4 | n |  | TRUE
44 | bus_LV_261-722_0_3_node_44 | 0.4 | n |  | TRUE
45 | bus_LV_261-722_0_3_node_45 | 0.4 | n |  | TRUE
46 | bus_LV_261-722_0_3_node_48 | 0.4 | n |  | TRUE
47 | bus_LV_261-722_0_3_node_49 | 0.4 | n |  | TRUE
48 | bus_MV_539_0_node_23 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-722_0_3_load_0 | 0 | 0.010415 | 0.0026102 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-722_0_3_load_4 | 3 | 0.0040836 | 0.0010234 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-722_0_3_load_5 | 4 | 0.0042716 | 0.0010706 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-722_0_3_load_27 | 7 | 0.0056355 | 0.0014124 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-722_0_3_load_16 | 8 | 0.012582 | 0.0031535 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-722_0_3_load_42 | 9 | 0.0092147 | 0.0023094 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-722_0_3_load_19 | 11 | 0.012879 | 0.0032277 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-722_0_3_load_25 | 12 | 0.010716 | 0.0026856 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-722_0_3_load_23 | 16 | 0.0095331 | 0.0023892 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-722_0_3_load_52 | 19 | 0.0026886 | 0.00067382 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-722_0_3_load_29 | 20 | 0.0082875 | 0.002077 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-722_0_3_load_26 | 21 | 0.007997 | 0.0020042 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-722_0_3_load_37 | 23 | 0.0029236 | 0.00073271 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-722_0_3_load_17 | 24 | 0.010034 | 0.0025146 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-722_0_3_load_46 | 25 | 0.016976 | 0.0042545 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-722_0_3_load_39 | 26 | 0.002997 | 0.00075111 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-722_0_3_load_43 | 27 | 0.0058775 | 0.001473 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_261-722_0_3_load_18 | 28 | 0.0102 | 0.0025563 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_261-722_0_3_load_28 | 29 | 0.0073619 | 0.0018451 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_261-722_0_3_load_21 | 30 | 0.010104 | 0.0025322 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_261-722_0_3_load_36 | 31 | 0.0031863 | 0.00079857 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_261-722_0_3_load_35 | 32 | 0.010433 | 0.0026148 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_261-722_0_3_load_50 | 33 | 0.0034288 | 0.00085935 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_261-722_0_3_load_51 | 34 | 0.0026986 | 0.00067632 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_261-722_0_3_load_38 | 35 | 0.0035274 | 0.00088405 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_261-722_0_3_load_20 | 36 | 0.011653 | 0.0029204 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_261-722_0_3_load_22 | 37 | 0.019076 | 0.004781 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_261-722_0_3_load_24 | 38 | 0.008475 | 0.002124 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_261-722_0_3_load_33 | 39 | 0.011106 | 0.0027834 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_261-722_0_3_load_31 | 40 | 0.021019 | 0.0052678 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_261-722_0_3_load_30 | 41 | 0.0083393 | 0.00209 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_261-722_0_3_load_32 | 42 | 0.010215 | 0.00256 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_261-722_0_3_load_34 | 43 | 0.022301 | 0.005589 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_261-722_0_3_load_44 | 44 | 0.0067027 | 0.0016799 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_261-722_0_3_load_45 | 45 | 0.0085637 | 0.0021463 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_261-722_0_3_load_48 | 46 | 0.0044474 | 0.0011146 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_261-722_0_3_load_49 | 47 | 0.0031675 | 0.00079385 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 40 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-722_0_3_line_0 |  | 0 | 1 | 0.017758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
1 | LV_261-722_0_3_line_1 |  | 0 | 2 | 0.012151 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
2 | LV_261-722_0_3_line_2 |  | 1 | 3 | 0.0097864 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
3 | LV_261-722_0_3_line_3 |  | 2 | 4 | 0.0080433 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
4 | LV_261-722_0_3_line_4 |  | 3 | 7 | 0.012604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
5 | LV_261-722_0_3_line_5 |  | 4 | 8 | 0.0071535 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
6 | LV_261-722_0_3_line_6 |  | 5 | 6 | 0.030891 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
7 | LV_261-722_0_3_line_7 |  | 5 | 7 | 0.025936 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
8 | LV_261-722_0_3_line_8 |  | 6 | 9 | 0.030739 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
9 | LV_261-722_0_3_line_9 |  | 8 | 24 | 0.029136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
10 | LV_261-722_0_3_line_10 |  | 9 | 27 | 0.025616 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
11 | LV_261-722_0_3_line_11 |  | 10 | 11 | 0.034717 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
12 | LV_261-722_0_3_line_12 |  | 10 | 12 | 0.01701 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
13 | LV_261-722_0_3_line_13 |  | 11 | 28 | 0.026786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
14 | LV_261-722_0_3_line_14 |  | 12 | 21 | 0.03061 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
15 | LV_261-722_0_3_line_15 |  | 13 | 14 | 0.00888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
16 | LV_261-722_0_3_line_16 |  | 13 | 15 | 0.009236 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_261-722_0_3_line_17 |  | 13 | 16 | 0.033248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
18 | LV_261-722_0_3_line_18 |  | 14 | 21 | 0.01106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
19 | LV_261-722_0_3_line_19 |  | 15 | 20 | 0.01003 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_261-722_0_3_line_20 |  | 16 | 30 | 0.0073331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
21 | LV_261-722_0_3_line_21 |  | 17 | 18 | 0.049615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
22 | LV_261-722_0_3_line_22 |  | 17 | 19 | 0.046158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
23 | LV_261-722_0_3_line_23 |  | 18 | 22 | 0.057163 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_261-722_0_3_line_24 |  | 18 | 23 | 0.019677 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
25 | LV_261-722_0_3_line_25 |  | 19 | 33 | 0.0059992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
26 | LV_261-722_0_3_line_26 |  | 20 | 29 | 0.017343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_261-722_0_3_line_27 |  | 22 | 34 | 0.0095631 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_261-722_0_3_line_28 |  | 23 | 35 | 0.023026 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
29 | LV_261-722_0_3_line_29 |  | 24 | 28 | 0.016282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
30 | LV_261-722_0_3_line_30 |  | 25 | 26 | 0.010748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_261-722_0_3_line_31 |  | 26 | 35 | 0.010234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
32 | LV_261-722_0_3_line_32 |  | 27 | 44 | 0.0013753 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
33 | LV_261-722_0_3_line_33 |  | 30 | 36 | 0.01578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
34 | LV_261-722_0_3_line_34 |  | 31 | 32 | 0.004136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_261-722_0_3_line_35 |  | 32 | 43 | 0.022778 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_261-722_0_3_line_36 |  | 33 | 47 | 0.011816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
37 | LV_261-722_0_3_line_37 |  | 36 | 37 | 0.012154 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
38 | LV_261-722_0_3_line_38 |  | 37 | 38 | 0.011287 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
39 | LV_261-722_0_3_line_39 |  | 38 | 39 | 0.00023728 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
40 | LV_261-722_0_3_line_40 |  | 39 | 40 | 0.018376 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
41 | LV_261-722_0_3_line_41 |  | 40 | 41 | 0.00092737 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_261-722_0_3_line_42 |  | 41 | 42 | 0.022723 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_261-722_0_3_line_43 |  | 42 | 43 | 0.0025129 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_261-722_0_3_line_44 |  | 44 | 45 | 0.013157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
45 | LV_261-722_0_3_line_45 |  | 45 | 46 | 0.012458 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
46 | LV_261-722_0_3_line_46 |  | 46 | 47 | 0.0029112 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-722_0_3_trafo_31 | 0.63 MVA 20/0.4 kV | 48 | 40 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2685100.6378 | 1246424.8519 | 2685110.7605 | 1246410.2617
1 | 2685117.6871 | 1246400.2784 | 2685110.7605 | 1246410.2617
2 | 2685100.6378 | 1246424.8519 | 2685099.4575 | 1246426.5473 | 2685105.0008 | 1246430.3741 | 2685104.4392 | 1246431.183
3 | 2685117.6871 | 1246400.2784 | 2685122.2714 | 1246393.6695
4 | 2685104.4392 | 1246431.183 | 2685097.2513 | 1246441.5364
5 | 2685126.3487 | 1246387.7916 | 2685122.2714 | 1246393.6695
6 | 2685064.3999 | 1246460.425 | 2685061.5923 | 1246458.6501 | 2685063.3872 | 1246456.7633 | 2685077.6204 | 1246436.2523
7 | 2685077.6204 | 1246436.2523 | 2685093.3751 | 1246447.1197 | 2685097.2513 | 1246441.5364
8 | 2685064.3999 | 1246460.425 | 2685067.0764 | 1246462.387 | 2685082.8862 | 1246472.5658 | 2685089.7313 | 1246477.8007
9 | 2685126.3487 | 1246387.7916 | 2685142.9553 | 1246363.8511
10 | 2685089.7313 | 1246477.8007 | 2685104.4901 | 1246489.0879 | 2685109.6853 | 1246493.8328
11 | 2685187.2902 | 1246299.9369 | 2685167.5027 | 1246328.463
12 | 2685187.2902 | 1246299.9369 | 2685191.1811 | 1246302.5614 | 2685201.2716 | 1246309.6244
13 | 2685152.2356 | 1246350.4724 | 2685167.5027 | 1246328.463
14 | 2685226.3485 | 1246327.1773 | 2685201.2716 | 1246309.6244
15 | 2685235.4093 | 1246333.5196 | 2685242.7022 | 1246338.617
16 | 2685250.2636 | 1246343.9519 | 2685242.7022 | 1246338.617
17 | 2685242.7022 | 1246338.617 | 2685229.8396 | 1246357.8019 | 2685224.6688 | 1246366.5367
18 | 2685235.4093 | 1246333.5196 | 2685226.3485 | 1246327.1773
19 | 2685250.2636 | 1246343.9519 | 2685258.4576 | 1246349.737
20 | 2685224.6688 | 1246366.5367 | 2685220.9333 | 1246372.847
21 | 2685142.0513 | 1246540.7428 | 2685149.0474 | 1246548.6046 | 2685155.1408 | 1246556.7203 | 2685159.657 | 1246552.6266 | 2685161.7483 | 1246554.8249 | 2685163.3426 | 1246556.3823 | 2685171.6322 | 1246565.1856 | 2685175.1752 | 1246560.9889
22 | 2685175.1752 | 1246560.9889 | 2685161.7404 | 1246548.5424 | 2685153.4606 | 1246539.5835 | 2685143.0056 | 1246527.9446
23 | 2685103.0529 | 1246536.569 | 2685117.9076 | 1246545.9001 | 2685120.5014 | 1246550.4629 | 2685120.5832 | 1246557.3914 | 2685124.1498 | 1246556.2863 | 2685131.2851 | 1246550.2509 | 2685139.9467 | 1246542.6251 | 2685142.0513 | 1246540.7428
24 | 2685142.0513 | 1246540.7428 | 2685133.0979 | 1246529.7618 | 2685129.4932 | 1246525.5969
25 | 2685138.9966 | 1246523.4816 | 2685143.0056 | 1246527.9446
26 | 2685258.4576 | 1246349.737 | 2685272.625 | 1246359.7396
27 | 2685103.0529 | 1246536.569 | 2685095.1343 | 1246531.2073
28 | 2685129.4932 | 1246525.5969 | 2685127.933 | 1246523.7943 | 2685118.4181 | 1246514.0395 | 2685113.4323 | 1246509.1049
29 | 2685142.9553 | 1246363.8511 | 2685152.2356 | 1246350.4724
30 | 2685098.0569 | 1246494.8467 | 2685105.3079 | 1246501.064 | 2685106.1584 | 1246501.9058
31 | 2685106.1584 | 1246501.9058 | 2685113.4323 | 1246509.1049
32 | 2685109.6853 | 1246493.8328 | 2685110.7008 | 1246494.7602
33 | 2685214.6338 | 1246387.2819 | 2685219.2857 | 1246375.6301 | 2685220.9333 | 1246372.847
34 | 2685200.5323 | 1246476.3844 | 2685200.7569 | 1246480.5144
35 | 2685200.5323 | 1246476.3844 | 2685200.434 | 1246474.5768 | 2685200.0856 | 1246453.6118
36 | 2685130.9391 | 1246514.841 | 2685135.9044 | 1246520.0393 | 2685138.9966 | 1246523.4816
37 | 2685210.2986 | 1246398.6265 | 2685210.6961 | 1246397.1448 | 2685214.6338 | 1246387.2819
38 | 2685207.3743 | 1246409.5276 | 2685210.2986 | 1246398.6265
39 | 2685207.3128 | 1246409.7568 | 2685207.3743 | 1246409.5276
40 | 2685203.2435 | 1246427.6393 | 2685203.8469 | 1246422.6764 | 2685207.3128 | 1246409.7568
41 | 2685203.1316 | 1246428.5599 | 2685203.2435 | 1246427.6393
42 | 2685203.1316 | 1246428.5599 | 2685200.3889 | 1246451.1173
43 | 2685200.0856 | 1246453.6118 | 2685200.0856 | 1246453.6118 | 2685200.3889 | 1246451.1173
44 | 2685110.7008 | 1246494.7602 | 2685118.9867 | 1246502.3279 | 2685120.3233 | 1246503.7272
45 | 2685120.3233 | 1246503.7272 | 2685128.9283 | 1246512.7359
46 | 2685128.9283 | 1246512.7359 | 2685130.9391 | 1246514.841

## bus_geodata
| x | y | coords
0 | 2685110.7605 | 1246410.2617
1 | 2685100.6378 | 1246424.8519
2 | 2685117.6871 | 1246400.2784
3 | 2685104.4392 | 1246431.183
4 | 2685122.2714 | 1246393.6695
5 | 2685077.6204 | 1246436.2523
6 | 2685064.3999 | 1246460.425
7 | 2685097.2513 | 1246441.5364
8 | 2685126.3487 | 1246387.7916
9 | 2685089.7313 | 1246477.8007
10 | 2685187.2902 | 1246299.9369
11 | 2685167.5027 | 1246328.463
12 | 2685201.2716 | 1246309.6244
13 | 2685242.7022 | 1246338.617
14 | 2685235.4093 | 1246333.5196
15 | 2685250.2636 | 1246343.9519
16 | 2685224.6688 | 1246366.5367
17 | 2685175.1752 | 1246560.9889
18 | 2685142.0513 | 1246540.7428
19 | 2685143.0056 | 1246527.9446
20 | 2685258.4576 | 1246349.737
21 | 2685226.3485 | 1246327.1773
22 | 2685103.0529 | 1246536.569
23 | 2685129.4932 | 1246525.5969
24 | 2685142.9553 | 1246363.8511
25 | 2685098.0569 | 1246494.8467
26 | 2685106.1584 | 1246501.9058
27 | 2685109.6853 | 1246493.8328
28 | 2685152.2356 | 1246350.4724
29 | 2685272.625 | 1246359.7396
30 | 2685220.9333 | 1246372.847
31 | 2685200.7569 | 1246480.5144
32 | 2685200.5323 | 1246476.3844
33 | 2685138.9966 | 1246523.4816
34 | 2685095.1343 | 1246531.2073
35 | 2685113.4323 | 1246509.1049
36 | 2685214.6338 | 1246387.2819
37 | 2685210.2986 | 1246398.6265
38 | 2685207.3743 | 1246409.5276
39 | 2685207.3128 | 1246409.7568
40 | 2685203.2435 | 1246427.6393
41 | 2685203.1316 | 1246428.5599
42 | 2685200.3889 | 1246451.1173
43 | 2685200.0856 | 1246453.6118
44 | 2685110.7008 | 1246494.7602
45 | 2685120.3233 | 1246503.7272
46 | 2685128.9283 | 1246512.7359
47 | 2685130.9391 | 1246514.841
48 | 2685201.7793 | 1246486.6272

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97831 | -0.41624 | 0.010415 | 0.0026102
1 | 0.97763 | -0.42966 | 0 | 0
2 | 0.97884 | -0.40592 | 0 | 0
3 | 0.97725 | -0.43707 | 0.0040836 | 0.0010234
4 | 0.97919 | -0.39909 | 0.0042716 | 0.0010706
5 | 0.9759 | -0.46351 | 0 | 0
6 | 0.97484 | -0.48423 | 0 | 0
7 | 0.97678 | -0.44615 | 0.0056355 | 0.0014124
8 | 0.97952 | -0.39274 | 0.012582 | 0.0031535
9 | 0.97379 | -0.5049 | 0.0092147 | 0.0023094
10 | 0.98586 | -0.26964 | 0 | 0
11 | 0.98355 | -0.31436 | 0.012879 | 0.0032277
12 | 0.987 | -0.2478 | 0.010716 | 0.0026856
13 | 0.99069 | -0.17697 | 0 | 0
14 | 0.99002 | -0.18976 | 0 | 0
15 | 0.99056 | -0.17954 | 0 | 0
16 | 0.99343 | -0.12465 | 0.0095331 | 0.0023892
17 | 0.97146 | -0.55091 | 0 | 0
18 | 0.97079 | -0.56426 | 0 | 0
19 | 0.97209 | -0.5385 | 0.0026886 | 0.00067382
20 | 0.99041 | -0.18232 | 0.0082875 | 0.002077
21 | 0.98919 | -0.20571 | 0.007997 | 0.0020042
22 | 0.97064 | -0.56712 | 0 | 0
23 | 0.97054 | -0.56907 | 0.0029236 | 0.00073271
24 | 0.98101 | -0.36361 | 0.010034 | 0.0025146
25 | 0.97003 | -0.57935 | 0.016976 | 0.0042545
26 | 0.9702 | -0.57597 | 0.002997 | 0.00075111
27 | 0.97303 | -0.51998 | 0.0058775 | 0.001473
28 | 0.98192 | -0.3459 | 0.0102 | 0.0025563
29 | 0.99029 | -0.18459 | 0.0073619 | 0.0018451
30 | 0.99406 | -0.11253 | 0.010104 | 0.0025322
31 | 0.99863 | -0.0264 | 0.0031863 | 0.00079857
32 | 0.99864 | -0.026169 | 0.010433 | 0.0026148
33 | 0.97218 | -0.53674 | 0.0034288 | 0.00085935
34 | 0.97062 | -0.5676 | 0.0026986 | 0.00067632
35 | 0.97029 | -0.57408 | 0.0035274 | 0.00088405
36 | 0.99551 | -0.085105 | 0.011653 | 0.0029204
37 | 0.99668 | -0.062793 | 0.019076 | 0.004781
38 | 0.99787 | -0.040236 | 0.008475 | 0.002124
39 | 0.9979 | -0.039745 | 0.011106 | 0.0027834
40 | 1 | 0 | -0.30763 | -0.078182
41 | 0.99995 | -0.00088056 | 0.0083393 | 0.00209
42 | 0.999 | -0.019172 | 0.010215 | 0.00256
43 | 0.99892 | -0.020749 | 0.022301 | 0.005589
44 | 0.97299 | -0.52072 | 0.0067027 | 0.0016799
45 | 0.97268 | -0.52695 | 0.0085637 | 0.0021463
46 | 0.97243 | -0.53187 | 0.0044474 | 0.0011146
47 | 0.97237 | -0.5329 | 0.0031675 | 0.00079385
48 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.083393 | 0.02107 | -0.08334 | -0.021036 | 5.3621e-05 | 3.3872e-05 | 0.1269 | 0.1269 | 0.1269 | 0.97831 | -0.41624 | 0.97763 | -0.42966 | 17.4317
1 | -0.093808 | -0.02368 | 0.093855 | 0.02371 | 4.6422e-05 | 2.9405e-05 | 0.14274 | 0.14274 | 0.14274 | 0.97831 | -0.41624 | 0.97884 | -0.40592 | 19.6076
2 | 0.08334 | 0.021036 | -0.08331 | -0.021018 | 2.9551e-05 | 1.8667e-05 | 0.1269 | 0.1269 | 0.1269 | 0.97763 | -0.42966 | 0.97725 | -0.43707 | 17.4317
3 | -0.093855 | -0.02371 | 0.093885 | 0.023729 | 3.0729e-05 | 1.9464e-05 | 0.14274 | 0.14274 | 0.14274 | 0.97884 | -0.40592 | 0.97919 | -0.39909 | 19.6076
4 | 0.079227 | 0.019994 | -0.079192 | -0.019973 | 3.442e-05 | 2.1713e-05 | 0.12068 | 0.12069 | 0.12069 | 0.97725 | -0.43707 | 0.97678 | -0.44615 | 16.5776
5 | -0.098157 | -0.0248 | 0.098187 | 0.024819 | 2.9872e-05 | 1.8938e-05 | 0.14923 | 0.14923 | 0.14923 | 0.97919 | -0.39909 | 0.97952 | -0.39274 | 20.4992
6 | 0.073496 | 0.018522 | -0.073423 | -0.018476 | 7.2787e-05 | 4.5812e-05 | 0.1121 | 0.1121 | 0.1121 | 0.9759 | -0.46351 | 0.97484 | -0.48423 | 15.3984
7 | -0.073496 | -0.018522 | 0.073557 | 0.01856 | 6.1111e-05 | 3.8462e-05 | 0.1121 | 0.1121 | 0.1121 | 0.9759 | -0.46351 | 0.97678 | -0.44615 | 15.3984
8 | 0.073423 | 0.018476 | -0.07335 | -0.01843 | 7.2428e-05 | 4.5589e-05 | 0.1121 | 0.1121 | 0.1121 | 0.97484 | -0.48423 | 0.97379 | -0.5049 | 15.3985
9 | -0.11077 | -0.027972 | 0.11092 | 0.028071 | 0.00015483 | 9.8356e-05 | 0.16835 | 0.16835 | 0.16835 | 0.97952 | -0.39274 | 0.98101 | -0.36361 | 23.1248
10 | 0.064136 | 0.016121 | -0.064089 | -0.016092 | 4.6147e-05 | 2.8897e-05 | 0.09802 | 0.09802 | 0.09802 | 0.97379 | -0.5049 | 0.97303 | -0.51998 | 13.4643
11 | 0.14465 | 0.036759 | -0.14434 | -0.036561 | 0.0003108 | 0.00019803 | 0.21851 | 0.21851 | 0.21851 | 0.98586 | -0.26964 | 0.98355 | -0.31436 | 30.0148
12 | -0.14465 | -0.036759 | 0.1448 | 0.036856 | 0.00015228 | 9.7025e-05 | 0.21851 | 0.21851 | 0.21851 | 0.98586 | -0.26964 | 0.987 | -0.2478 | 30.0148
13 | 0.13146 | 0.033334 | -0.13126 | -0.033207 | 0.00019894 | 0.00012664 | 0.19902 | 0.19902 | 0.19902 | 0.98355 | -0.31436 | 0.98192 | -0.3459 | 27.3385
14 | -0.15552 | -0.039542 | 0.15583 | 0.039743 | 0.00031605 | 0.00020148 | 0.23466 | 0.23466 | 0.23466 | 0.987 | -0.2478 | 0.98919 | -0.20571 | 32.2339
15 | 0.16406 | 0.041893 | -0.16396 | -0.041828 | 0.00010133 | 6.4621e-05 | 0.24669 | 0.24669 | 0.24669 | 0.99069 | -0.17697 | 0.99002 | -0.18976 | 33.8863
16 | 0.015654 | 0.0039247 | -0.015652 | -0.0039236 | 1.9149e-06 | 1.1066e-06 | 0.023513 | 0.023513 | 0.023513 | 0.99069 | -0.17697 | 0.99056 | -0.17954 | 6.4597
17 | -0.17971 | -0.045817 | 0.18017 | 0.046108 | 0.00045515 | 0.00029044 | 0.2702 | 0.2702 | 0.2702 | 0.99069 | -0.17697 | 0.99343 | -0.12465 | 37.1161
18 | 0.16396 | 0.041828 | -0.16383 | -0.041748 | 0.0001262 | 8.0485e-05 | 0.24669 | 0.24669 | 0.24669 | 0.99002 | -0.18976 | 0.98919 | -0.20571 | 33.8863
19 | 0.015652 | 0.0039236 | -0.01565 | -0.0039224 | 2.0796e-06 | 1.2018e-06 | 0.023513 | 0.023513 | 0.023513 | 0.99056 | -0.17954 | 0.99041 | -0.18232 | 6.4597
20 | -0.1897 | -0.048497 | 0.18981 | 0.048568 | 0.00011128 | 7.1027e-05 | 0.28448 | 0.28448 | 0.28448 | 0.99343 | -0.12465 | 0.99406 | -0.11253 | 39.0774
21 | 0.029157 | 0.0073178 | -0.029139 | -0.0073071 | 1.8559e-05 | 1.065e-05 | 0.044665 | 0.044665 | 0.044665 | 0.97146 | -0.55091 | 0.97079 | -0.56426 | 6.1354
22 | -0.029157 | -0.0073178 | 0.029175 | 0.0073277 | 1.7266e-05 | 9.9063e-06 | 0.044665 | 0.044665 | 0.044665 | 0.97146 | -0.55091 | 0.97209 | -0.5385 | 6.1353
23 | 0.002699 | 0.00067577 | -0.0026986 | -0.00067625 | 3.6685e-07 | -4.7187e-07 | 0.0041368 | 0.004137 | 0.004137 | 0.97079 | -0.56426 | 0.97064 | -0.56712 | 1.1365
24 | 0.02644 | 0.0066313 | -0.026434 | -0.0066279 | 6.0601e-06 | 3.392e-06 | 0.040529 | 0.040529 | 0.040529 | 0.97079 | -0.56426 | 0.97054 | -0.56907 | 5.5672
25 | -0.031863 | -0.0080015 | 0.031866 | 0.0080031 | 2.6766e-06 | 1.5643e-06 | 0.04878 | 0.04878 | 0.04878 | 0.97209 | -0.5385 | 0.97218 | -0.53674 | 6.7006
26 | 0.0073627 | 0.0018454 | -0.0073619 | -0.0018451 | 7.9582e-07 | 2.8617e-07 | 0.011062 | 0.011062 | 0.011062 | 0.99041 | -0.18232 | 0.99029 | -0.18459 | 3.039
27 | 0.0026986 | 0.00067625 | -0.0026986 | -0.00067632 | 6.1377e-08 | -7.8918e-08 | 0.004137 | 0.0041371 | 0.0041371 | 0.97064 | -0.56712 | 0.97062 | -0.5676 | 1.1366
28 | 0.02351 | 0.0058952 | -0.023505 | -0.0058922 | 5.6098e-06 | 3.0213e-06 | 0.036047 | 0.036047 | 0.036047 | 0.97054 | -0.56907 | 0.97029 | -0.57408 | 4.9515
29 | -0.12096 | -0.030585 | 0.12106 | 0.030651 | 0.00010287 | 6.5428e-05 | 0.18357 | 0.18357 | 0.18357 | 0.98101 | -0.36361 | 0.98192 | -0.3459 | 25.2153
30 | -0.016976 | -0.0042545 | 0.016979 | 0.0042562 | 2.7332e-06 | 1.6165e-06 | 0.026041 | 0.026041 | 0.026041 | 0.97003 | -0.57935 | 0.9702 | -0.57597 | 7.1541
31 | -0.019975 | -0.0050073 | 0.019977 | 0.0050082 | 1.8012e-06 | 8.9996e-07 | 0.030637 | 0.030637 | 0.030637 | 0.9702 | -0.57597 | 0.97029 | -0.57408 | 4.2084
32 | 0.058212 | 0.014619 | -0.05821 | -0.014618 | 2.044e-06 | 1.274e-06 | 0.089032 | 0.089032 | 0.089032 | 0.97303 | -0.51998 | 0.97299 | -0.52072 | 12.2297
33 | -0.19991 | -0.0511 | 0.20018 | 0.05127 | 0.0002656 | 0.00016957 | 0.29961 | 0.29961 | 0.29961 | 0.99406 | -0.11253 | 0.99551 | -0.085105 | 41.1549
34 | -0.0031863 | -0.00079857 | 0.0031864 | 0.00079853 | 3.4962e-08 | -3.1738e-08 | 0.0047478 | 0.0047478 | 0.0047478 | 0.99863 | -0.0264 | 0.99864 | -0.026169 | 1.3043
35 | -0.01362 | -0.0034133 | 0.013623 | 0.0034153 | 3.5178e-06 | 1.9533e-06 | 0.020294 | 0.020294 | 0.020294 | 0.99864 | -0.026169 | 0.99892 | -0.020749 | 5.5752
36 | -0.035295 | -0.0088624 | 0.035301 | 0.0088662 | 6.4671e-06 | 3.8458e-06 | 0.054028 | 0.054028 | 0.054028 | 0.97218 | -0.53674 | 0.97237 | -0.5329 | 7.4215
37 | -0.21183 | -0.05419 | 0.21206 | 0.054337 | 0.00022904 | 0.00014627 | 0.31702 | 0.31702 | 0.31702 | 0.99551 | -0.085105 | 0.99668 | -0.062793 | 43.5474
38 | -0.23114 | -0.059118 | 0.23139 | 0.059279 | 0.00025262 | 0.00016138 | 0.3455 | 0.3455 | 0.3455 | 0.99668 | -0.062793 | 0.99787 | -0.040236 | 47.4595
39 | -0.23987 | -0.061403 | 0.23987 | 0.061407 | 5.7066e-06 | 3.646e-06 | 0.35814 | 0.35814 | 0.35814 | 0.99787 | -0.040236 | 0.9979 | -0.039745 | 49.1954
40 | -0.25098 | -0.06419 | 0.25146 | 0.064499 | 0.00048375 | 0.00030912 | 0.3747 | 0.3747 | 0.3747 | 0.9979 | -0.039745 | 1 | 0 | 51.4701
41 | 0.054523 | 0.013683 | -0.054521 | -0.013682 | 2.2894e-06 | 1.4531e-06 | 0.081137 | 0.081137 | 0.081137 | 1 | 0 | 0.99995 | -0.00088056 | 22.2904
42 | 0.046181 | 0.011592 | -0.046141 | -0.011566 | 4.025e-05 | 2.5462e-05 | 0.068728 | 0.068728 | 0.068728 | 0.99995 | -0.00088056 | 0.999 | -0.019172 | 18.8812
43 | 0.035926 | 0.009006 | -0.035924 | -0.0090043 | 2.6986e-06 | 1.6942e-06 | 0.053513 | 0.053513 | 0.053513 | 0.999 | -0.019172 | 0.99892 | -0.020749 | 14.7014
44 | 0.051507 | 0.012938 | -0.051492 | -0.012928 | 1.5311e-05 | 9.4722e-06 | 0.078781 | 0.078782 | 0.078782 | 0.97299 | -0.52072 | 0.97268 | -0.52695 | 10.8216
45 | 0.042928 | 0.010782 | -0.042918 | -0.010776 | 1.0077e-05 | 6.14e-06 | 0.065681 | 0.065681 | 0.065681 | 0.97268 | -0.52695 | 0.97243 | -0.53187 | 9.0221
46 | 0.038471 | 0.0096612 | -0.038469 | -0.0096601 | 1.8921e-06 | 1.1387e-06 | 0.058875 | 0.058875 | 0.058875 | 0.97243 | -0.53187 | 0.97237 | -0.5329 | 8.0873

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.32865 | 0.08345

## res_load
| p_mw | q_mvar
0 | 0.010415 | 0.0026102
1 | 0.0040836 | 0.0010234
2 | 0.0042716 | 0.0010706
3 | 0.0056355 | 0.0014124
4 | 0.012582 | 0.0031535
5 | 0.0092147 | 0.0023094
6 | 0.012879 | 0.0032277
7 | 0.010716 | 0.0026856
8 | 0.0095331 | 0.0023892
9 | 0.0026886 | 0.00067382
10 | 0.0082875 | 0.002077
11 | 0.007997 | 0.0020042
12 | 0.0029236 | 0.00073271
13 | 0.010034 | 0.0025146
14 | 0.016976 | 0.0042545
15 | 0.002997 | 0.00075111
16 | 0.0058775 | 0.001473
17 | 0.0102 | 0.0025563
18 | 0.0073619 | 0.0018451
19 | 0.010104 | 0.0025322
20 | 0.0031863 | 0.00079857
21 | 0.010433 | 0.0026148
22 | 0.0034288 | 0.00085935
23 | 0.0026986 | 0.00067632
24 | 0.0035274 | 0.00088405
25 | 0.011653 | 0.0029204
26 | 0.019076 | 0.004781
27 | 0.008475 | 0.002124
28 | 0.011106 | 0.0027834
29 | 0.021019 | 0.0052678
30 | 0.0083393 | 0.00209
31 | 0.010215 | 0.00256
32 | 0.022301 | 0.005589
33 | 0.0067027 | 0.0016799
34 | 0.0085637 | 0.0021463
35 | 0.0044474 | 0.0011146
36 | 0.0031675 | 0.00079385

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1