## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-723_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-723_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-723_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_261-723_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_261-723_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_261-723_0_3_node_36 | 0.4 | n |  | TRUE
6 | bus_LV_261-723_0_3_node_15 | 0.4 | n |  | TRUE
7 | bus_LV_261-723_0_3_node_8 | 0.4 | n |  | TRUE
8 | bus_LV_261-723_0_3_node_33 | 0.4 | n |  | TRUE
9 | bus_LV_261-723_0_3_node_34 | 0.4 | n |  | TRUE
10 | bus_LV_261-723_0_3_node_5 | 0.4 | n |  | TRUE
11 | bus_LV_261-723_0_3_node_6 | 0.4 | n |  | TRUE
12 | bus_LV_261-723_0_3_node_7 | 0.4 | n |  | TRUE
13 | bus_LV_261-723_0_3_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_261-723_0_3_node_10 | 0.4 | n |  | TRUE
15 | bus_LV_261-723_0_3_node_37 | 0.4 | n |  | TRUE
16 | bus_LV_261-723_0_3_node_21 | 0.4 | n |  | TRUE
17 | bus_LV_261-723_0_3_node_40 | 0.4 | n |  | TRUE
18 | bus_LV_261-723_0_3_node_11 | 0.4 | n |  | TRUE
19 | bus_LV_261-723_0_3_node_13 | 0.4 | n |  | TRUE
20 | bus_LV_261-723_0_3_node_30 | 0.4 | n |  | TRUE
21 | bus_LV_261-723_0_3_node_38 | 0.4 | n |  | TRUE
22 | bus_LV_261-723_0_3_node_16 | 0.4 | n |  | TRUE
23 | bus_LV_261-723_0_3_node_19 | 0.4 | n |  | TRUE
24 | bus_LV_261-723_0_3_node_18 | 0.4 | n |  | TRUE
25 | bus_LV_261-723_0_3_node_39 | 0.4 | n |  | TRUE
26 | bus_LV_261-723_0_3_node_46 | 0.4 | n |  | TRUE
27 | bus_LV_261-723_0_3_node_42 | 0.4 | n |  | TRUE
28 | bus_LV_261-723_0_3_node_22 | 0.4 | n |  | TRUE
29 | bus_LV_261-723_0_3_node_45 | 0.4 | n |  | TRUE
30 | bus_LV_261-723_0_3_node_43 | 0.4 | n |  | TRUE
31 | bus_LV_261-723_0_3_node_35 | 0.4 | n |  | TRUE
32 | bus_LV_261-723_0_3_node_29 | 0.4 | n |  | TRUE
33 | bus_LV_261-723_0_3_node_44 | 0.4 | n |  | TRUE
34 | bus_LV_261-723_0_3_node_32 | 0.4 | n |  | TRUE
35 | bus_LV_261-723_0_3_node_41 | 0.4 | n |  | TRUE
36 | bus_LV_261-723_0_3_node_31 | 0.4 | n |  | TRUE
37 | bus_LV_261-723_0_3_node_26 | 0.4 | n |  | TRUE
38 | bus_LV_261-723_0_3_node_23 | 0.4 | n |  | TRUE
39 | bus_LV_261-723_0_3_node_24 | 0.4 | n |  | TRUE
40 | bus_LV_261-723_0_3_node_25 | 0.4 | n |  | TRUE
41 | bus_LV_261-723_0_3_node_27 | 0.4 | n |  | TRUE
42 | bus_LV_261-723_0_3_node_28 | 0.4 | n |  | TRUE
43 | bus_MV_539_0_node_160 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-723_0_3_load_0 | 0 | 0.005363 | 0.0013441 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-723_0_3_load_1 | 1 | 0.0079442 | 0.001991 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-723_0_3_load_2 | 2 | 0.0046774 | 0.0011723 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-723_0_3_load_3 | 3 | 0.0047028 | 0.0011786 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-723_0_3_load_4 | 4 | 0.0084223 | 0.0021108 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-723_0_3_load_36 | 5 | 0.0095043 | 0.002382 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-723_0_3_load_33 | 8 | 0.0085594 | 0.0021452 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-723_0_3_load_34 | 9 | 0.011682 | 0.0029279 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-723_0_3_load_5 | 10 | 0.018477 | 0.0046309 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-723_0_3_load_6 | 11 | 0.0085151 | 0.0021341 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-723_0_3_load_9 | 13 | 0.040973 | 0.010269 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-723_0_3_load_37 | 15 | 0.008971 | 0.0022483 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-723_0_3_load_40 | 17 | 0.09278 | 0.023253 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-723_0_3_load_30 | 20 | 0.0052198 | 0.0013082 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-723_0_3_load_38 | 21 | 0.0048161 | 0.001207 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-723_0_3_load_39 | 25 | 0.034565 | 0.0086629 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-723_0_3_load_46 | 26 | 0.022863 | 0.0057301 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_261-723_0_3_load_42 | 27 | 0.0089354 | 0.0022394 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_261-723_0_3_load_45 | 29 | 0.0061418 | 0.0015393 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_261-723_0_3_load_35 | 31 | 0.0089243 | 0.0022366 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_261-723_0_3_load_29 | 32 | 0.0067727 | 0.0016974 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_261-723_0_3_load_44 | 33 | 0.0054888 | 0.0013756 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_261-723_0_3_load_32 | 34 | 0.0070315 | 0.0017623 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_261-723_0_3_load_41 | 35 | 0.0034668 | 0.00086887 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_261-723_0_3_load_31 | 36 | 0.0070966 | 0.0017786 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_261-723_0_3_load_26 | 37 | 0.011527 | 0.0028889 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_261-723_0_3_load_23 | 38 | 0.011208 | 0.0028089 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_261-723_0_3_load_24 | 39 | 0.0071228 | 0.0017851 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_261-723_0_3_load_25 | 40 | 0.0080304 | 0.0020126 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_261-723_0_3_load_27 | 41 | 0.006647 | 0.0016659 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_261-723_0_3_load_28 | 42 | 0.0072897 | 0.001827 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 13 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-723_0_3_line_0 |  | 0 | 1 | 0.007756 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-723_0_3_line_1 |  | 0 | 2 | 0.0012425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-723_0_3_line_2 |  | 1 | 3 | 0.0017149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-723_0_3_line_3 |  | 2 | 4 | 0.023945 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-723_0_3_line_4 |  | 3 | 5 | 0.019325 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_261-723_0_3_line_5 |  | 4 | 6 | 0.010941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_261-723_0_3_line_6 |  | 5 | 7 | 0.012422 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_261-723_0_3_line_7 |  | 6 | 8 | 0.022104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_261-723_0_3_line_8 |  | 6 | 9 | 0.019533 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_261-723_0_3_line_9 |  | 7 | 15 | 0.01493 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_261-723_0_3_line_10 |  | 7 | 11 | 0.02137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_261-723_0_3_line_11 |  | 8 | 34 | 0.017203 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_261-723_0_3_line_12 |  | 10 | 11 | 0.017875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-723_0_3_line_13 |  | 12 | 13 | 0.005698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
14 | LV_261-723_0_3_line_14 |  | 12 | 14 | 0.019978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
15 | LV_261-723_0_3_line_15 |  | 14 | 16 | 0.016345 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
16 | LV_261-723_0_3_line_16 |  | 14 | 17 | 0.0074066 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
17 | LV_261-723_0_3_line_17 |  | 15 | 21 | 0.0097951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_261-723_0_3_line_18 |  | 16 | 28 | 0.004536 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
19 | LV_261-723_0_3_line_19 |  | 16 | 29 | 0.025955 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_261-723_0_3_line_20 |  | 17 | 25 | 0.037069 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_261-723_0_3_line_21 |  | 18 | 19 | 0.011449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_261-723_0_3_line_22 |  | 18 | 20 | 0.01396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_261-723_0_3_line_23 |  | 19 | 21 | 0.028844 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_261-723_0_3_line_24 |  | 20 | 32 | 0.017004 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_261-723_0_3_line_25 |  | 22 | 23 | 0.039882 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_261-723_0_3_line_26 |  | 22 | 24 | 0.069327 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_261-723_0_3_line_27 |  | 22 | 25 | 0.0032186 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_261-723_0_3_line_28 |  | 23 | 27 | 0.0085206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_261-723_0_3_line_29 |  | 24 | 26 | 0.034333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_261-723_0_3_line_30 |  | 27 | 35 | 0.030323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_261-723_0_3_line_31 |  | 28 | 30 | 0.025397 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_261-723_0_3_line_32 |  | 28 | 31 | 0.016542 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
33 | LV_261-723_0_3_line_33 |  | 30 | 33 | 0.018467 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_261-723_0_3_line_34 |  | 31 | 37 | 0.012758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
35 | LV_261-723_0_3_line_35 |  | 32 | 42 | 0.010577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_261-723_0_3_line_36 |  | 34 | 36 | 0.020384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_261-723_0_3_line_37 |  | 37 | 39 | 0.017635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
38 | LV_261-723_0_3_line_38 |  | 38 | 39 | 0.012098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
39 | LV_261-723_0_3_line_39 |  | 38 | 40 | 0.018305 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
40 | LV_261-723_0_3_line_40 |  | 40 | 41 | 0.010134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
41 | LV_261-723_0_3_line_41 |  | 41 | 42 | 0.015415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-723_0_3_trafo_9 | 0.63 MVA 20/0.4 kV | 43 | 13 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2685312.3444 | 1246461.7276 | 2685306.0893 | 1246457.142
1 | 2685312.3444 | 1246461.7276 | 2685313.3465 | 1246462.4622
2 | 2685304.7063 | 1246456.128 | 2685306.0893 | 1246457.142
3 | 2685332.6582 | 1246476.6197 | 2685313.3465 | 1246462.4622
4 | 2685304.7063 | 1246456.128 | 2685289.1206 | 1246444.7021
5 | 2685341.4821 | 1246483.0885 | 2685332.6582 | 1246476.6197
6 | 2685279.1021 | 1246437.3576 | 2685289.1206 | 1246444.7021
7 | 2685341.4821 | 1246483.0885 | 2685331.4047 | 1246502.7612
8 | 2685341.4821 | 1246483.0885 | 2685347.3662 | 1246472.6766 | 2685351.5 | 1246466.3309
9 | 2685279.1021 | 1246437.3576 | 2685287.5979 | 1246425.0809
10 | 2685279.1021 | 1246437.3576 | 2685266.9539 | 1246454.9389
11 | 2685331.4047 | 1246502.7612 | 2685327.7932 | 1246509.8113 | 2685323.9745 | 1246518.2708
12 | 2685256.7923 | 1246469.6451 | 2685266.9539 | 1246454.9389
13 | 2685236.453 | 1246499.9797 | 2685241.4136 | 1246502.8086
14 | 2685228.2658 | 1246518.2088 | 2685234.4274 | 1246504.2426 | 2685236.453 | 1246499.9797
15 | 2685215.6391 | 1246508.409 | 2685221.3614 | 1246515.0072 | 2685228.2658 | 1246518.2088
16 | 2685228.2658 | 1246518.2088 | 2685225.1715 | 1246524.9381
17 | 2685293.1719 | 1246417.0264 | 2685287.5979 | 1246425.0809
18 | 2685218.3657 | 1246504.7789 | 2685215.6391 | 1246508.409
19 | 2685215.6391 | 1246508.409 | 2685209.1257 | 1246508.4822 | 2685205.9743 | 1246508.5592 | 2685202.9062 | 1246509.1378 | 2685200.655 | 1246510.184 | 2685198.6917 | 1246511.6902 | 2685197.6398 | 1246519.8326
20 | 2685209.6414 | 1246558.5949 | 2685214.7412 | 1246547.2137 | 2685216.6968 | 1246543.0832 | 2685220.9819 | 1246534.0492 | 2685225.1715 | 1246524.9381
21 | 2685300.6838 | 1246386.1078 | 2685305.5081 | 1246390.0134 | 2685309.5857 | 1246393.3078
22 | 2685300.6838 | 1246386.1078 | 2685292.676 | 1246397.543
23 | 2685309.5857 | 1246393.3078 | 2685293.1719 | 1246417.0264
24 | 2685282.9223 | 1246411.4715 | 2685292.676 | 1246397.543
25 | 2685175.1752 | 1246560.9889 | 2685178.2677 | 1246561.3336 | 2685181.4956 | 1246560.1457 | 2685189.3203 | 1246551.3516 | 2685199.6662 | 1246556.8932 | 2685208.3253 | 1246561.5321
26 | 2685208.3253 | 1246561.5321 | 2685200.1953 | 1246580.5293 | 2685198.8475 | 1246587.0481 | 2685199.2612 | 1246591.9021 | 2685200.3446 | 1246594.3194 | 2685203.2561 | 1246598.3198 | 2685206.7041 | 1246602.3056 | 2685226.5922 | 1246616.2127
27 | 2685208.3253 | 1246561.5321 | 2685209.6414 | 1246558.5949
28 | 2685175.1752 | 1246560.9889 | 2685168.9247 | 1246555.1982
29 | 2685245.8355 | 1246587.746 | 2685226.5922 | 1246616.2127
30 | 2685147.8936 | 1246533.3861 | 2685153.4606 | 1246539.5835 | 2685161.7404 | 1246548.5424 | 2685168.9247 | 1246555.1982
31 | 2685201.7793 | 1246486.6272 | 2685203.8962 | 1246491.7725 | 2685206.9213 | 1246496.286 | 2685212.6365 | 1246501.8055 | 2685218.3657 | 1246504.7789
32 | 2685218.3657 | 1246504.7789 | 2685224.8762 | 1246495.4433 | 2685227.8066 | 1246491.1953
33 | 2685201.7793 | 1246486.6272 | 2685200.8642 | 1246482.4888 | 2685200.434 | 1246474.5768 | 2685200.3292 | 1246468.2726
34 | 2685227.8066 | 1246491.1953 | 2685235.0512 | 1246480.6934
35 | 2685282.9223 | 1246411.4715 | 2685276.855 | 1246420.1357
36 | 2685323.9745 | 1246518.2708 | 2685322.2526 | 1246522.0851 | 2685315.2752 | 1246536.7049
37 | 2685245.0648 | 1246466.1775 | 2685235.0512 | 1246480.6934
38 | 2685251.9343 | 1246456.2193 | 2685245.0648 | 1246466.1775
39 | 2685251.9343 | 1246456.2193 | 2685262.3283 | 1246441.1518
40 | 2685262.3283 | 1246441.1518 | 2685268.0825 | 1246432.8105
41 | 2685268.0825 | 1246432.8105 | 2685274.9053 | 1246422.9199 | 2685276.855 | 1246420.1357

## bus_geodata
| x | y | coords
0 | 2685312.3444 | 1246461.7276
1 | 2685306.0893 | 1246457.142
2 | 2685313.3465 | 1246462.4622
3 | 2685304.7063 | 1246456.128
4 | 2685332.6582 | 1246476.6197
5 | 2685289.1206 | 1246444.7021
6 | 2685341.4821 | 1246483.0885
7 | 2685279.1021 | 1246437.3576
8 | 2685331.4047 | 1246502.7612
9 | 2685351.5 | 1246466.3309
10 | 2685256.7923 | 1246469.6451
11 | 2685266.9539 | 1246454.9389
12 | 2685236.453 | 1246499.9797
13 | 2685241.4136 | 1246502.8086
14 | 2685228.2658 | 1246518.2088
15 | 2685287.5979 | 1246425.0809
16 | 2685215.6391 | 1246508.4091
17 | 2685225.1715 | 1246524.9381
18 | 2685300.6838 | 1246386.1078
19 | 2685309.5857 | 1246393.3078
20 | 2685292.676 | 1246397.543
21 | 2685293.1719 | 1246417.0264
22 | 2685208.3253 | 1246561.5321
23 | 2685175.1752 | 1246560.9889
24 | 2685226.5922 | 1246616.2127
25 | 2685209.6414 | 1246558.5949
26 | 2685245.8355 | 1246587.746
27 | 2685168.9247 | 1246555.1982
28 | 2685218.3657 | 1246504.7789
29 | 2685197.6398 | 1246519.8326
30 | 2685201.7793 | 1246486.6272
31 | 2685227.8066 | 1246491.1953
32 | 2685282.9223 | 1246411.4715
33 | 2685200.3292 | 1246468.2726
34 | 2685323.9745 | 1246518.2708
35 | 2685147.8936 | 1246533.3861
36 | 2685315.2752 | 1246536.7049
37 | 2685235.0512 | 1246480.6934
38 | 2685251.9343 | 1246456.2193
39 | 2685245.0648 | 1246466.1775
40 | 2685262.3283 | 1246441.1518
41 | 2685268.0825 | 1246432.8105
42 | 2685276.855 | 1246420.1357
43 | 2685236.453 | 1246499.9797

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97528 | -0.47629 | 0.005363 | 0.0013441
1 | 0.97566 | -0.46878 | 0.0079442 | 0.001991
2 | 0.97523 | -0.47737 | 0.0046774 | 0.0011723
3 | 0.97576 | -0.46688 | 0.0047028 | 0.0011786
4 | 0.97427 | -0.49617 | 0.0084223 | 0.0021108
5 | 0.97694 | -0.44374 | 0.0095043 | 0.002382
6 | 0.97392 | -0.50308 | 0 | 0
7 | 0.9778 | -0.42674 | 0 | 0
8 | 0.97345 | -0.5123 | 0.0085594 | 0.0021452
9 | 0.97371 | -0.50727 | 0.011682 | 0.0029279
10 | 0.97696 | -0.44329 | 0.018477 | 0.0046309
11 | 0.97727 | -0.43726 | 0.0085151 | 0.0021341
12 | 0.99937 | -0.012017 | 0 | 0
13 | 1 | 0 | -0.36834 | -0.093425
14 | 0.99715 | -0.054271 | 0 | 0
15 | 0.97922 | -0.39902 | 0.008971 | 0.0022483
16 | 0.99614 | -0.073406 | 0 | 0
17 | 0.9966 | -0.064834 | 0.09278 | 0.023253
18 | 0.98457 | -0.29505 | 0 | 0
19 | 0.98333 | -0.31891 | 0 | 0
20 | 0.98607 | -0.26603 | 0.0052198 | 0.0013082
21 | 0.98023 | -0.37929 | 0.0048161 | 0.001207
22 | 0.99413 | -0.11237 | 0 | 0
23 | 0.99368 | -0.1211 | 0 | 0
24 | 0.99268 | -0.14037 | 0 | 0
25 | 0.99424 | -0.11037 | 0.034565 | 0.0086629
26 | 0.99197 | -0.15426 | 0.022863 | 0.0057301
27 | 0.99359 | -0.12297 | 0.0089354 | 0.0022394
28 | 0.99587 | -0.07856 | 0 | 0
29 | 0.996 | -0.076207 | 0.0061418 | 0.0015393
30 | 0.99574 | -0.081011 | 0 | 0
31 | 0.99491 | -0.096847 | 0.0089243 | 0.0022366
32 | 0.98798 | -0.22922 | 0.0067727 | 0.0016974
33 | 0.99565 | -0.082793 | 0.0054888 | 0.0013756
34 | 0.97323 | -0.51677 | 0.0070315 | 0.0017623
35 | 0.99349 | -0.12482 | 0.0034668 | 0.00086887
36 | 0.97309 | -0.51943 | 0.0070966 | 0.0017786
37 | 0.9942 | -0.11031 | 0.011527 | 0.0028889
38 | 0.99269 | -0.13921 | 0.011208 | 0.0028089
39 | 0.99329 | -0.12774 | 0.0071228 | 0.0017851
40 | 0.99184 | -0.15539 | 0.0080304 | 0.0020126
41 | 0.99117 | -0.16812 | 0.006647 | 0.0016659
42 | 0.98924 | -0.20512 | 0.0072897 | 0.001827
43 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.052901 | -0.013283 | 0.05292 | 0.013295 | 1.8952e-05 | 1.2032e-05 | 0.080722 | 0.080722 | 0.080722 | 0.97528 | -0.47629 | 0.97566 | -0.46878 | 22.1763
1 | 0.047538 | 0.011939 | -0.047535 | -0.011938 | 2.4517e-06 | 1.5536e-06 | 0.072539 | 0.072539 | 0.072539 | 0.97528 | -0.47629 | 0.97523 | -0.47737 | 19.9283
2 | -0.060864 | -0.015286 | 0.06087 | 0.01529 | 5.5426e-06 | 3.5258e-06 | 0.092838 | 0.092838 | 0.092838 | 0.97566 | -0.46878 | 0.97576 | -0.46688 | 25.5048
3 | 0.042858 | 0.010766 | -0.04282 | -0.010741 | 3.8409e-05 | 2.4283e-05 | 0.065402 | 0.065402 | 0.065402 | 0.97523 | -0.47737 | 0.97427 | -0.49617 | 17.9677
4 | -0.065572 | -0.016469 | 0.065645 | 0.016515 | 7.2483e-05 | 4.6147e-05 | 0.10001 | 0.10001 | 0.10001 | 0.97576 | -0.46688 | 0.97694 | -0.44374 | 27.475
5 | 0.034397 | 0.0086304 | -0.034386 | -0.0086233 | 1.1325e-05 | 7.1121e-06 | 0.052539 | 0.052539 | 0.052539 | 0.97427 | -0.49617 | 0.97392 | -0.50308 | 14.4338
6 | -0.075149 | -0.018897 | 0.07521 | 0.018936 | 6.1056e-05 | 3.892e-05 | 0.11449 | 0.11449 | 0.11449 | 0.97694 | -0.44374 | 0.9778 | -0.42674 | 31.4521
7 | 0.022701 | 0.0056942 | -0.022691 | -0.0056881 | 9.9726e-06 | 6.1076e-06 | 0.034686 | 0.034686 | 0.034686 | 0.97392 | -0.50308 | 0.97345 | -0.5123 | 9.5292
8 | 0.011685 | 0.0029291 | -0.011682 | -0.0029279 | 2.3346e-06 | 1.2511e-06 | 0.017853 | 0.017853 | 0.017853 | 0.97392 | -0.50308 | 0.97371 | -0.50727 | 4.9046
9 | -0.10222 | -0.025712 | 0.10236 | 0.025799 | 0.00013554 | 8.6558e-05 | 0.15559 | 0.15559 | 0.15559 | 0.9778 | -0.42674 | 0.97922 | -0.39902 | 42.7455
10 | 0.027011 | 0.0067765 | -0.026998 | -0.0067681 | 1.3542e-05 | 8.3992e-06 | 0.041108 | 0.041108 | 0.041108 | 0.9778 | -0.42674 | 0.97727 | -0.43726 | 11.2935
11 | 0.014132 | 0.0035429 | -0.014129 | -0.0035412 | 3.0105e-06 | 1.7129e-06 | 0.021603 | 0.021603 | 0.021603 | 0.97345 | -0.5123 | 0.97323 | -0.51677 | 5.9348
12 | -0.018477 | -0.0046309 | 0.018483 | 0.004634 | 5.3092e-06 | 3.174e-06 | 0.028143 | 0.028143 | 0.028143 | 0.97696 | -0.44329 | 0.97727 | -0.43726 | 7.7316
13 | -0.36648 | -0.093289 | 0.36669 | 0.093424 | 0.00021247 | 0.00013576 | 0.54618 | 0.54618 | 0.54618 | 0.99937 | -0.012017 | 1 | 0 | 50.0166
14 | 0.36648 | 0.093289 | -0.36573 | -0.092813 | 0.00074496 | 0.00047599 | 0.54618 | 0.54618 | 0.54618 | 0.99937 | -0.012017 | 0.99715 | -0.054271 | 50.0166
15 | 0.20283 | 0.051876 | -0.20265 | -0.051757 | 0.00018764 | 0.00011945 | 0.30305 | 0.30305 | 0.30305 | 0.99715 | -0.054271 | 0.99614 | -0.073406 | 27.752
16 | 0.1629 | 0.040937 | -0.16282 | -0.040884 | 8.2092e-05 | 5.2346e-05 | 0.24313 | 0.24313 | 0.24313 | 0.99715 | -0.054271 | 0.9966 | -0.064834 | 33.3971
17 | -0.11133 | -0.028047 | 0.11143 | 0.028114 | 0.00010519 | 6.7198e-05 | 0.16923 | 0.16923 | 0.16923 | 0.97922 | -0.39902 | 0.98023 | -0.37929 | 46.4906
18 | 0.1965 | 0.050217 | -0.19645 | -0.050186 | 4.8968e-05 | 3.1162e-05 | 0.29388 | 0.29388 | 0.29388 | 0.99614 | -0.073406 | 0.99587 | -0.07856 | 26.9117
19 | 0.0061426 | 0.0015395 | -0.0061418 | -0.0015393 | 8.1949e-07 | 1.8663e-07 | 0.0091757 | 0.0091758 | 0.0091758 | 0.99614 | -0.073406 | 0.996 | -0.076207 | 2.5208
20 | 0.070039 | 0.017631 | -0.069887 | -0.017535 | 0.0001521 | 9.6859e-05 | 0.1046 | 0.1046 | 0.1046 | 0.9966 | -0.064834 | 0.99424 | -0.11037 | 28.7368
21 | 0.11672 | 0.029622 | -0.11659 | -0.029537 | 0.00013381 | 8.549e-05 | 0.17654 | 0.17654 | 0.17654 | 0.98457 | -0.29505 | 0.98333 | -0.31891 | 48.499
22 | -0.11672 | -0.029622 | 0.11688 | 0.029726 | 0.00016315 | 0.00010424 | 0.17654 | 0.17654 | 0.17654 | 0.98457 | -0.29505 | 0.98607 | -0.26603 | 48.499
23 | 0.11659 | 0.029537 | -0.11625 | -0.029321 | 0.0003371 | 0.00021538 | 0.17654 | 0.17654 | 0.17654 | 0.98333 | -0.31891 | 0.98023 | -0.37929 | 48.4991
24 | -0.1221 | -0.031035 | 0.12232 | 0.031173 | 0.00021685 | 0.00013857 | 0.18441 | 0.18441 | 0.18441 | 0.98607 | -0.26603 | 0.98798 | -0.22922 | 50.663
25 | 0.012409 | 0.0031115 | -0.012404 | -0.0031087 | 5.1597e-06 | 2.7854e-06 | 0.018574 | 0.018574 | 0.018574 | 0.99413 | -0.11237 | 0.99368 | -0.1211 | 5.1028
26 | 0.022909 | 0.005758 | -0.022879 | -0.0057394 | 3.0579e-05 | 1.8673e-05 | 0.034296 | 0.034296 | 0.034296 | 0.99413 | -0.11237 | 0.99268 | -0.14037 | 9.4221
27 | -0.035318 | -0.0088695 | 0.035321 | 0.0088716 | 3.3738e-06 | 2.1175e-06 | 0.05287 | 0.05287 | 0.05287 | 0.99413 | -0.11237 | 0.99424 | -0.11037 | 14.5247
28 | 0.012404 | 0.0031087 | -0.012403 | -0.0031081 | 1.1024e-06 | 5.9514e-07 | 0.018574 | 0.018574 | 0.018574 | 0.99368 | -0.1211 | 0.99359 | -0.12297 | 5.1028
29 | 0.022879 | 0.0057394 | -0.022863 | -0.0057301 | 1.5144e-05 | 9.2487e-06 | 0.034296 | 0.034297 | 0.034297 | 0.99268 | -0.14037 | 0.99197 | -0.15426 | 9.4221
30 | 0.0034671 | 0.00086868 | -0.0034668 | -0.00086887 | 3.0659e-07 | -1.9648e-07 | 0.0051924 | 0.0051925 | 0.0051925 | 0.99359 | -0.12297 | 0.99349 | -0.12482 | 1.4265
31 | 0.0054899 | 0.0013758 | -0.0054892 | -0.0013757 | 6.4085e-07 | 7.9735e-08 | 0.0082028 | 0.008203 | 0.008203 | 0.99587 | -0.07856 | 0.99574 | -0.081011 | 2.2536
32 | 0.19096 | 0.04881 | -0.19079 | -0.048703 | 0.00016875 | 0.00010736 | 0.28567 | 0.28567 | 0.28567 | 0.99587 | -0.07856 | 0.99491 | -0.096847 | 26.1606
33 | 0.0054892 | 0.0013757 | -0.0054888 | -0.0013756 | 4.6599e-07 | 5.8038e-08 | 0.008203 | 0.008203 | 0.008203 | 0.99574 | -0.081011 | 0.99565 | -0.082793 | 2.2536
34 | 0.18187 | 0.046466 | -0.18175 | -0.046391 | 0.00011827 | 7.5197e-05 | 0.27233 | 0.27233 | 0.27233 | 0.99491 | -0.096847 | 0.9942 | -0.11031 | 24.9383
35 | -0.12909 | -0.032871 | 0.12924 | 0.032967 | 0.00015023 | 9.6011e-05 | 0.19461 | 0.19461 | 0.19461 | 0.98798 | -0.22922 | 0.98924 | -0.20512 | 53.4652
36 | 0.0070975 | 0.0017789 | -0.0070966 | -0.0017786 | 9.0019e-07 | 3.2286e-07 | 0.010852 | 0.010852 | 0.010852 | 0.97323 | -0.51677 | 0.97309 | -0.51943 | 2.9813
37 | 0.17023 | 0.043502 | -0.17008 | -0.043411 | 0.00014342 | 9.1104e-05 | 0.25507 | 0.25507 | 0.25507 | 0.9942 | -0.11031 | 0.99329 | -0.12774 | 23.3585
38 | -0.16287 | -0.041569 | 0.16296 | 0.041626 | 9.033e-05 | 5.7342e-05 | 0.2444 | 0.2444 | 0.2444 | 0.99269 | -0.13921 | 0.99329 | -0.12774 | 22.3814
39 | 0.15166 | 0.03876 | -0.15154 | -0.038685 | 0.00011853 | 7.5151e-05 | 0.2276 | 0.2276 | 0.2276 | 0.99269 | -0.13921 | 0.99184 | -0.15539 | 20.8429
40 | 0.14351 | 0.036672 | -0.14342 | -0.036616 | 8.8285e-05 | 5.6241e-05 | 0.21556 | 0.21556 | 0.21556 | 0.99184 | -0.15539 | 0.99117 | -0.16812 | 29.6095
41 | 0.13678 | 0.03495 | -0.13653 | -0.034794 | 0.0002443 | 0.00015615 | 0.20558 | 0.20558 | 0.20558 | 0.99117 | -0.16812 | 0.98924 | -0.20512 | 56.4776

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.40931 | 0.10369

## res_load
| p_mw | q_mvar
0 | 0.005363 | 0.0013441
1 | 0.0079442 | 0.001991
2 | 0.0046774 | 0.0011723
3 | 0.0047028 | 0.0011786
4 | 0.0084223 | 0.0021108
5 | 0.0095043 | 0.002382
6 | 0.0085594 | 0.0021452
7 | 0.011682 | 0.0029279
8 | 0.018477 | 0.0046309
9 | 0.0085151 | 0.0021341
10 | 0.040973 | 0.010269
11 | 0.008971 | 0.0022483
12 | 0.09278 | 0.023253
13 | 0.0052198 | 0.0013082
14 | 0.0048161 | 0.001207
15 | 0.034565 | 0.0086629
16 | 0.022863 | 0.0057301
17 | 0.0089354 | 0.0022394
18 | 0.0061418 | 0.0015393
19 | 0.0089243 | 0.0022366
20 | 0.0067727 | 0.0016974
21 | 0.0054888 | 0.0013756
22 | 0.0070315 | 0.0017623
23 | 0.0034668 | 0.00086887
24 | 0.0070966 | 0.0017786
25 | 0.011527 | 0.0028889
26 | 0.011208 | 0.0028089
27 | 0.0071228 | 0.0017851
28 | 0.0080304 | 0.0020126
29 | 0.006647 | 0.0016659
30 | 0.0072897 | 0.001827

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1