## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-724_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-724_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-724_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_261-724_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_261-724_0_4_node_19 | 0.4 | n |  | TRUE
5 | bus_LV_261-724_0_4_node_6 | 0.4 | n |  | TRUE
6 | bus_LV_261-724_0_4_node_4 | 0.4 | n |  | TRUE
7 | bus_LV_261-724_0_4_node_49 | 0.4 | n |  | TRUE
8 | bus_LV_261-724_0_4_node_5 | 0.4 | n |  | TRUE
9 | bus_LV_261-724_0_4_node_32 | 0.4 | n |  | TRUE
10 | bus_LV_261-724_0_4_node_29 | 0.4 | n |  | TRUE
11 | bus_LV_261-724_0_4_node_28 | 0.4 | n |  | TRUE
12 | bus_LV_261-724_0_4_node_48 | 0.4 | n |  | TRUE
13 | bus_LV_261-724_0_4_node_47 | 0.4 | n |  | TRUE
14 | bus_LV_261-724_0_4_node_7 | 0.4 | n |  | TRUE
15 | bus_LV_261-724_0_4_node_39 | 0.4 | n |  | TRUE
16 | bus_LV_261-724_0_4_node_40 | 0.4 | n |  | TRUE
17 | bus_LV_261-724_0_4_node_38 | 0.4 | n |  | TRUE
18 | bus_LV_261-724_0_4_node_8 | 0.4 | n |  | TRUE
19 | bus_LV_261-724_0_4_node_18 | 0.4 | n |  | TRUE
20 | bus_LV_261-724_0_4_node_46 | 0.4 | n |  | TRUE
21 | bus_LV_261-724_0_4_node_9 | 0.4 | n |  | TRUE
22 | bus_LV_261-724_0_4_node_37 | 0.4 | n |  | TRUE
23 | bus_LV_261-724_0_4_node_10 | 0.4 | n |  | TRUE
24 | bus_LV_261-724_0_4_node_36 | 0.4 | n |  | TRUE
25 | bus_LV_261-724_0_4_node_13 | 0.4 | n |  | TRUE
26 | bus_LV_261-724_0_4_node_27 | 0.4 | n |  | TRUE
27 | bus_LV_261-724_0_4_node_12 | 0.4 | n |  | TRUE
28 | bus_LV_261-724_0_4_node_23 | 0.4 | n |  | TRUE
29 | bus_LV_261-724_0_4_node_20 | 0.4 | n |  | TRUE
30 | bus_LV_261-724_0_4_node_25 | 0.4 | n |  | TRUE
31 | bus_LV_261-724_0_4_node_15 | 0.4 | n |  | TRUE
32 | bus_LV_261-724_0_4_node_35 | 0.4 | n |  | TRUE
33 | bus_LV_261-724_0_4_node_17 | 0.4 | n |  | TRUE
34 | bus_LV_261-724_0_4_node_42 | 0.4 | n |  | TRUE
35 | bus_LV_261-724_0_4_node_41 | 0.4 | n |  | TRUE
36 | bus_LV_261-724_0_4_node_31 | 0.4 | n |  | TRUE
37 | bus_LV_261-724_0_4_node_43 | 0.4 | n |  | TRUE
38 | bus_LV_261-724_0_4_node_44 | 0.4 | n |  | TRUE
39 | bus_LV_261-724_0_4_node_22 | 0.4 | n |  | TRUE
40 | bus_LV_261-724_0_4_node_21 | 0.4 | n |  | TRUE
41 | bus_LV_261-724_0_4_node_26 | 0.4 | n |  | TRUE
42 | bus_LV_261-724_0_4_node_34 | 0.4 | n |  | TRUE
43 | bus_LV_261-724_0_4_node_45 | 0.4 | n |  | TRUE
44 | bus_LV_261-724_0_4_node_30 | 0.4 | n |  | TRUE
45 | bus_LV_261-724_0_4_node_33 | 0.4 | n |  | TRUE
46 | bus_MV_539_0_node_27 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-724_0_4_load_0 | 0 | 0.0092503 | 0.0023183 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-724_0_4_load_19 | 4 | 0.0059401 | 0.0014887 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-724_0_4_load_49 | 7 | 0.003843 | 0.00096314 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-724_0_4_load_32 | 9 | 0.0097543 | 0.0024447 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-724_0_4_load_29 | 10 | 0.031657 | 0.0079339 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-724_0_4_load_28 | 11 | 0.0322 | 0.00807 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-724_0_4_load_48 | 12 | 0.022094 | 0.0055372 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-724_0_4_load_47 | 13 | 0.032108 | 0.008047 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-724_0_4_load_39 | 15 | 0.053916 | 0.013513 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-724_0_4_load_40 | 16 | 0.028104 | 0.0070435 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-724_0_4_load_38 | 17 | 0.030551 | 0.0076568 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-724_0_4_load_46 | 20 | 0.014567 | 0.0036508 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-724_0_4_load_37 | 22 | 0.030723 | 0.0076999 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-724_0_4_load_36 | 24 | 0.011077 | 0.0027762 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-724_0_4_load_27 | 26 | 0.0082964 | 0.0020793 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-724_0_4_load_23 | 28 | 0.021456 | 0.0053775 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-724_0_4_load_20 | 29 | 0.0066791 | 0.0016739 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_261-724_0_4_load_25 | 30 | 0.0070848 | 0.0017756 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_261-724_0_4_load_42 | 34 | 0.020567 | 0.0051545 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_261-724_0_4_load_41 | 35 | 0.014875 | 0.0037279 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_261-724_0_4_load_43 | 37 | 0.023651 | 0.0059276 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_261-724_0_4_load_44 | 38 | 0.028516 | 0.0071468 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_261-724_0_4_load_22 | 39 | 0.016125 | 0.0040414 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_261-724_0_4_load_21 | 40 | 0.027802 | 0.006968 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_261-724_0_4_load_26 | 41 | 0.0068769 | 0.0017235 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_261-724_0_4_load_34 | 42 | 0.016593 | 0.0041585 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_261-724_0_4_load_45 | 43 | 0.018229 | 0.0045686 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_261-724_0_4_load_30 | 44 | 0.0087735 | 0.0021988 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_261-724_0_4_load_33 | 45 | 0.007185 | 0.0018007 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 37 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-724_0_4_line_0 |  | 0 | 1 | 0.06005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-724_0_4_line_1 |  | 0 | 2 | 0.013044 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-724_0_4_line_2 |  | 1 | 3 | 0.060774 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-724_0_4_line_3 |  | 2 | 4 | 0.063147 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-724_0_4_line_4 |  | 2 | 5 | 0.013516 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_261-724_0_4_line_5 |  | 2 | 6 | 0.014509 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_261-724_0_4_line_6 |  | 3 | 7 | 0.046083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_261-724_0_4_line_7 |  | 5 | 12 | 0.024848 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_261-724_0_4_line_8 |  | 5 | 13 | 0.059456 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_261-724_0_4_line_9 |  | 6 | 8 | 0.025881 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_261-724_0_4_line_10 |  | 6 | 9 | 0.02571 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_261-724_0_4_line_11 |  | 8 | 10 | 0.016705 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_261-724_0_4_line_12 |  | 8 | 11 | 0.024206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-724_0_4_line_13 |  | 9 | 36 | 0.018162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_261-724_0_4_line_14 |  | 10 | 35 | 0.025076 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
15 | LV_261-724_0_4_line_15 |  | 14 | 15 | 0.028763 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
16 | LV_261-724_0_4_line_16 |  | 14 | 16 | 0.010555 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
17 | LV_261-724_0_4_line_17 |  | 14 | 17 | 0.012216 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
18 | LV_261-724_0_4_line_18 |  | 15 | 37 | 0.019018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
19 | LV_261-724_0_4_line_19 |  | 16 | 38 | 0.01122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
20 | LV_261-724_0_4_line_20 |  | 17 | 22 | 0.015347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
21 | LV_261-724_0_4_line_21 |  | 18 | 19 | 0.00656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_261-724_0_4_line_22 |  | 18 | 20 | 0.0028816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_261-724_0_4_line_23 |  | 19 | 33 | 0.0098295 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_261-724_0_4_line_24 |  | 21 | 22 | 0.0066971 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_261-724_0_4_line_25 |  | 21 | 23 | 0.030246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_261-724_0_4_line_26 |  | 21 | 24 | 0.010106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_261-724_0_4_line_27 |  | 23 | 25 | 0.008794 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_261-724_0_4_line_28 |  | 23 | 26 | 0.018705 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_261-724_0_4_line_29 |  | 24 | 31 | 0.017097 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_261-724_0_4_line_30 |  | 25 | 30 | 0.025929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_261-724_0_4_line_31 |  | 26 | 39 | 0.01263 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_261-724_0_4_line_32 |  | 27 | 28 | 0.015208 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_261-724_0_4_line_33 |  | 27 | 29 | 0.028683 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_261-724_0_4_line_34 |  | 29 | 40 | 0.0052175 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_261-724_0_4_line_35 |  | 30 | 41 | 0.011111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_261-724_0_4_line_36 |  | 31 | 32 | 0.024138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_261-724_0_4_line_37 |  | 32 | 42 | 0.012674 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_261-724_0_4_line_38 |  | 33 | 34 | 0.015242 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
39 | LV_261-724_0_4_line_39 |  | 33 | 35 | 0.016801 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
40 | LV_261-724_0_4_line_40 |  | 34 | 43 | 0.011337 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
41 | LV_261-724_0_4_line_41 |  | 36 | 45 | 0.0045186 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_261-724_0_4_line_42 |  | 36 | 44 | 0.0051822 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_261-724_0_4_line_43 |  | 38 | 43 | 0.018325 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
44 | LV_261-724_0_4_line_44 |  | 39 | 40 | 0.012796 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-724_0_4_trafo_43 | 0.63 MVA 20/0.4 kV | 46 | 37 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2684361.0112 | 1246349.9202 | 2684361.2281 | 1246351.1353 | 2684361.721 | 1246352.0652 | 2684362.9563 | 1246352.8612 | 2684401.4212 | 1246374.4465 | 2684412.043 | 1246380.4201
1 | 2684423.5048 | 1246386.6253 | 2684421.8075 | 1246385.9117 | 2684412.043 | 1246380.4201
2 | 2684361.0112 | 1246349.9202 | 2684361.5148 | 1246347.4478 | 2684365.3098 | 1246337.728 | 2684371.3113 | 1246323.7252 | 2684377.0062 | 1246312.1644 | 2684384.5419 | 1246299.1954 | 2684386.792 | 1246295.0466
3 | 2684423.5048 | 1246386.6253 | 2684425.3423 | 1246386.5069 | 2684426.6365 | 1246385.8137 | 2684427.589 | 1246384.7153 | 2684457.7795 | 1246334.7437
4 | 2684423.5048 | 1246386.6253 | 2684428.8259 | 1246389.6366 | 2684435.2713 | 1246393.2754
5 | 2684423.5048 | 1246386.6253 | 2684428.8259 | 1246389.6366 | 2684426.4198 | 1246393.6052 | 2684424.5676 | 1246396.8702
6 | 2684386.792 | 1246295.0466 | 2684411.3039 | 1246313.3866 | 2684421.5041 | 1246301.6565
7 | 2684435.2713 | 1246393.2754 | 2684436.8647 | 1246394.3878 | 2684456.7798 | 1246405.7028
8 | 2684435.2713 | 1246393.2754 | 2684434.3056 | 1246391.5938 | 2684434.1323 | 1246389.9679 | 2684434.5704 | 1246388.3841 | 2684462.6322 | 1246341.9694
9 | 2684424.5676 | 1246396.8702 | 2684430.8181 | 1246400.4062 | 2684447.0886 | 1246409.6224
10 | 2684424.5676 | 1246396.8702 | 2684411.8748 | 1246419.2287
11 | 2684447.0886 | 1246409.6224 | 2684461.6603 | 1246417.7905
12 | 2684447.0886 | 1246409.6224 | 2684434.977 | 1246430.5803
13 | 2684402.9082 | 1246435.0233 | 2684411.8748 | 1246419.2287
14 | 2684483.5338 | 1246430.0516 | 2684461.6603 | 1246417.7905
15 | 2684450.7354 | 1246486.6643 | 2684430.2548 | 1246466.469
16 | 2684450.7354 | 1246486.6643 | 2684458.2827 | 1246479.285
17 | 2684450.7354 | 1246486.6643 | 2684443.716 | 1246493.0914 | 2684441.5329 | 1246494.6778
18 | 2684430.2548 | 1246466.469 | 2684443.1089 | 1246452.4528
19 | 2684458.2827 | 1246479.285 | 2684466.305 | 1246471.4412
20 | 2684429.096 | 1246503.6693 | 2684430.1049 | 1246502.9827 | 2684441.5329 | 1246494.6778
21 | 2684508.8549 | 1246427.3151 | 2684504.3296 | 1246432.0763
22 | 2684508.8549 | 1246427.3151 | 2684509.9057 | 1246426.207 | 2684510.8577 | 1246425.2436
23 | 2684504.3296 | 1246432.0763 | 2684501.016 | 1246435.5761 | 2684497.5645 | 1246439.2074
24 | 2684423.5594 | 1246507.4372 | 2684429.096 | 1246503.6693
25 | 2684423.5594 | 1246507.4372 | 2684423.9367 | 1246507.9986 | 2684427.7758 | 1246513.7463 | 2684432.8798 | 1246521.3802 | 2684433.516 | 1246522.3344 | 2684434.7622 | 1246521.2958 | 2684438.8891 | 1246517.9743 | 2684442.8623 | 1246514.3059
26 | 2684423.5594 | 1246507.4372 | 2684416.2727 | 1246511.9479 | 2684414.8832 | 1246512.6039
27 | 2684442.8623 | 1246514.3059 | 2684446.1378 | 1246518.7781 | 2684447.7215 | 1246521.625
28 | 2684442.8623 | 1246514.3059 | 2684456.1411 | 1246501.1326
29 | 2684399.3961 | 1246519.8469 | 2684404.7954 | 1246517.3664 | 2684414.8832 | 1246512.6039
30 | 2684447.7215 | 1246521.625 | 2684452.7202 | 1246520.2173 | 2684458.671 | 1246521.4474 | 2684472.0999 | 1246527.3273
31 | 2684465.0852 | 1246492.2155 | 2684456.4644 | 1246500.8119 | 2684456.1411 | 1246501.1326
32 | 2684499.1899 | 1246460.3239 | 2684510.6759 | 1246470.2917
33 | 2684499.1899 | 1246460.3239 | 2684478.1328 | 1246479.7999
34 | 2684478.1328 | 1246479.7999 | 2684474.3024 | 1246483.3426
35 | 2684472.0999 | 1246527.3273 | 2684482.2777 | 1246531.7837
36 | 2684390.3545 | 1246497.4574 | 2684399.3961 | 1246519.8469
37 | 2684390.3545 | 1246497.4574 | 2684395.5487 | 1246495.5854 | 2684399.9915 | 1246489.9802
38 | 2684497.5645 | 1246439.2074 | 2684494.6498 | 1246442.2793 | 2684487.0811 | 1246450.272
39 | 2684497.5645 | 1246439.2074 | 2684491.6842 | 1246434.6203 | 2684483.5338 | 1246430.0516
40 | 2684479.1663 | 1246458.3878 | 2684485.7982 | 1246451.6267 | 2684487.0811 | 1246450.272
41 | 2684402.9082 | 1246435.0233 | 2684406.9096 | 1246437.1227
42 | 2684402.9082 | 1246435.0233 | 2684398.3178 | 1246432.6185
43 | 2684466.305 | 1246471.4412 | 2684467.7058 | 1246470.0715 | 2684479.1663 | 1246458.3878
44 | 2684465.0852 | 1246492.2155 | 2684469.8989 | 1246487.4155 | 2684474.3024 | 1246483.3426

## bus_geodata
| x | y | coords
0 | 2684412.043 | 1246380.4201
1 | 2684361.0112 | 1246349.9202
2 | 2684423.5048 | 1246386.6253
3 | 2684386.792 | 1246295.0466
4 | 2684457.7795 | 1246334.7437
5 | 2684435.2713 | 1246393.2754
6 | 2684424.5676 | 1246396.8702
7 | 2684421.5041 | 1246301.6565
8 | 2684447.0886 | 1246409.6224
9 | 2684411.8748 | 1246419.2287
10 | 2684461.6603 | 1246417.7905
11 | 2684434.977 | 1246430.5803
12 | 2684456.7798 | 1246405.7028
13 | 2684462.6322 | 1246341.9694
14 | 2684450.7354 | 1246486.6643
15 | 2684430.2548 | 1246466.469
16 | 2684458.2827 | 1246479.285
17 | 2684441.5329 | 1246494.6778
18 | 2684508.8549 | 1246427.3151
19 | 2684504.3296 | 1246432.0763
20 | 2684510.8577 | 1246425.2436
21 | 2684423.5594 | 1246507.4372
22 | 2684429.096 | 1246503.6693
23 | 2684442.8623 | 1246514.3059
24 | 2684414.8832 | 1246512.6039
25 | 2684447.7215 | 1246521.625
26 | 2684456.1411 | 1246501.1326
27 | 2684499.1899 | 1246460.3239
28 | 2684510.6759 | 1246470.2917
29 | 2684478.1328 | 1246479.7999
30 | 2684472.0999 | 1246527.3273
31 | 2684399.3961 | 1246519.8469
32 | 2684390.3545 | 1246497.4574
33 | 2684497.5645 | 1246439.2074
34 | 2684487.0811 | 1246450.272
35 | 2684483.5338 | 1246430.0516
36 | 2684402.9082 | 1246435.0233
37 | 2684443.1089 | 1246452.4528
38 | 2684466.305 | 1246471.4412
39 | 2684465.0852 | 1246492.2155
40 | 2684474.3024 | 1246483.3426
41 | 2684482.2777 | 1246531.7837
42 | 2684399.9915 | 1246489.9802
43 | 2684479.1663 | 1246458.3878
44 | 2684398.3178 | 1246432.6185
45 | 2684406.9096 | 1246437.1227
46 | 2684434.8049 | 1246444.0506

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98294 | -0.3287 | 0.0092503 | 0.0023183
1 | 0.98273 | -0.33287 | 0 | 0
2 | 0.9831 | -0.32562 | 0 | 0
3 | 0.98251 | -0.33709 | 0 | 0
4 | 0.98275 | -0.33238 | 0.0059401 | 0.0014887
5 | 0.98242 | -0.33884 | 0 | 0
6 | 0.98408 | -0.30647 | 0 | 0
7 | 0.98235 | -0.34028 | 0.003843 | 0.00096314
8 | 0.98644 | -0.26048 | 0 | 0
9 | 0.98347 | -0.31838 | 0.0097543 | 0.0024447
10 | 0.98846 | -0.22132 | 0.031657 | 0.0079339
11 | 0.98573 | -0.27446 | 0.0322 | 0.00807
12 | 0.98191 | -0.34876 | 0.022094 | 0.0055372
13 | 0.98065 | -0.37337 | 0.032108 | 0.008047
14 | 0.9946 | -0.10308 | 0 | 0
15 | 0.99771 | -0.043596 | 0.053916 | 0.013513
16 | 0.99391 | -0.11646 | 0.028104 | 0.0070435
17 | 0.99409 | -0.11295 | 0.030551 | 0.0076568
18 | 0.99081 | -0.17595 | 0 | 0
19 | 0.9909 | -0.17426 | 0 | 0
20 | 0.99078 | -0.1767 | 0.014567 | 0.0036508
21 | 0.99227 | -0.14809 | 0 | 0
22 | 0.99302 | -0.13364 | 0.030723 | 0.0076999
23 | 0.98964 | -0.19873 | 0 | 0
24 | 0.99201 | -0.15304 | 0.011077 | 0.0027762
25 | 0.98953 | -0.20091 | 0 | 0
26 | 0.98826 | -0.22551 | 0.0082964 | 0.0020793
27 | 0.98607 | -0.26823 | 0 | 0
28 | 0.98577 | -0.27408 | 0.021456 | 0.0053775
29 | 0.98663 | -0.2572 | 0.0066791 | 0.0016739
30 | 0.9892 | -0.20736 | 0.0070848 | 0.0017756
31 | 0.99175 | -0.15807 | 0 | 0
32 | 0.99138 | -0.16517 | 0 | 0
33 | 0.99103 | -0.17172 | 0 | 0
34 | 0.99171 | -0.15872 | 0.020567 | 0.0051545
35 | 0.99035 | -0.18497 | 0.014875 | 0.0037279
36 | 0.9832 | -0.3236 | 0 | 0
37 | 1 | 0 | -0.53161 | -0.1348
38 | 0.99324 | -0.12932 | 0.028516 | 0.0071468
39 | 0.98743 | -0.24177 | 0.016125 | 0.0040414
40 | 0.98677 | -0.25458 | 0.027802 | 0.006968
41 | 0.98913 | -0.20872 | 0.0068769 | 0.0017235
42 | 0.99119 | -0.1689 | 0.016593 | 0.0041585
43 | 0.99226 | -0.14804 | 0.018229 | 0.0045686
44 | 0.98316 | -0.32442 | 0.0087735 | 0.0021988
45 | 0.98317 | -0.32419 | 0.007185 | 0.0018007
46 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0038451 | 0.00096238 | -0.0038443 | -0.00096266 | 7.6291e-07 | -2.7273e-07 | 0.0058204 | 0.0058207 | 0.0058207 | 0.98294 | -0.3287 | 0.98273 | -0.33287 | 1.5991
1 | -0.013095 | -0.0032807 | 0.013097 | 0.0032818 | 1.9223e-06 | 1.0649e-06 | 0.019824 | 0.019824 | 0.019824 | 0.98294 | -0.3287 | 0.9831 | -0.32562 | 5.4461
2 | 0.0038443 | 0.00096266 | -0.0038436 | -0.00096293 | 7.7218e-07 | -2.7564e-07 | 0.0058207 | 0.005821 | 0.005821 | 0.98273 | -0.33287 | 0.98251 | -0.33709 | 1.5992
3 | 0.005942 | 0.0014892 | -0.0059401 | -0.0014887 | 1.9155e-06 | 4.2554e-07 | 0.0089938 | 0.0089941 | 0.0089941 | 0.9831 | -0.32562 | 0.98275 | -0.33238 | 2.4709
4 | 0.054299 | 0.013645 | -0.054265 | -0.013624 | 3.4247e-05 | 2.1747e-05 | 0.0822 | 0.082201 | 0.082201 | 0.9831 | -0.32562 | 0.98242 | -0.33884 | 22.5826
5 | -0.073338 | -0.018416 | 0.073405 | 0.018459 | 6.7058e-05 | 4.2733e-05 | 0.11102 | 0.11102 | 0.11102 | 0.9831 | -0.32562 | 0.98408 | -0.30647 | 30.4995
6 | 0.0038436 | 0.00096293 | -0.003843 | -0.00096314 | 5.8557e-07 | -2.0875e-07 | 0.005821 | 0.0058212 | 0.0058212 | 0.98251 | -0.33709 | 0.98235 | -0.34028 | 1.5992
7 | 0.022104 | 0.0055436 | -0.022094 | -0.0055372 | 1.0446e-05 | 6.3708e-06 | 0.033481 | 0.033482 | 0.033482 | 0.98242 | -0.33884 | 0.98191 | -0.34876 | 9.1982
8 | 0.032161 | 0.0080801 | -0.032108 | -0.008047 | 5.2921e-05 | 3.3118e-05 | 0.048719 | 0.048719 | 0.048719 | 0.98242 | -0.33884 | 0.98065 | -0.37337 | 13.3844
9 | -0.099137 | -0.024915 | 0.099356 | 0.025054 | 0.00021816 | 0.0001393 | 0.14993 | 0.14993 | 0.14993 | 0.98408 | -0.30647 | 0.98644 | -0.26048 | 41.1894
10 | 0.025732 | 0.0064558 | -0.025717 | -0.0064468 | 1.4598e-05 | 9.0163e-06 | 0.038912 | 0.038912 | 0.038912 | 0.98408 | -0.30647 | 0.98347 | -0.31838 | 10.69
11 | -0.13158 | -0.033138 | 0.13182 | 0.033295 | 0.00024692 | 0.00015782 | 0.19854 | 0.19854 | 0.19854 | 0.98644 | -0.26048 | 0.98846 | -0.22132 | 54.5431
12 | 0.032221 | 0.0080834 | -0.0322 | -0.00807 | 2.1447e-05 | 1.3417e-05 | 0.048607 | 0.048607 | 0.048607 | 0.98644 | -0.26048 | 0.98573 | -0.27446 | 13.3537
13 | 0.015963 | 0.0040021 | -0.015959 | -0.0039998 | 3.9733e-06 | 2.3125e-06 | 0.024153 | 0.024153 | 0.024153 | 0.98347 | -0.31838 | 0.9832 | -0.3236 | 6.6355
14 | -0.16348 | -0.041229 | 0.16377 | 0.041411 | 0.00028497 | 0.00018174 | 0.24619 | 0.24619 | 0.24619 | 0.98846 | -0.22132 | 0.99035 | -0.18497 | 33.8176
15 | -0.47358 | -0.11971 | 0.47494 | 0.12058 | 0.001355 | 0.00086573 | 0.70888 | 0.70888 | 0.70888 | 0.9946 | -0.10308 | 0.99771 | -0.043596 | 48.687
16 | 0.28952 | 0.073276 | -0.28934 | -0.073158 | 0.00018588 | 0.00011842 | 0.43341 | 0.43341 | 0.43341 | 0.9946 | -0.10308 | 0.99391 | -0.11646 | 29.7671
17 | 0.18406 | 0.046433 | -0.18397 | -0.046378 | 8.6907e-05 | 5.4987e-05 | 0.27547 | 0.27547 | 0.27547 | 0.9946 | -0.10308 | 0.99409 | -0.11295 | 18.9199
18 | -0.52885 | -0.13409 | 0.52996 | 0.1348 | 0.0011107 | 0.00070988 | 0.78929 | 0.78929 | 0.78929 | 0.99771 | -0.043596 | 1 | 0 | 54.2097
19 | 0.26124 | 0.066115 | -0.26107 | -0.066012 | 0.00016108 | 0.00010251 | 0.39133 | 0.39133 | 0.39133 | 0.99391 | -0.11646 | 0.99324 | -0.12932 | 26.8773
20 | 0.15342 | 0.038721 | -0.15327 | -0.038625 | 0.00015189 | 9.681e-05 | 0.22974 | 0.22974 | 0.22974 | 0.99409 | -0.11295 | 0.99302 | -0.13364 | 31.5581
21 | -0.014567 | -0.0036511 | 0.014569 | 0.0036518 | 1.1774e-06 | 6.6905e-07 | 0.021878 | 0.021878 | 0.021878 | 0.99081 | -0.17595 | 0.9909 | -0.17426 | 6.0103
22 | 0.014567 | 0.0036511 | -0.014567 | -0.0036508 | 5.172e-07 | 2.939e-07 | 0.021878 | 0.021878 | 0.021878 | 0.99081 | -0.17595 | 0.99078 | -0.1767 | 6.0103
23 | -0.014569 | -0.0036518 | 0.01457 | 0.0036528 | 1.7642e-06 | 1.0025e-06 | 0.021878 | 0.021877 | 0.021878 | 0.9909 | -0.17426 | 0.99103 | -0.17172 | 6.0103
24 | -0.12246 | -0.030871 | 0.12254 | 0.030925 | 8.4755e-05 | 5.4157e-05 | 0.18371 | 0.18371 | 0.18371 | 0.99227 | -0.14809 | 0.99302 | -0.13364 | 50.4685
25 | 0.094771 | 0.023925 | -0.094541 | -0.023778 | 0.00022928 | 0.00014635 | 0.14218 | 0.14218 | 0.14218 | 0.99227 | -0.14809 | 0.98964 | -0.19873 | 39.0607
26 | 0.027689 | 0.0069461 | -0.027682 | -0.006942 | 6.535e-06 | 4.0519e-06 | 0.041525 | 0.041525 | 0.041525 | 0.99227 | -0.14809 | 0.99201 | -0.15304 | 11.4079
27 | 0.013968 | 0.0035025 | -0.013966 | -0.0035017 | 1.4547e-06 | 8.18e-07 | 0.021003 | 0.021003 | 0.021003 | 0.98964 | -0.19873 | 0.98953 | -0.20091 | 5.7699
28 | 0.080573 | 0.020276 | -0.08047 | -0.02021 | 0.000103 | 6.5679e-05 | 0.12118 | 0.12118 | 0.12118 | 0.98964 | -0.19873 | 0.98826 | -0.22551 | 33.2908
29 | 0.016605 | 0.0041658 | -0.016601 | -0.0041635 | 3.9781e-06 | 2.3253e-06 | 0.024909 | 0.024909 | 0.024909 | 0.99201 | -0.15304 | 0.99175 | -0.15807 | 6.8432
30 | 0.013966 | 0.0035017 | -0.013962 | -0.0034993 | 4.2892e-06 | 2.4121e-06 | 0.021003 | 0.021003 | 0.021003 | 0.98953 | -0.20091 | 0.9892 | -0.20736 | 5.77
31 | 0.072174 | 0.018131 | -0.072118 | -0.018095 | 5.5947e-05 | 3.5645e-05 | 0.10869 | 0.10869 | 0.10869 | 0.98826 | -0.22551 | 0.98743 | -0.24177 | 29.859
32 | 0.021462 | 0.0053811 | -0.021456 | -0.0053775 | 5.9824e-06 | 3.6348e-06 | 0.032388 | 0.032388 | 0.032388 | 0.98607 | -0.26823 | 0.98577 | -0.27408 | 8.8979
33 | -0.021462 | -0.0053811 | 0.021474 | 0.0053879 | 1.1283e-05 | 6.8551e-06 | 0.032388 | 0.032388 | 0.032388 | 0.98607 | -0.26823 | 0.98663 | -0.2572 | 8.8979
34 | -0.028153 | -0.0070619 | 0.028156 | 0.0070641 | 3.5276e-06 | 2.191e-06 | 0.042461 | 0.042461 | 0.042461 | 0.98663 | -0.2572 | 0.98677 | -0.25458 | 11.6652
35 | 0.0068773 | 0.0017237 | -0.0068769 | -0.0017235 | 4.4592e-07 | 1.4277e-07 | 0.010345 | 0.010345 | 0.010345 | 0.9892 | -0.20736 | 0.98913 | -0.20872 | 2.8421
36 | 0.016601 | 0.0041635 | -0.016595 | -0.0041602 | 5.6163e-06 | 3.2831e-06 | 0.024909 | 0.024909 | 0.024909 | 0.99175 | -0.15807 | 0.99138 | -0.16517 | 6.8432
37 | 0.016595 | 0.0041602 | -0.016593 | -0.0041585 | 2.9489e-06 | 1.7239e-06 | 0.024909 | 0.024909 | 0.024909 | 0.99138 | -0.16517 | 0.99119 | -0.1689 | 6.8432
38 | -0.19332 | -0.048864 | 0.19344 | 0.04894 | 0.00012052 | 7.6348e-05 | 0.29042 | 0.29042 | 0.29042 | 0.99103 | -0.17172 | 0.99171 | -0.15872 | 19.9463
39 | 0.17875 | 0.045211 | -0.17864 | -0.045139 | 0.00011359 | 7.1832e-05 | 0.26854 | 0.26854 | 0.26854 | 0.99103 | -0.17172 | 0.99035 | -0.18497 | 18.4438
40 | -0.21401 | -0.054094 | 0.21412 | 0.054164 | 0.0001097 | 6.9623e-05 | 0.32128 | 0.32128 | 0.32128 | 0.99171 | -0.15872 | 0.99226 | -0.14804 | 22.0657
41 | 0.0071852 | 0.0018008 | -0.007185 | -0.0018007 | 2.0038e-07 | 7.0938e-08 | 0.010874 | 0.010874 | 0.010874 | 0.9832 | -0.3236 | 0.98317 | -0.32419 | 2.9875
42 | 0.0087738 | 0.002199 | -0.0087735 | -0.0021988 | 3.4265e-07 | 1.5358e-07 | 0.013279 | 0.013279 | 0.013279 | 0.9832 | -0.3236 | 0.98316 | -0.32442 | 3.648
43 | 0.23256 | 0.058865 | -0.23235 | -0.058733 | 0.00020879 | 0.00013268 | 0.34861 | 0.34861 | 0.34861 | 0.99324 | -0.12932 | 0.99226 | -0.14804 | 23.9432
44 | 0.055993 | 0.014054 | -0.055959 | -0.014032 | 3.4171e-05 | 2.1706e-05 | 0.084386 | 0.084386 | 0.084386 | 0.98743 | -0.24177 | 0.98677 | -0.25458 | 23.1831

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.55526 | 0.14073

## res_load
| p_mw | q_mvar
0 | 0.0092503 | 0.0023183
1 | 0.0059401 | 0.0014887
2 | 0.003843 | 0.00096314
3 | 0.0097543 | 0.0024447
4 | 0.031657 | 0.0079339
5 | 0.0322 | 0.00807
6 | 0.022094 | 0.0055372
7 | 0.032108 | 0.008047
8 | 0.053916 | 0.013513
9 | 0.028104 | 0.0070435
10 | 0.030551 | 0.0076568
11 | 0.014567 | 0.0036508
12 | 0.030723 | 0.0076999
13 | 0.011077 | 0.0027762
14 | 0.0082964 | 0.0020793
15 | 0.021456 | 0.0053775
16 | 0.0066791 | 0.0016739
17 | 0.0070848 | 0.0017756
18 | 0.020567 | 0.0051545
19 | 0.014875 | 0.0037279
20 | 0.023651 | 0.0059276
21 | 0.028516 | 0.0071468
22 | 0.016125 | 0.0040414
23 | 0.027802 | 0.006968
24 | 0.0068769 | 0.0017235
25 | 0.016593 | 0.0041585
26 | 0.018229 | 0.0045686
27 | 0.0087735 | 0.0021988
28 | 0.007185 | 0.0018007

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1