## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-732_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-732_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-732_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_261-732_0_5_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_261-732_0_5_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_261-732_0_5_node_16 | 0.4 | n |  | TRUE
6 | bus_LV_261-732_0_5_node_28 | 0.4 | n |  | TRUE
7 | bus_LV_261-732_0_5_node_13 | 0.4 | n |  | TRUE
8 | bus_LV_261-732_0_5_node_27 | 0.4 | n |  | TRUE
9 | bus_LV_261-732_0_5_node_5 | 0.4 | n |  | TRUE
10 | bus_LV_261-732_0_5_node_7 | 0.4 | n |  | TRUE
11 | bus_LV_261-732_0_5_node_9 | 0.4 | n |  | TRUE
12 | bus_LV_261-732_0_5_node_11 | 0.4 | n |  | TRUE
13 | bus_LV_261-732_0_5_node_12 | 0.4 | n |  | TRUE
14 | bus_LV_261-732_0_5_node_29 | 0.4 | n |  | TRUE
15 | bus_LV_261-732_0_5_node_32 | 0.4 | n |  | TRUE
16 | bus_LV_261-732_0_5_node_14 | 0.4 | n |  | TRUE
17 | bus_LV_261-732_0_5_node_22 | 0.4 | n |  | TRUE
18 | bus_LV_261-732_0_5_node_23 | 0.4 | n |  | TRUE
19 | bus_LV_261-732_0_5_node_25 | 0.4 | n |  | TRUE
20 | bus_LV_261-732_0_5_node_18 | 0.4 | n |  | TRUE
21 | bus_LV_261-732_0_5_node_26 | 0.4 | n |  | TRUE
22 | bus_LV_261-732_0_5_node_24 | 0.4 | n |  | TRUE
23 | bus_LV_261-732_0_5_node_30 | 0.4 | n |  | TRUE
24 | bus_LV_261-732_0_5_node_20 | 0.4 | n |  | TRUE
25 | bus_LV_261-732_0_5_node_19 | 0.4 | n |  | TRUE
26 | bus_LV_261-732_0_5_node_33 | 0.4 | n |  | TRUE
27 | bus_LV_261-732_0_5_node_21 | 0.4 | n |  | TRUE
28 | bus_LV_261-732_0_5_node_31 | 0.4 | n |  | TRUE
29 | bus_MV_539_0_node_53 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-732_0_5_load_0 | 0 | 0.034317 | 0.0086007 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-732_0_5_load_1 | 1 | 0.013629 | 0.0034156 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-732_0_5_load_2 | 2 | 0.012175 | 0.0030513 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-732_0_5_load_3 | 3 | 0.013106 | 0.0032846 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-732_0_5_load_4 | 4 | 0.011829 | 0.0029647 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-732_0_5_load_28 | 6 | 0.017244 | 0.0043218 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-732_0_5_load_27 | 8 | 0.018402 | 0.0046121 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-732_0_5_load_5 | 9 | 0.014193 | 0.0035571 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-732_0_5_load_29 | 14 | 0.055946 | 0.014021 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-732_0_5_load_32 | 15 | 0.079369 | 0.019892 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-732_0_5_load_22 | 17 | 0.015694 | 0.0039333 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-732_0_5_load_23 | 18 | 0.013247 | 0.0033201 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-732_0_5_load_25 | 19 | 0.041945 | 0.010512 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-732_0_5_load_26 | 21 | 0.018188 | 0.0045583 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-732_0_5_load_24 | 22 | 0.015919 | 0.0039896 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-732_0_5_load_30 | 23 | 0.017522 | 0.0043914 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-732_0_5_load_20 | 24 | 0.033284 | 0.0083417 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_261-732_0_5_load_19 | 25 | 0.01538 | 0.0038547 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_261-732_0_5_load_33 | 26 | 0.030379 | 0.0076136 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_261-732_0_5_load_21 | 27 | 0.015563 | 0.0039003 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_261-732_0_5_load_31 | 28 | 0.056264 | 0.014101 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 25 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-732_0_5_line_0 |  | 0 | 1 | 0.0047255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-732_0_5_line_1 |  | 0 | 2 | 0.014719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-732_0_5_line_2 |  | 1 | 3 | 0.011149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-732_0_5_line_3 |  | 2 | 4 | 0.011054 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-732_0_5_line_4 |  | 3 | 5 | 0.023015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_261-732_0_5_line_5 |  | 4 | 6 | 0.00068136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_261-732_0_5_line_6 |  | 5 | 7 | 0.050237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_261-732_0_5_line_7 |  | 6 | 8 | 0.013047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
8 | LV_261-732_0_5_line_8 |  | 7 | 18 | 0.023406 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_261-732_0_5_line_9 |  | 7 | 10 | 0.0077663 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_261-732_0_5_line_10 |  | 8 | 21 | 0.016143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
11 | LV_261-732_0_5_line_11 |  | 9 | 10 | 0.027325 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_261-732_0_5_line_12 |  | 11 | 12 | 0.053486 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-732_0_5_line_13 |  | 11 | 13 | 0.01164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
14 | LV_261-732_0_5_line_14 |  | 11 | 14 | 0.021659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_261-732_0_5_line_15 |  | 12 | 15 | 0.044313 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_261-732_0_5_line_16 |  | 13 | 16 | 0.012111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
17 | LV_261-732_0_5_line_17 |  | 13 | 17 | 0.019514 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
18 | LV_261-732_0_5_line_18 |  | 14 | 23 | 0.020881 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_261-732_0_5_line_19 |  | 15 | 26 | 0.019333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_261-732_0_5_line_20 |  | 16 | 19 | 0.0080647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
21 | LV_261-732_0_5_line_21 |  | 17 | 27 | 0.014043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
22 | LV_261-732_0_5_line_22 |  | 18 | 22 | 0.020364 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_261-732_0_5_line_23 |  | 19 | 20 | 0.031081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
24 | LV_261-732_0_5_line_24 |  | 20 | 21 | 0.028473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
25 | LV_261-732_0_5_line_25 |  | 23 | 28 | 0.031841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_261-732_0_5_line_26 |  | 24 | 25 | 0.020722 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_261-732_0_5_line_27 |  | 25 | 27 | 0.013904 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-732_0_5_trafo_19 | 0.63 MVA 20/0.4 kV | 29 | 25 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2684246.0094 | 1245726.9096 | 2684241.8008 | 1245724.7605
1 | 2684246.0094 | 1245726.9096 | 2684259.1177 | 1245733.6034
2 | 2684241.8008 | 1245724.7605 | 2684231.8717 | 1245719.6902
3 | 2684268.9623 | 1245738.6306 | 2684259.1177 | 1245733.6034
4 | 2684211.3745 | 1245709.2233 | 2684231.8717 | 1245719.6902
5 | 2684268.9623 | 1245738.6306 | 2684269.5692 | 1245738.9405
6 | 2684211.3745 | 1245709.2233 | 2684213.1159 | 1245705.7788 | 2684232.5225 | 1245669.3943 | 2684234.2744 | 1245668.4073 | 2684237.4001 | 1245668.5741
7 | 2684269.5692 | 1245738.9405 | 2684281.1891 | 1245744.8742
8 | 2684237.4001 | 1245668.5741 | 2684258.4021 | 1245678.9071
9 | 2684237.4001 | 1245668.5741 | 2684238.9611 | 1245665.6052 | 2684240.9438 | 1245661.6638
10 | 2684295.5661 | 1245752.2158 | 2684281.1891 | 1245744.8742
11 | 2684240.9438 | 1245661.6638 | 2684265.3704 | 1245673.9117
12 | 2684256.5788 | 1245856.6289 | 2684267.4396 | 1245840.4491 | 2684282.6114 | 1245812.811 | 2684281.7452 | 1245810.497
13 | 2684281.7452 | 1245810.497 | 2684284.4969 | 1245805.6103 | 2684287.4654 | 1245800.3597
14 | 2684281.7452 | 1245810.497 | 2684276.7179 | 1245807.5011 | 2684272.0434 | 1245805.7334 | 2684262.4074 | 1245800.8368
15 | 2684256.5788 | 1245856.6289 | 2684252.9321 | 1245854.3087 | 2684235.4161 | 1245847.0102 | 2684231.6369 | 1245846.5784 | 2684229.3211 | 1245846.312 | 2684215.6381 | 1245840.4636
16 | 2684287.4654 | 1245800.3597 | 2684290.5629 | 1245800.9152 | 2684292.7277 | 1245800.6458 | 2684294.5327 | 1245799.6374 | 2684297.1428 | 1245795.6827
17 | 2684287.4654 | 1245800.3597 | 2684283.4945 | 1245798.5242 | 2684270.0677 | 1245791.5295
18 | 2684262.4074 | 1245800.8368 | 2684243.7919 | 1245791.377
19 | 2684215.6381 | 1245840.4636 | 2684197.8611 | 1245832.8653
20 | 2684297.1428 | 1245795.6827 | 2684301.8372 | 1245789.1252
21 | 2684257.6136 | 1245785.0415 | 2684270.0677 | 1245791.5295
22 | 2684276.6743 | 1245687.897 | 2684258.4021 | 1245678.9071
23 | 2684320.9241 | 1245765.1649 | 2684318.2106 | 1245768.9513 | 2684315.6056 | 1245769.8928 | 2684301.8372 | 1245789.1252
24 | 2684320.9241 | 1245765.1649 | 2684295.5661 | 1245752.2158
25 | 2684243.7919 | 1245791.377 | 2684215.4054 | 1245776.9519
26 | 2684245.2828 | 1245778.6177 | 2684226.9046 | 1245769.0436
27 | 2684257.6136 | 1245785.0415 | 2684245.2828 | 1245778.6177

## bus_geodata
| x | y | coords
0 | 2684246.0094 | 1245726.9096
1 | 2684241.8008 | 1245724.7605
2 | 2684259.1177 | 1245733.6034
3 | 2684231.8717 | 1245719.6902
4 | 2684268.9623 | 1245738.6306
5 | 2684211.3745 | 1245709.2233
6 | 2684269.5692 | 1245738.9405
7 | 2684237.4001 | 1245668.5741
8 | 2684281.1891 | 1245744.8742
9 | 2684265.3704 | 1245673.9117
10 | 2684240.9438 | 1245661.6638
11 | 2684281.7452 | 1245810.497
12 | 2684256.5788 | 1245856.6289
13 | 2684287.4654 | 1245800.3597
14 | 2684262.4074 | 1245800.8368
15 | 2684215.6381 | 1245840.4636
16 | 2684297.1428 | 1245795.6827
17 | 2684270.0677 | 1245791.5295
18 | 2684258.4021 | 1245678.9071
19 | 2684301.8372 | 1245789.1252
20 | 2684320.9241 | 1245765.1649
21 | 2684295.5661 | 1245752.2158
22 | 2684276.6743 | 1245687.897
23 | 2684243.7919 | 1245791.377
24 | 2684226.9046 | 1245769.0436
25 | 2684245.2828 | 1245778.6177
26 | 2684197.8611 | 1245832.8653
27 | 2684257.6136 | 1245785.0415
28 | 2684215.4054 | 1245776.9519
29 | 2684245.2828 | 1245778.6177

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9871 | -0.24783 | 0.034317 | 0.0086007
1 | 0.9868 | -0.25376 | 0.013629 | 0.0034156
2 | 0.98852 | -0.22038 | 0.012175 | 0.0030513
3 | 0.98621 | -0.26503 | 0.013106 | 0.0032846
4 | 0.9897 | -0.19742 | 0.011829 | 0.0029647
5 | 0.98529 | -0.28293 | 0 | 0
6 | 0.98978 | -0.19586 | 0.017244 | 0.0043218
7 | 0.98328 | -0.32212 | 0 | 0
8 | 0.99066 | -0.17897 | 0.018402 | 0.0046121
9 | 0.98282 | -0.33111 | 0.014193 | 0.0035571
10 | 0.98318 | -0.32411 | 0 | 0
11 | 0.99351 | -0.12385 | 0 | 0
12 | 0.9881 | -0.22807 | 0 | 0
13 | 0.9948 | -0.099266 | 0 | 0
14 | 0.99094 | -0.17359 | 0.055946 | 0.014021
15 | 0.98361 | -0.31528 | 0.079369 | 0.019892
16 | 0.99417 | -0.11123 | 0 | 0
17 | 0.99687 | -0.059507 | 0.015694 | 0.0039333
18 | 0.98265 | -0.33444 | 0.013247 | 0.0033201
19 | 0.99376 | -0.1192 | 0.041945 | 0.010512
20 | 0.99246 | -0.14423 | 0 | 0
21 | 0.99126 | -0.16722 | 0.018188 | 0.0045583
22 | 0.98235 | -0.34029 | 0.015919 | 0.0039896
23 | 0.98952 | -0.20098 | 0.017522 | 0.0043914
24 | 0.99937 | -0.012029 | 0.033284 | 0.0083417
25 | 1 | 0 | -0.53531 | -0.13585
26 | 0.98307 | -0.32587 | 0.030379 | 0.0076136
27 | 0.99842 | -0.030034 | 0.015563 | 0.0039003
28 | 0.98788 | -0.23292 | 0.056264 | 0.014101
29 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.07029 | 0.017691 | -0.07027 | -0.017678 | 1.9905e-05 | 1.2679e-05 | 0.10599 | 0.10599 | 0.10599 | 0.9871 | -0.24783 | 0.9868 | -0.25376 | 29.1169
1 | -0.10461 | -0.026291 | 0.10474 | 0.026379 | 0.0001373 | 8.7681e-05 | 0.15772 | 0.15772 | 0.15772 | 0.9871 | -0.24783 | 0.98852 | -0.22038 | 43.3289
2 | 0.056641 | 0.014262 | -0.056611 | -0.014243 | 3.0516e-05 | 1.9388e-05 | 0.085435 | 0.085435 | 0.085435 | 0.9868 | -0.25376 | 0.98621 | -0.26503 | 23.4711
3 | -0.11692 | -0.02943 | 0.11705 | 0.029512 | 0.00012847 | 8.2077e-05 | 0.17604 | 0.17604 | 0.17604 | 0.98852 | -0.22038 | 0.9897 | -0.19742 | 48.3638
4 | 0.043505 | 0.010958 | -0.043468 | -0.010935 | 3.721e-05 | 2.3521e-05 | 0.065661 | 0.065661 | 0.065661 | 0.98621 | -0.26503 | 0.98529 | -0.28293 | 18.0387
5 | -0.12888 | -0.032477 | 0.12889 | 0.032483 | 9.5995e-06 | 6.1349e-06 | 0.19383 | 0.19383 | 0.19383 | 0.9897 | -0.19742 | 0.98978 | -0.19586 | 53.2498
6 | 0.043468 | 0.010935 | -0.043387 | -0.010883 | 8.1222e-05 | 5.1343e-05 | 0.065661 | 0.065661 | 0.065661 | 0.98529 | -0.28293 | 0.98328 | -0.32212 | 18.0388
7 | -0.14613 | -0.036805 | 0.14625 | 0.03688 | 0.00011814 | 7.5274e-05 | 0.21975 | 0.21975 | 0.21975 | 0.98978 | -0.19586 | 0.99066 | -0.17897 | 30.186
8 | 0.029188 | 0.0073229 | -0.02917 | -0.0073123 | 1.7127e-05 | 1.0664e-05 | 0.044173 | 0.044173 | 0.044173 | 0.98328 | -0.32212 | 0.98265 | -0.33444 | 12.1354
9 | 0.014199 | 0.0035606 | -0.014198 | -0.0035598 | 1.3448e-06 | 7.6216e-07 | 0.021488 | 0.021488 | 0.021488 | 0.98328 | -0.32212 | 0.98318 | -0.32411 | 5.9034
10 | -0.16465 | -0.041492 | 0.16474 | 0.041551 | 9.2627e-05 | 5.8449e-05 | 0.2474 | 0.24739 | 0.2474 | 0.99066 | -0.17897 | 0.99126 | -0.16722 | 16.9914
11 | -0.014193 | -0.0035571 | 0.014198 | 0.0035598 | 4.7316e-06 | 2.6818e-06 | 0.021489 | 0.021488 | 0.021489 | 0.98282 | -0.33111 | 0.98318 | -0.32411 | 5.9034
12 | 0.11077 | 0.028161 | -0.11022 | -0.027808 | 0.00055305 | 0.00035326 | 0.16605 | 0.16605 | 0.16605 | 0.99351 | -0.12385 | 0.9881 | -0.22807 | 45.6187
13 | -0.241 | -0.060988 | 0.24128 | 0.06117 | 0.00028467 | 0.00018189 | 0.36116 | 0.36116 | 0.36116 | 0.99351 | -0.12385 | 0.9948 | -0.099266 | 49.6098
14 | 0.13022 | 0.032828 | -0.12991 | -0.03263 | 0.00030918 | 0.00019759 | 0.19511 | 0.19511 | 0.19511 | 0.99351 | -0.12385 | 0.99094 | -0.17359 | 53.601
15 | 0.11022 | 0.027808 | -0.10976 | -0.027515 | 0.0004582 | 0.00029268 | 0.16605 | 0.16605 | 0.16605 | 0.9881 | -0.22807 | 0.98361 | -0.31528 | 45.6187
16 | 0.22551 | 0.057025 | -0.22538 | -0.056943 | 0.00012933 | 8.2144e-05 | 0.3375 | 0.3375 | 0.3375 | 0.9948 | -0.099266 | 0.99417 | -0.11123 | 23.1801
17 | -0.4668 | -0.1182 | 0.46769 | 0.11877 | 0.000893 | 0.00057051 | 0.69866 | 0.69866 | 0.69866 | 0.9948 | -0.099266 | 0.99687 | -0.059507 | 47.985
18 | 0.073969 | 0.018609 | -0.073872 | -0.018547 | 9.665e-05 | 6.1587e-05 | 0.1111 | 0.1111 | 0.1111 | 0.99094 | -0.17359 | 0.98952 | -0.20098 | 30.5214
19 | 0.030394 | 0.0076232 | -0.030379 | -0.0076136 | 1.5329e-05 | 9.5651e-06 | 0.045982 | 0.045982 | 0.045982 | 0.98361 | -0.31528 | 0.98307 | -0.32587 | 12.6325
20 | 0.22538 | 0.056943 | -0.2253 | -0.056888 | 8.6121e-05 | 5.47e-05 | 0.3375 | 0.3375 | 0.3375 | 0.99417 | -0.11123 | 0.99376 | -0.1192 | 23.1801
21 | -0.48338 | -0.1227 | 0.48407 | 0.12314 | 0.00068644 | 0.00043859 | 0.72209 | 0.72209 | 0.72209 | 0.99687 | -0.059507 | 0.99842 | -0.030034 | 49.5939
22 | 0.015923 | 0.0039922 | -0.015919 | -0.0039896 | 4.4401e-06 | 2.5838e-06 | 0.024113 | 0.024113 | 0.024113 | 0.98265 | -0.33444 | 0.98235 | -0.34029 | 6.6244
23 | 0.18335 | 0.046376 | -0.18313 | -0.046237 | 0.00021987 | 0.00013911 | 0.2747 | 0.2747 | 0.2747 | 0.99376 | -0.1192 | 0.99246 | -0.14423 | 18.8665
24 | 0.18313 | 0.046237 | -0.18293 | -0.046109 | 0.00020142 | 0.00012744 | 0.2747 | 0.2747 | 0.2747 | 0.99246 | -0.14423 | 0.99126 | -0.16722 | 18.8666
25 | 0.05635 | 0.014156 | -0.056264 | -0.014101 | 8.5761e-05 | 5.4479e-05 | 0.084749 | 0.084749 | 0.084749 | 0.98952 | -0.20098 | 0.98788 | -0.23292 | 23.2827
26 | -0.033284 | -0.0083417 | 0.033303 | 0.0083536 | 1.9085e-05 | 1.1943e-05 | 0.049558 | 0.049558 | 0.049558 | 0.99937 | -0.012029 | 1 | 0 | 13.6148
27 | 0.50036 | 0.1275 | -0.49963 | -0.12704 | 0.00072401 | 0.00046264 | 0.74528 | 0.74528 | 0.74528 | 1 | 0 | 0.99842 | -0.030034 | 51.1869

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.55069 | 0.13971

## res_load
| p_mw | q_mvar
0 | 0.034317 | 0.0086007
1 | 0.013629 | 0.0034156
2 | 0.012175 | 0.0030513
3 | 0.013106 | 0.0032846
4 | 0.011829 | 0.0029647
5 | 0.017244 | 0.0043218
6 | 0.018402 | 0.0046121
7 | 0.014193 | 0.0035571
8 | 0.055946 | 0.014021
9 | 0.079369 | 0.019892
10 | 0.015694 | 0.0039333
11 | 0.013247 | 0.0033201
12 | 0.041945 | 0.010512
13 | 0.018188 | 0.0045583
14 | 0.015919 | 0.0039896
15 | 0.017522 | 0.0043914
16 | 0.033284 | 0.0083417
17 | 0.01538 | 0.0038547
18 | 0.030379 | 0.0076136
19 | 0.015563 | 0.0039003
20 | 0.056264 | 0.014101

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1