## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-737_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-737_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-737_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_261-737_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_261-737_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_261-737_0_3_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_261-737_0_3_node_23 | 0.4 | n |  | TRUE
7 | bus_LV_261-737_0_3_node_17 | 0.4 | n |  | TRUE
8 | bus_LV_261-737_0_3_node_28 | 0.4 | n |  | TRUE
9 | bus_LV_261-737_0_3_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_261-737_0_3_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_261-737_0_3_node_24 | 0.4 | n |  | TRUE
12 | bus_LV_261-737_0_3_node_9 | 0.4 | n |  | TRUE
13 | bus_LV_261-737_0_3_node_15 | 0.4 | n |  | TRUE
14 | bus_LV_261-737_0_3_node_21 | 0.4 | n |  | TRUE
15 | bus_LV_261-737_0_3_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_261-737_0_3_node_12 | 0.4 | n |  | TRUE
17 | bus_LV_261-737_0_3_node_11 | 0.4 | n |  | TRUE
18 | bus_LV_261-737_0_3_node_20 | 0.4 | n |  | TRUE
19 | bus_LV_261-737_0_3_node_22 | 0.4 | n |  | TRUE
20 | bus_LV_261-737_0_3_node_14 | 0.4 | n |  | TRUE
21 | bus_LV_261-737_0_3_node_25 | 0.4 | n |  | TRUE
22 | bus_LV_261-737_0_3_node_26 | 0.4 | n |  | TRUE
23 | bus_LV_261-737_0_3_node_18 | 0.4 | n |  | TRUE
24 | bus_LV_261-737_0_3_node_16 | 0.4 | n |  | TRUE
25 | bus_LV_261-737_0_3_node_27 | 0.4 | n |  | TRUE
26 | bus_LV_261-737_0_3_node_19 | 0.4 | n |  | TRUE
27 | bus_MV_532_0_node_61 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-737_0_3_load_0 | 0 | 0.032584 | 0.0081662 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-737_0_3_load_1 | 1 | 0.026007 | 0.0065181 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-737_0_3_load_3 | 3 | 0.029001 | 0.0072684 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-737_0_3_load_4 | 4 | 0.025792 | 0.0064642 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-737_0_3_load_23 | 6 | 0.018053 | 0.0045246 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-737_0_3_load_17 | 7 | 0.026267 | 0.0065831 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-737_0_3_load_28 | 8 | 0.031056 | 0.0077833 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-737_0_3_load_24 | 11 | 0.0071239 | 0.0017854 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-737_0_3_load_21 | 14 | 0.090873 | 0.022775 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-737_0_3_load_20 | 18 | 0.011323 | 0.0028379 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-737_0_3_load_22 | 19 | 0.0065883 | 0.0016512 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-737_0_3_load_25 | 21 | 0.0068962 | 0.0017284 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-737_0_3_load_26 | 22 | 0.0071506 | 0.0017921 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-737_0_3_load_18 | 23 | 0.022503 | 0.0056397 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-737_0_3_load_27 | 25 | 0.014252 | 0.0035718 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-737_0_3_load_19 | 26 | 0.018681 | 0.0046819 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 0 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-737_0_3_line_0 |  | 0 | 1 | 0.032302 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
1 | LV_261-737_0_3_line_1 |  | 0 | 2 | 0.012331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-737_0_3_line_2 |  | 1 | 3 | 0.01481 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
3 | LV_261-737_0_3_line_3 |  | 2 | 4 | 0.033559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-737_0_3_line_4 |  | 2 | 5 | 0.012519 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_261-737_0_3_line_5 |  | 3 | 6 | 0.026121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
6 | LV_261-737_0_3_line_6 |  | 4 | 7 | 0.0039921 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_261-737_0_3_line_7 |  | 5 | 8 | 0.012134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_261-737_0_3_line_8 |  | 6 | 15 | 0.017852 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
9 | LV_261-737_0_3_line_9 |  | 7 | 9 | 0.035338 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_261-737_0_3_line_10 |  | 9 | 10 | 0.002654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_261-737_0_3_line_11 |  | 10 | 11 | 0.038496 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_261-737_0_3_line_12 |  | 11 | 21 | 0.023355 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-737_0_3_line_13 |  | 12 | 13 | 0.016624 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_261-737_0_3_line_14 |  | 12 | 14 | 0.056808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_261-737_0_3_line_15 |  | 13 | 23 | 0.012812 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_261-737_0_3_line_16 |  | 14 | 24 | 0.029598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_261-737_0_3_line_17 |  | 15 | 16 | 0.044273 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_261-737_0_3_line_18 |  | 15 | 17 | 0.020296 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_261-737_0_3_line_19 |  | 16 | 19 | 0.052711 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_261-737_0_3_line_20 |  | 17 | 18 | 0.0034012 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_261-737_0_3_line_21 |  | 19 | 24 | 0.010077 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_261-737_0_3_line_22 |  | 20 | 21 | 0.039571 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_261-737_0_3_line_23 |  | 20 | 22 | 0.039871 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_261-737_0_3_line_24 |  | 22 | 25 | 0.0041297 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_261-737_0_3_line_25 |  | 23 | 26 | 0.0033023 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-737_0_3_trafo_0 | 0.63 MVA 20/0.4 kV | 27 | 0 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2682557.6415 | 1246253.2523 | 2682559.3086 | 1246236.4313 | 2682560.7312 | 1246221.0982
1 | 2682556.4253 | 1246265.5236 | 2682557.6415 | 1246253.2523
2 | 2682562.0995 | 1246206.3518 | 2682560.7312 | 1246221.0982
3 | 2682556.4253 | 1246265.5236 | 2682588.9775 | 1246273.6819
4 | 2682555.2016 | 1246277.9823 | 2682555.7755 | 1246272.0415 | 2682556.4253 | 1246265.5236
5 | 2682564.7564 | 1246180.3691 | 2682563.8689 | 1246187.2811 | 2682562.0995 | 1246206.3518
6 | 2682588.9775 | 1246273.6819 | 2682592.8498 | 1246274.6524
7 | 2682555.2016 | 1246277.9823 | 2682567.0005 | 1246280.8153
8 | 2682567.0299 | 1246162.6626 | 2682564.7564 | 1246180.3691
9 | 2682627.1278 | 1246283.2432 | 2682592.8498 | 1246274.6524
10 | 2682629.4449 | 1246282.3304 | 2682628.6028 | 1246283.1192 | 2682627.8747 | 1246283.3203 | 2682627.1278 | 1246283.2432
11 | 2682629.4449 | 1246282.3304 | 2682638.6982 | 1246244.9634
12 | 2682644.3122 | 1246222.2929 | 2682638.6982 | 1246244.9634
13 | 2682520.5131 | 1246303.1848 | 2682503.9049 | 1246301.7193
14 | 2682520.5131 | 1246303.1848 | 2682526.1728 | 1246246.659
15 | 2682503.9049 | 1246301.7193 | 2682504.8529 | 1246289.5236 | 2682504.8976 | 1246288.9457
16 | 2682529.1216 | 1246217.2083 | 2682526.1728 | 1246246.659
17 | 2682537.1568 | 1246155.0636 | 2682538.727 | 1246147.5577 | 2682544.5404 | 1246150.563 | 2682550.6349 | 1246152.3714 | 2682552.9223 | 1246153.0482 | 2682559.0544 | 1246154.8682 | 2682568.0369 | 1246157.0837 | 2682567.0299 | 1246162.6626
18 | 2682568.3582 | 1246142.6999 | 2682567.8858 | 1246145.1506 | 2682569.0535 | 1246151.3603 | 2682568.8402 | 1246152.5694 | 2682568.0369 | 1246157.0837 | 2682567.0299 | 1246162.6626
19 | 2682537.1568 | 1246155.0636 | 2682535.0958 | 1246161.4618 | 2682530.1954 | 1246207.1888
20 | 2682568.3582 | 1246142.6999 | 2682569.0039 | 1246139.3605
21 | 2682529.1216 | 1246217.2083 | 2682530.1954 | 1246207.1888
22 | 2682652.249 | 1246184.0428 | 2682652.9818 | 1246185.1316 | 2682653.1601 | 1246185.8902 | 2682653.1341 | 1246186.6682 | 2682644.3122 | 1246222.2929
23 | 2682652.249 | 1246184.0428 | 2682651.1174 | 1246183.3821 | 2682613.6767 | 1246174.1566
24 | 2682609.667 | 1246173.1686 | 2682613.6767 | 1246174.1566
25 | 2682504.8976 | 1246288.9457 | 2682505.1523 | 1246285.6533

## bus_geodata
| x | y | coords
0 | 2682557.6415 | 1246253.2523
1 | 2682560.7312 | 1246221.0982
2 | 2682556.4253 | 1246265.5236
3 | 2682562.0995 | 1246206.3518
4 | 2682588.9775 | 1246273.6819
5 | 2682555.2016 | 1246277.9823
6 | 2682564.7564 | 1246180.3691
7 | 2682592.8498 | 1246274.6524
8 | 2682567.0005 | 1246280.8153
9 | 2682627.1278 | 1246283.2432
10 | 2682629.4449 | 1246282.3304
11 | 2682638.6982 | 1246244.9634
12 | 2682520.5131 | 1246303.1848
13 | 2682503.9049 | 1246301.7193
14 | 2682526.1728 | 1246246.659
15 | 2682567.0299 | 1246162.6626
16 | 2682537.1568 | 1246155.0636
17 | 2682568.3582 | 1246142.6999
18 | 2682569.0039 | 1246139.3605
19 | 2682530.1954 | 1246207.1888
20 | 2682652.249 | 1246184.0428
21 | 2682644.3122 | 1246222.2929
22 | 2682613.6767 | 1246174.1566
23 | 2682504.8976 | 1246288.9457
24 | 2682529.1216 | 1246217.2083
25 | 2682609.667 | 1246173.1686
26 | 2682505.1523 | 1246285.6533
27 | 2682556.4253 | 1246265.5236

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 1 | 0 | -0.34755 | -0.088367
1 | 0.99667 | -0.062998 | 0.026007 | 0.0065181
2 | 0.99867 | -0.025513 | 0 | 0
3 | 0.99531 | -0.088633 | 0.029001 | 0.0072684
4 | 0.99599 | -0.076961 | 0.025792 | 0.0064642
5 | 0.99831 | -0.03231 | 0 | 0
6 | 0.99327 | -0.12732 | 0.018053 | 0.0045246
7 | 0.99577 | -0.081289 | 0.026267 | 0.0065831
8 | 0.99797 | -0.038902 | 0.031056 | 0.0077833
9 | 0.99462 | -0.10332 | 0 | 0
10 | 0.99453 | -0.10498 | 0 | 0
11 | 0.99329 | -0.12904 | 0.0071239 | 0.0017854
12 | 0.97243 | -0.53089 | 0 | 0
13 | 0.97179 | -0.54352 | 0 | 0
14 | 0.97461 | -0.48786 | 0.090873 | 0.022775
15 | 0.99203 | -0.151 | 0 | 0
16 | 0.9863 | -0.26035 | 0 | 0
17 | 0.99182 | -0.15507 | 0 | 0
18 | 0.99178 | -0.15576 | 0.011323 | 0.0028379
19 | 0.97949 | -0.3922 | 0.0065883 | 0.0016512
20 | 0.99191 | -0.15572 | 0 | 0
21 | 0.99268 | -0.14072 | 0.0068962 | 0.0017284
22 | 0.99113 | -0.17085 | 0.0071506 | 0.0017921
23 | 0.9713 | -0.55326 | 0.022503 | 0.0056397
24 | 0.97825 | -0.41641 | 0 | 0
25 | 0.99107 | -0.17189 | 0.014252 | 0.0035718
26 | 0.97124 | -0.5544 | 0.018681 | 0.0046819
27 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.22684 | 0.058328 | -0.22615 | -0.057886 | 0.0006922 | 0.00044216 | 0.33806 | 0.33806 | 0.33806 | 1 | 0 | 0.99667 | -0.062998 | 46.4372
1 | 0.11906 | 0.030039 | -0.11891 | -0.029946 | 0.00014526 | 9.2802e-05 | 0.17723 | 0.17723 | 0.17723 | 1 | 0 | 0.99867 | -0.025513 | 48.6904
2 | 0.20014 | 0.051368 | -0.19989 | -0.051209 | 0.00024864 | 0.00015874 | 0.29923 | 0.29923 | 0.29923 | 0.99667 | -0.062998 | 0.99531 | -0.088633 | 41.1037
3 | 0.087839 | 0.02215 | -0.087623 | -0.022013 | 0.00021573 | 0.00013763 | 0.13093 | 0.13093 | 0.13093 | 0.99867 | -0.025513 | 0.99599 | -0.076961 | 35.9691
4 | 0.031076 | 0.0077957 | -0.031066 | -0.0077894 | 1.0066e-05 | 6.2785e-06 | 0.046305 | 0.046306 | 0.046306 | 0.99867 | -0.025513 | 0.99831 | -0.03231 | 12.7213
5 | 0.17089 | 0.04394 | -0.17057 | -0.043736 | 0.00032067 | 0.00020455 | 0.25588 | 0.25588 | 0.25588 | 0.99531 | -0.088633 | 0.99327 | -0.12732 | 35.1481
6 | 0.06183 | 0.015549 | -0.061818 | -0.015541 | 1.278e-05 | 8.127e-06 | 0.092394 | 0.092394 | 0.092394 | 0.99599 | -0.076961 | 0.99577 | -0.081289 | 25.3829
7 | 0.031066 | 0.0077894 | -0.031056 | -0.0077833 | 9.7568e-06 | 6.0858e-06 | 0.046306 | 0.046306 | 0.046306 | 0.99831 | -0.03231 | 0.99797 | -0.038902 | 12.7213
8 | 0.15251 | 0.039211 | -0.15234 | -0.0391 | 0.00017528 | 0.00011171 | 0.22883 | 0.22883 | 0.22883 | 0.99327 | -0.12732 | 0.99203 | -0.151 | 31.4331
9 | 0.035551 | 0.0089574 | -0.035513 | -0.0089339 | 3.7424e-05 | 2.3492e-05 | 0.053142 | 0.053142 | 0.053142 | 0.99577 | -0.081289 | 0.99462 | -0.10332 | 14.5995
10 | 0.035513 | 0.0089339 | -0.035511 | -0.0089322 | 2.8107e-06 | 1.7644e-06 | 0.053142 | 0.053142 | 0.053142 | 0.99462 | -0.10332 | 0.99453 | -0.10498 | 14.5995
11 | 0.035511 | 0.0089322 | -0.03547 | -0.0089066 | 4.0768e-05 | 2.5593e-05 | 0.053142 | 0.053142 | 0.053142 | 0.99453 | -0.10498 | 0.99329 | -0.12904 | 14.5995
12 | 0.028346 | 0.0071212 | -0.02833 | -0.0071114 | 1.5797e-05 | 9.8082e-06 | 0.04247 | 0.04247 | 0.04247 | 0.99329 | -0.12904 | 0.99268 | -0.14072 | 11.6677
13 | 0.041229 | 0.01035 | -0.041204 | -0.010334 | 2.4817e-05 | 1.5677e-05 | 0.063095 | 0.063095 | 0.063095 | 0.97243 | -0.53089 | 0.97179 | -0.54352 | 17.3337
14 | -0.041229 | -0.01035 | 0.041314 | 0.010404 | 8.4806e-05 | 5.3569e-05 | 0.063095 | 0.063094 | 0.063095 | 0.97243 | -0.53089 | 0.97461 | -0.48786 | 17.3337
15 | 0.041204 | 0.010334 | -0.041185 | -0.010322 | 1.9127e-05 | 1.2082e-05 | 0.063095 | 0.063095 | 0.063095 | 0.97179 | -0.54352 | 0.9713 | -0.55326 | 17.3337
16 | -0.13219 | -0.033178 | 0.13264 | 0.033467 | 0.00045216 | 0.00028901 | 0.20184 | 0.20184 | 0.20184 | 0.97461 | -0.48786 | 0.97825 | -0.41641 | 55.4497
17 | 0.14101 | 0.03626 | -0.14027 | -0.035784 | 0.00074508 | 0.00047628 | 0.21184 | 0.21184 | 0.21184 | 0.99203 | -0.151 | 0.9863 | -0.26035 | 58.1992
18 | 0.011326 | 0.0028392 | -0.011324 | -0.0028381 | 2.1967e-06 | 1.1439e-06 | 0.016989 | 0.016989 | 0.016989 | 0.99203 | -0.151 | 0.99182 | -0.15507 | 4.6673
19 | 0.14027 | 0.035784 | -0.13938 | -0.035217 | 0.00088709 | 0.00056707 | 0.21184 | 0.21185 | 0.21185 | 0.9863 | -0.26035 | 0.97949 | -0.3922 | 58.1992
20 | 0.011324 | 0.0028381 | -0.011323 | -0.0028379 | 3.6813e-07 | 1.9171e-07 | 0.016989 | 0.016989 | 0.016989 | 0.99182 | -0.15507 | 0.99178 | -0.15576 | 4.6673
21 | 0.13279 | 0.033566 | -0.13264 | -0.033467 | 0.00015394 | 9.8396e-05 | 0.20184 | 0.20184 | 0.20184 | 0.97949 | -0.3922 | 0.97825 | -0.41641 | 55.4496
22 | -0.021419 | -0.0053737 | 0.021434 | 0.005383 | 1.5322e-05 | 9.2948e-06 | 0.032133 | 0.032133 | 0.032133 | 0.99191 | -0.15572 | 0.99268 | -0.14072 | 8.8278
23 | 0.021419 | 0.0053737 | -0.021403 | -0.0053643 | 1.5438e-05 | 9.3662e-06 | 0.032133 | 0.032133 | 0.032133 | 0.99191 | -0.15572 | 0.99113 | -0.17085 | 8.8278
24 | 0.014252 | 0.0035722 | -0.014252 | -0.0035718 | 7.0906e-07 | 4.0058e-07 | 0.021398 | 0.021398 | 0.021398 | 0.99113 | -0.17085 | 0.99107 | -0.17189 | 5.8785
25 | 0.018682 | 0.0046825 | -0.018681 | -0.0046819 | 1.0144e-06 | 6.0834e-07 | 0.028621 | 0.028621 | 0.028621 | 0.9713 | -0.55326 | 0.97124 | -0.5544 | 7.8628

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.38013 | 0.096533

## res_load
| p_mw | q_mvar
0 | 0.032584 | 0.0081662
1 | 0.026007 | 0.0065181
2 | 0.029001 | 0.0072684
3 | 0.025792 | 0.0064642
4 | 0.018053 | 0.0045246
5 | 0.026267 | 0.0065831
6 | 0.031056 | 0.0077833
7 | 0.0071239 | 0.0017854
8 | 0.090873 | 0.022775
9 | 0.011323 | 0.0028379
10 | 0.0065883 | 0.0016512
11 | 0.0068962 | 0.0017284
12 | 0.0071506 | 0.0017921
13 | 0.022503 | 0.0056397
14 | 0.014252 | 0.0035718
15 | 0.018681 | 0.0046819

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1