## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-745_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-745_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-745_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_261-745_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_261-745_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_261-745_0_3_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_261-745_0_3_node_8 | 0.4 | n |  | TRUE
7 | bus_LV_261-745_0_3_node_18 | 0.4 | n |  | TRUE
8 | bus_LV_261-745_0_3_node_10 | 0.4 | n |  | TRUE
9 | bus_LV_261-745_0_3_node_32 | 0.4 | n |  | TRUE
10 | bus_LV_261-745_0_3_node_9 | 0.4 | n |  | TRUE
11 | bus_LV_261-745_0_3_node_30 | 0.4 | n |  | TRUE
12 | bus_LV_261-745_0_3_node_23 | 0.4 | n |  | TRUE
13 | bus_LV_261-745_0_3_node_11 | 0.4 | n |  | TRUE
14 | bus_LV_261-745_0_3_node_15 | 0.4 | n |  | TRUE
15 | bus_LV_261-745_0_3_node_28 | 0.4 | n |  | TRUE
16 | bus_LV_261-745_0_3_node_29 | 0.4 | n |  | TRUE
17 | bus_LV_261-745_0_3_node_34 | 0.4 | n |  | TRUE
18 | bus_LV_261-745_0_3_node_26 | 0.4 | n |  | TRUE
19 | bus_LV_261-745_0_3_node_24 | 0.4 | n |  | TRUE
20 | bus_LV_261-745_0_3_node_19 | 0.4 | n |  | TRUE
21 | bus_LV_261-745_0_3_node_20 | 0.4 | n |  | TRUE
22 | bus_LV_261-745_0_3_node_31 | 0.4 | n |  | TRUE
23 | bus_LV_261-745_0_3_node_22 | 0.4 | n |  | TRUE
24 | bus_LV_261-745_0_3_node_27 | 0.4 | n |  | TRUE
25 | bus_LV_261-745_0_3_node_21 | 0.4 | n |  | TRUE
26 | bus_LV_261-745_0_3_node_25 | 0.4 | n |  | TRUE
27 | bus_LV_261-745_0_3_node_33 | 0.4 | n |  | TRUE
28 | bus_MV_539_0_node_175 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-745_0_3_load_0 | 0 | 0.010077 | 0.0025256 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-745_0_3_load_1 | 1 | 0.0085682 | 0.0021474 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-745_0_3_load_4 | 4 | 0.0060453 | 0.0015151 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-745_0_3_load_5 | 5 | 0.0046622 | 0.0011685 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-745_0_3_load_18 | 7 | 0.0021836 | 0.00054725 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-745_0_3_load_32 | 9 | 0.018853 | 0.004725 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-745_0_3_load_30 | 11 | 0.021085 | 0.0052844 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-745_0_3_load_23 | 12 | 0.0062237 | 0.0015598 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-745_0_3_load_34 | 17 | 0.0046939 | 0.0011764 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-745_0_3_load_26 | 18 | 0.017565 | 0.0044022 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-745_0_3_load_24 | 19 | 0.013485 | 0.0033797 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-745_0_3_load_19 | 20 | 0.0029293 | 0.00073414 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-745_0_3_load_20 | 21 | 0.0061481 | 0.0015409 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-745_0_3_load_31 | 22 | 0.019325 | 0.0048434 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-745_0_3_load_22 | 23 | 0.013045 | 0.0032693 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-745_0_3_load_27 | 24 | 0.032779 | 0.0082152 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-745_0_3_load_21 | 25 | 0.092558 | 0.023197 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_261-745_0_3_load_25 | 26 | 0.026077 | 0.0065354 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_261-745_0_3_load_33 | 27 | 0.0059609 | 0.0014939 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 15 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-745_0_3_line_0 |  | 0 | 1 | 0.020236 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-745_0_3_line_1 |  | 0 | 2 | 0.033298 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-745_0_3_line_2 |  | 1 | 3 | 0.008888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-745_0_3_line_3 |  | 2 | 4 | 0.013756 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-745_0_3_line_4 |  | 2 | 5 | 0.018139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_261-745_0_3_line_5 |  | 3 | 6 | 0.029129 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_261-745_0_3_line_6 |  | 4 | 7 | 0.0082917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_261-745_0_3_line_7 |  | 6 | 8 | 0.010753 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_261-745_0_3_line_8 |  | 6 | 9 | 0.0079351 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_261-745_0_3_line_9 |  | 8 | 12 | 0.030656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_261-745_0_3_line_10 |  | 8 | 10 | 0.002024 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_261-745_0_3_line_11 |  | 9 | 22 | 0.01476 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_261-745_0_3_line_12 |  | 10 | 11 | 0.020681 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-745_0_3_line_13 |  | 11 | 18 | 0.020386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_261-745_0_3_line_14 |  | 12 | 23 | 0.0095953 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_261-745_0_3_line_15 |  | 13 | 14 | 0.013414 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
16 | LV_261-745_0_3_line_16 |  | 13 | 15 | 0.022164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
17 | LV_261-745_0_3_line_17 |  | 13 | 16 | 0.056288 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_261-745_0_3_line_18 |  | 13 | 17 | 0.064203 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_261-745_0_3_line_19 |  | 14 | 18 | 0.004313 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_261-745_0_3_line_20 |  | 14 | 19 | 0.0060952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_261-745_0_3_line_21 |  | 15 | 24 | 0.055609 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_261-745_0_3_line_22 |  | 16 | 25 | 0.024273 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_261-745_0_3_line_23 |  | 19 | 26 | 0.021459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_261-745_0_3_line_24 |  | 20 | 21 | 0.012263 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_261-745_0_3_line_25 |  | 21 | 25 | 0.022392 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_261-745_0_3_line_26 |  | 22 | 27 | 0.0052835 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-745_0_3_trafo_28 | 0.63 MVA 20/0.4 kV | 28 | 15 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2685147.0864 | 1246262.7668 | 2685130.5182 | 1246251.1476
1 | 2685174.2969 | 1246281.9592 | 2685164.8739 | 1246275.2412 | 2685147.0864 | 1246262.7668
2 | 2685123.2413 | 1246246.0443 | 2685130.5182 | 1246251.1476
3 | 2685174.2969 | 1246281.9592 | 2685183.1383 | 1246271.4213
4 | 2685174.2969 | 1246281.9592 | 2685186.2999 | 1246290.5157 | 2685189.0891 | 1246292.4578
5 | 2685101.6769 | 1246236.1832 | 2685105.2909 | 1246236.0016 | 2685112.3709 | 1246232.7897 | 2685116.6886 | 1246236.7434 | 2685121.0136 | 1246240.7084 | 2685121.3272 | 1246243.6039 | 2685123.2413 | 1246246.0443
6 | 2685183.1383 | 1246271.4213 | 2685188.4677 | 1246265.0692
7 | 2685099.3428 | 1246246.6796 | 2685100.6918 | 1246240.5945 | 2685101.6769 | 1246236.1832
8 | 2685101.6769 | 1246236.1832 | 2685093.8681 | 1246234.7736
9 | 2685099.3428 | 1246246.6796 | 2685095.6669 | 1246246.4378 | 2685081.5827 | 1246243.9006 | 2685069.1232 | 1246241.6508
10 | 2685099.3428 | 1246246.6796 | 2685099.2986 | 1246248.7027
11 | 2685079.3424 | 1246232.1515 | 2685093.8681 | 1246234.7736
12 | 2685099.2986 | 1246248.7027 | 2685095.9553 | 1246252.1351 | 2685093.8598 | 1246256.0079 | 2685085.8679 | 1246264.2584
13 | 2685085.8679 | 1246264.2584 | 2685071.684 | 1246278.9013
14 | 2685069.1232 | 1246241.6508 | 2685059.6807 | 1246239.9457
15 | 2685068.6832 | 1246281.9992 | 2685071.0154 | 1246284.2677 | 2685069.4661 | 1246285.88 | 2685072.0439 | 1246288.4077 | 2685075.1207 | 1246291.4319
16 | 2685075.1207 | 1246291.4319 | 2685076.8046 | 1246293.0794 | 2685090.317 | 1246278.5959
17 | 2685075.1207 | 1246291.4319 | 2685076.8046 | 1246293.0794 | 2685096.9325 | 1246316.1519 | 2685083.7138 | 1246329.65 | 2685086.8958 | 1246332.7201
18 | 2685075.1207 | 1246291.4319 | 2685029.6743 | 1246336.7821
19 | 2685068.6832 | 1246281.9992 | 2685071.684 | 1246278.9013
20 | 2685068.6832 | 1246281.9992 | 2685064.385 | 1246286.321
21 | 2685090.317 | 1246278.5959 | 2685107.7967 | 1246259.8551 | 2685129.9331 | 1246280.0766
22 | 2685086.8958 | 1246332.7201 | 2685104.3552 | 1246349.583
23 | 2685064.385 | 1246286.321 | 2685059.0013 | 1246291.7342 | 2685049.408 | 1246301.6886
24 | 2685088.9452 | 1246365.8288 | 2685080.5056 | 1246374.7261
25 | 2685088.9452 | 1246365.8288 | 2685104.3552 | 1246349.583
26 | 2685079.3424 | 1246232.1515 | 2685074.1429 | 1246231.2129

## bus_geodata
| x | y | coords
0 | 2685147.0864 | 1246262.7668
1 | 2685130.5182 | 1246251.1476
2 | 2685174.2969 | 1246281.9592
3 | 2685123.2413 | 1246246.0443
4 | 2685183.1383 | 1246271.4213
5 | 2685189.0891 | 1246292.4578
6 | 2685101.6769 | 1246236.1832
7 | 2685188.4677 | 1246265.0692
8 | 2685099.3428 | 1246246.6796
9 | 2685093.8681 | 1246234.7736
10 | 2685099.2986 | 1246248.7027
11 | 2685085.8679 | 1246264.2584
12 | 2685069.1232 | 1246241.6508
13 | 2685075.1207 | 1246291.4319
14 | 2685068.6832 | 1246281.9992
15 | 2685090.317 | 1246278.5959
16 | 2685086.8958 | 1246332.7201
17 | 2685029.6743 | 1246336.7821
18 | 2685071.684 | 1246278.9013
19 | 2685064.385 | 1246286.321
20 | 2685080.5056 | 1246374.7261
21 | 2685088.9452 | 1246365.8288
22 | 2685079.3424 | 1246232.1515
23 | 2685059.6807 | 1246239.9457
24 | 2685129.9331 | 1246280.0766
25 | 2685104.3552 | 1246349.583
26 | 2685049.408 | 1246301.6886
27 | 2685074.1429 | 1246231.2129
28 | 2685076.8045 | 1246293.0794

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98917 | -0.20852 | 0.010077 | 0.0025256
1 | 0.98959 | -0.20025 | 0.0085682 | 0.0021474
2 | 0.98877 | -0.21617 | 0 | 0
3 | 0.98985 | -0.19526 | 0 | 0
4 | 0.98867 | -0.21819 | 0.0060453 | 0.0015151
5 | 0.98869 | -0.21768 | 0.0046622 | 0.0011685
6 | 0.99069 | -0.17893 | 0 | 0
7 | 0.98865 | -0.21851 | 0.0021836 | 0.00054725
8 | 0.99144 | -0.16449 | 0 | 0
9 | 0.99037 | -0.18515 | 0.018853 | 0.004725
10 | 0.99161 | -0.16108 | 0 | 0
11 | 0.99341 | -0.12634 | 0.021085 | 0.0052844
12 | 0.9909 | -0.17497 | 0.0062237 | 0.0015598
13 | 0.99717 | -0.05414 | 0 | 0
14 | 0.9961 | -0.07452 | 0 | 0
15 | 1 | 0 | -0.3162 | -0.079713
16 | 0.99192 | -0.15495 | 0 | 0
17 | 0.99689 | -0.059425 | 0.0046939 | 0.0011764
18 | 0.99558 | -0.084647 | 0.017565 | 0.0044022
19 | 0.99588 | -0.078756 | 0.013485 | 0.0033797
20 | 0.98944 | -0.20301 | 0.0029293 | 0.00073414
21 | 0.98948 | -0.20237 | 0.0061481 | 0.0015409
22 | 0.99003 | -0.19178 | 0.019325 | 0.0048434
23 | 0.99078 | -0.17719 | 0.013045 | 0.0032693
24 | 0.99834 | -0.031824 | 0.032779 | 0.0082152
25 | 0.98966 | -0.19875 | 0.092558 | 0.023197
26 | 0.99537 | -0.088596 | 0.026077 | 0.0065354
27 | 0.99 | -0.19235 | 0.0059609 | 0.0014939
28 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.022974 | -0.0057592 | 0.022983 | 0.0057647 | 9.0642e-06 | 5.5412e-06 | 0.034561 | 0.034561 | 0.034561 | 0.98917 | -0.20852 | 0.98959 | -0.20025 | 9.4947
1 | 0.012897 | 0.0032336 | -0.012892 | -0.003231 | 4.7003e-06 | 2.5809e-06 | 0.019401 | 0.019402 | 0.019402 | 0.98917 | -0.20852 | 0.98877 | -0.21617 | 5.3301
2 | -0.031551 | -0.0079121 | 0.031559 | 0.0079168 | 7.5024e-06 | 4.6873e-06 | 0.047444 | 0.047444 | 0.047444 | 0.98959 | -0.20025 | 0.98985 | -0.19526 | 13.0342
3 | 0.0082297 | 0.0020626 | -0.0082289 | -0.0020623 | 7.9123e-07 | 3.2997e-07 | 0.012385 | 0.012385 | 0.012385 | 0.98877 | -0.21617 | 0.98867 | -0.21819 | 3.4025
4 | 0.0046625 | 0.0011684 | -0.0046622 | -0.0011685 | 3.349e-07 | -1.8304e-08 | 0.0070167 | 0.0070168 | 0.0070168 | 0.98877 | -0.21617 | 0.98869 | -0.21768 | 1.9277
5 | -0.031559 | -0.0079168 | 0.031583 | 0.0079322 | 2.4588e-05 | 1.5362e-05 | 0.047444 | 0.047444 | 0.047444 | 0.98985 | -0.19526 | 0.99069 | -0.17893 | 13.0341
6 | 0.0021836 | 0.00054717 | -0.0021836 | -0.00054725 | 3.3584e-08 | -8.4834e-08 | 0.0032864 | 0.0032865 | 0.0032865 | 0.98867 | -0.21819 | 0.98865 | -0.21851 | 0.90288
7 | -0.075744 | -0.019008 | 0.075796 | 0.019041 | 5.2198e-05 | 3.3268e-05 | 0.11378 | 0.11378 | 0.11378 | 0.99069 | -0.17893 | 0.99144 | -0.16449 | 31.2571
8 | 0.04416 | 0.011076 | -0.044147 | -0.011067 | 1.3093e-05 | 8.2771e-06 | 0.066332 | 0.066332 | 0.066332 | 0.99069 | -0.17893 | 0.99037 | -0.18515 | 18.223
9 | 0.019279 | 0.0048356 | -0.01927 | -0.0048299 | 9.6262e-06 | 5.7656e-06 | 0.028937 | 0.028937 | 0.028937 | 0.99144 | -0.16449 | 0.9909 | -0.17497 | 7.9498
10 | -0.095075 | -0.023877 | 0.095091 | 0.023886 | 1.5459e-05 | 9.8673e-06 | 0.14271 | 0.14271 | 0.14271 | 0.99144 | -0.16449 | 0.99161 | -0.16108 | 39.2068
11 | 0.025294 | 0.0063423 | -0.025286 | -0.0063374 | 7.9951e-06 | 4.927e-06 | 0.038005 | 0.038006 | 0.038006 | 0.99037 | -0.18515 | 0.99003 | -0.19178 | 10.4411
12 | -0.095091 | -0.023886 | 0.095249 | 0.023987 | 0.00015796 | 0.00010083 | 0.14271 | 0.14271 | 0.14271 | 0.99161 | -0.16108 | 0.99341 | -0.12634 | 39.2068
13 | -0.11633 | -0.029272 | 0.11657 | 0.02942 | 0.00023224 | 0.00014837 | 0.1743 | 0.1743 | 0.1743 | 0.99341 | -0.12634 | 0.99558 | -0.084647 | 47.8835
14 | 0.013046 | 0.00327 | -0.013045 | -0.0032693 | 1.381e-06 | 7.6028e-07 | 0.019591 | 0.019591 | 0.019591 | 0.9909 | -0.17497 | 0.99078 | -0.17719 | 5.3822
15 | 0.17395 | 0.0439 | -0.17378 | -0.043792 | 0.0001696 | 0.0001082 | 0.25968 | 0.25968 | 0.25968 | 0.99717 | -0.05414 | 0.9961 | -0.07452 | 35.6704
16 | -0.28099 | -0.071 | 0.28172 | 0.071467 | 0.00073134 | 0.00046748 | 0.4195 | 0.4195 | 0.4195 | 0.99717 | -0.05414 | 1 | 0 | 57.6242
17 | 0.10234 | 0.025923 | -0.10185 | -0.025609 | 0.00049294 | 0.00031475 | 0.15282 | 0.15282 | 0.15282 | 0.99717 | -0.05414 | 0.99192 | -0.15495 | 41.983
18 | 0.0046951 | 0.0011763 | -0.0046939 | -0.0011764 | 1.1818e-06 | -8.0933e-08 | 0.0070061 | 0.0070063 | 0.0070063 | 0.99717 | -0.05414 | 0.99689 | -0.059425 | 1.9248
19 | 0.1342 | 0.033864 | -0.13413 | -0.033822 | 6.505e-05 | 4.1576e-05 | 0.20055 | 0.20055 | 0.20055 | 0.9961 | -0.07452 | 0.99558 | -0.084647 | 55.0958
20 | 0.039582 | 0.0099277 | -0.039574 | -0.0099227 | 7.9921e-06 | 5.0356e-06 | 0.059132 | 0.059132 | 0.059132 | 0.9961 | -0.07452 | 0.99588 | -0.078756 | 16.245
21 | 0.032829 | 0.0082463 | -0.032779 | -0.0082152 | 4.9777e-05 | 3.1129e-05 | 0.048856 | 0.048857 | 0.048857 | 1 | 0 | 0.99834 | -0.031824 | 13.4222
22 | 0.10185 | 0.025609 | -0.10164 | -0.025473 | 0.00021257 | 0.00013573 | 0.15282 | 0.15282 | 0.15282 | 0.99192 | -0.15495 | 0.98966 | -0.19875 | 41.983
23 | 0.026089 | 0.0065429 | -0.026077 | -0.0065354 | 1.2229e-05 | 7.5474e-06 | 0.038983 | 0.038983 | 0.038983 | 0.99588 | -0.078756 | 0.99537 | -0.088596 | 10.7095
24 | -0.0029293 | -0.00073414 | 0.0029294 | 0.00073404 | 8.9245e-08 | -1.0039e-07 | 0.0044053 | 0.0044052 | 0.0044053 | 0.98944 | -0.20301 | 0.98948 | -0.20237 | 1.2102
25 | -0.0090775 | -0.0022749 | 0.0090791 | 0.0022756 | 1.5648e-06 | 7.1379e-07 | 0.013651 | 0.013651 | 0.013651 | 0.98948 | -0.20237 | 0.98966 | -0.19875 | 3.7503
26 | 0.0059611 | 0.001494 | -0.0059609 | -0.0014939 | 1.5905e-07 | 3.3852e-08 | 0.0089595 | 0.0089596 | 0.0089596 | 0.99003 | -0.19178 | 0.99 | -0.19235 | 2.4614

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.3162 | 0.079713

## res_load
| p_mw | q_mvar
0 | 0.010077 | 0.0025256
1 | 0.0085682 | 0.0021474
2 | 0.0060453 | 0.0015151
3 | 0.0046622 | 0.0011685
4 | 0.0021836 | 0.00054725
5 | 0.018853 | 0.004725
6 | 0.021085 | 0.0052844
7 | 0.0062237 | 0.0015598
8 | 0.0046939 | 0.0011764
9 | 0.017565 | 0.0044022
10 | 0.013485 | 0.0033797
11 | 0.0029293 | 0.00073414
12 | 0.0061481 | 0.0015409
13 | 0.019325 | 0.0048434
14 | 0.013045 | 0.0032693
15 | 0.032779 | 0.0082152
16 | 0.092558 | 0.023197
17 | 0.026077 | 0.0065354
18 | 0.0059609 | 0.0014939

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1