## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-765_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-765_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-765_0_2_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_261-765_0_2_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_261-765_0_2_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_261-765_0_2_node_7 | 0.4 | n |  | TRUE
6 | bus_LV_261-765_0_2_node_17 | 0.4 | n |  | TRUE
7 | bus_LV_261-765_0_2_node_21 | 0.4 | n |  | TRUE
8 | bus_LV_261-765_0_2_node_14 | 0.4 | n |  | TRUE
9 | bus_LV_261-765_0_2_node_5 | 0.4 | n |  | TRUE
10 | bus_LV_261-765_0_2_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_261-765_0_2_node_24 | 0.4 | n |  | TRUE
12 | bus_LV_261-765_0_2_node_34 | 0.4 | n |  | TRUE
13 | bus_LV_261-765_0_2_node_31 | 0.4 | n |  | TRUE
14 | bus_LV_261-765_0_2_node_11 | 0.4 | n |  | TRUE
15 | bus_LV_261-765_0_2_node_13 | 0.4 | n |  | TRUE
16 | bus_LV_261-765_0_2_node_27 | 0.4 | n |  | TRUE
17 | bus_LV_261-765_0_2_node_19 | 0.4 | n |  | TRUE
18 | bus_LV_261-765_0_2_node_28 | 0.4 | n |  | TRUE
19 | bus_LV_261-765_0_2_node_35 | 0.4 | n |  | TRUE
20 | bus_LV_261-765_0_2_node_15 | 0.4 | n |  | TRUE
21 | bus_LV_261-765_0_2_node_16 | 0.4 | n |  | TRUE
22 | bus_LV_261-765_0_2_node_29 | 0.4 | n |  | TRUE
23 | bus_LV_261-765_0_2_node_26 | 0.4 | n |  | TRUE
24 | bus_LV_261-765_0_2_node_18 | 0.4 | n |  | TRUE
25 | bus_LV_261-765_0_2_node_25 | 0.4 | n |  | TRUE
26 | bus_LV_261-765_0_2_node_20 | 0.4 | n |  | TRUE
27 | bus_LV_261-765_0_2_node_22 | 0.4 | n |  | TRUE
28 | bus_LV_261-765_0_2_node_23 | 0.4 | n |  | TRUE
29 | bus_LV_261-765_0_2_node_30 | 0.4 | n |  | TRUE
30 | bus_LV_261-765_0_2_node_33 | 0.4 | n |  | TRUE
31 | bus_LV_261-765_0_2_node_32 | 0.4 | n |  | TRUE
32 | bus_MV_536_0_node_50 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-765_0_2_load_0 | 0 | 0.0014376 | 0.00036029 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-765_0_2_load_21 | 7 | 0.0025757 | 0.00064553 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-765_0_2_load_24 | 11 | 0.066383 | 0.016637 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-765_0_2_load_34 | 12 | 0.061623 | 0.015444 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-765_0_2_load_31 | 13 | 0.0014511 | 0.00036369 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-765_0_2_load_27 | 16 | 0.0022501 | 0.00056394 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-765_0_2_load_28 | 18 | 0.0011576 | 0.00029013 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-765_0_2_load_35 | 19 | 0.041942 | 0.010512 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-765_0_2_load_29 | 22 | 0.0010497 | 0.00026308 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-765_0_2_load_26 | 23 | 0.00067685 | 0.00016963 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-765_0_2_load_25 | 25 | 0.0006718 | 0.00016837 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-765_0_2_load_20 | 26 | 0.00077799 | 0.00019498 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-765_0_2_load_22 | 27 | 0.026804 | 0.0067178 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-765_0_2_load_23 | 28 | 0.012674 | 0.0031765 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-765_0_2_load_30 | 29 | 0.040421 | 0.010131 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-765_0_2_load_33 | 30 | 0.0045496 | 0.0011402 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-765_0_2_load_32 | 31 | 0.0052861 | 0.0013248 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 27 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-765_0_2_line_0 |  | 0 | 1 | 0.027121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-765_0_2_line_1 |  | 0 | 2 | 0.010036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-765_0_2_line_2 |  | 1 | 3 | 0.004926 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-765_0_2_line_3 |  | 1 | 4 | 0.049601 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-765_0_2_line_4 |  | 2 | 5 | 0.0097358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_261-765_0_2_line_5 |  | 2 | 6 | 0.0093365 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_261-765_0_2_line_6 |  | 3 | 7 | 0.014387 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_261-765_0_2_line_7 |  | 4 | 8 | 0.038622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_261-765_0_2_line_8 |  | 5 | 13 | 0.010508 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_261-765_0_2_line_9 |  | 6 | 24 | 0.0066147 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_261-765_0_2_line_10 |  | 6 | 18 | 0.0086615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_261-765_0_2_line_11 |  | 8 | 19 | 0.04428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_261-765_0_2_line_12 |  | 9 | 10 | 0.017704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
13 | LV_261-765_0_2_line_13 |  | 9 | 11 | 0.0088287 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
14 | LV_261-765_0_2_line_14 |  | 10 | 12 | 0.02211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
15 | LV_261-765_0_2_line_15 |  | 11 | 28 | 0.021865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
16 | LV_261-765_0_2_line_16 |  | 12 | 19 | 0.016454 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_261-765_0_2_line_17 |  | 13 | 29 | 0.058843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_261-765_0_2_line_18 |  | 14 | 15 | 0.009201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_261-765_0_2_line_19 |  | 14 | 16 | 0.0030877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_261-765_0_2_line_20 |  | 15 | 17 | 0.0093337 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_261-765_0_2_line_21 |  | 15 | 18 | 0.020334 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_261-765_0_2_line_22 |  | 17 | 26 | 0.0027663 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_261-765_0_2_line_23 |  | 20 | 21 | 0.0070675 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_261-765_0_2_line_24 |  | 20 | 22 | 0.010875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_261-765_0_2_line_25 |  | 21 | 23 | 0.0094224 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_261-765_0_2_line_26 |  | 23 | 24 | 0.011736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_261-765_0_2_line_27 |  | 24 | 25 | 0.0069507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_261-765_0_2_line_28 |  | 27 | 28 | 0.017561 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
29 | LV_261-765_0_2_line_29 |  | 29 | 31 | 0.021249 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_261-765_0_2_line_30 |  | 30 | 31 | 0.011716 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-765_0_2_trafo_22 | 0.63 MVA 20/0.4 kV | 32 | 27 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2682962.593 | 1248302.5324 | 2682951.7099 | 1248292.2836 | 2682950.2987 | 1248290.5849 | 2682949.3088 | 1248289.0032 | 2682946.4403 | 1248281.4309
1 | 2682942.8849 | 1248272.0453 | 2682946.4403 | 1248281.4309
2 | 2682966.1385 | 1248304.45 | 2682963.3588 | 1248301.7758 | 2682962.593 | 1248302.5324
3 | 2682928.5924 | 1248338.639 | 2682954.7986 | 1248310.6404 | 2682957.4689 | 1248307.6422 | 2682960.0194 | 1248305.0982 | 2682962.593 | 1248302.5324
4 | 2682934.9957 | 1248277.7502 | 2682939.749 | 1248274.3142 | 2682942.8849 | 1248272.0453
5 | 2682939.5479 | 1248263.3255 | 2682940.9974 | 1248267.1375 | 2682942.8849 | 1248272.0453
6 | 2682966.1385 | 1248304.45 | 2682976.0573 | 1248294.0283
7 | 2682928.4765 | 1248365.8129 | 2682942.2485 | 1248351.495 | 2682939.7364 | 1248349.1359 | 2682931.3802 | 1248341.2688 | 2682928.5924 | 1248338.639
8 | 2682934.9957 | 1248277.7502 | 2682933.5756 | 1248277.7637 | 2682932.3204 | 1248278.4133 | 2682926.3622 | 1248283.2502
9 | 2682933.2364 | 1248265.3053 | 2682936.2328 | 1248264.3688 | 2682939.5479 | 1248263.3255
10 | 2682939.5479 | 1248263.3255 | 2682947.6626 | 1248260.2969
11 | 2682928.4765 | 1248365.8129 | 2682906.0734 | 1248388.1384 | 2682897.4141 | 1248397.363
12 | 2682858.2406 | 1248413.2439 | 2682863.9716 | 1248418.728 | 2682864.8883 | 1248419.6081 | 2682865.9167 | 1248420.5899 | 2682871.0291 | 1248425.4872
13 | 2682858.2406 | 1248413.2439 | 2682864.2506 | 1248406.7767
14 | 2682871.0291 | 1248425.4872 | 2682874.6097 | 1248421.6566 | 2682886.1532 | 1248409.3593
15 | 2682864.2506 | 1248406.7767 | 2682873.0316 | 1248397.3277 | 2682879.1642 | 1248390.7875
16 | 2682886.1532 | 1248409.3593 | 2682897.4141 | 1248397.363
17 | 2682880.6775 | 1248320.3367 | 2682926.3622 | 1248283.2502
18 | 2682963.4269 | 1248244.5902 | 2682966.2099 | 1248251.8789 | 2682966.7127 | 1248253.1869
19 | 2682963.4269 | 1248244.5902 | 2682962.3286 | 1248241.7044
20 | 2682966.7127 | 1248253.1869 | 2682968.352 | 1248257.4797 | 2682970.0422 | 1248261.9066
21 | 2682966.7127 | 1248253.1869 | 2682947.6626 | 1248260.2969
22 | 2682970.0422 | 1248261.9066 | 2682967.4505 | 1248262.8741
23 | 2682925.3014 | 1248245.691 | 2682928.681 | 1248244.3484 | 2682931.8781 | 1248243.1033
24 | 2682931.8781 | 1248243.1033 | 2682931.8786 | 1248240.368 | 2682934.3802 | 1248238.6239 | 2682939.164 | 1248236.8837
25 | 2682925.3014 | 1248245.691 | 2682928.835 | 1248254.4257
26 | 2682933.2364 | 1248265.3053 | 2682928.835 | 1248254.4257
27 | 2682933.2364 | 1248265.3053 | 2682932.8572 | 1248265.4223 | 2682927.7723 | 1248269.5571
28 | 2682891.1763 | 1248377.977 | 2682879.1642 | 1248390.7875
29 | 2682880.6775 | 1248320.3367 | 2682864.1802 | 1248333.729
30 | 2682864.1802 | 1248333.729 | 2682855.0844 | 1248341.1129

## bus_geodata
| x | y | coords
0 | 2682946.4403 | 1248281.4309
1 | 2682962.593 | 1248302.5324
2 | 2682942.8849 | 1248272.0453
3 | 2682966.1385 | 1248304.45
4 | 2682928.5924 | 1248338.639
5 | 2682934.9957 | 1248277.7502
6 | 2682939.5479 | 1248263.3255
7 | 2682976.0573 | 1248294.0283
8 | 2682928.4765 | 1248365.8129
9 | 2682858.2406 | 1248413.2439
10 | 2682871.0291 | 1248425.4872
11 | 2682864.2506 | 1248406.7767
12 | 2682886.1532 | 1248409.3593
13 | 2682926.3622 | 1248283.2502
14 | 2682963.4269 | 1248244.5902
15 | 2682966.7127 | 1248253.1869
16 | 2682962.3286 | 1248241.7044
17 | 2682970.0422 | 1248261.9066
18 | 2682947.6626 | 1248260.2969
19 | 2682897.4141 | 1248397.363
20 | 2682931.8781 | 1248243.1033
21 | 2682925.3014 | 1248245.691
22 | 2682939.164 | 1248236.8837
23 | 2682928.835 | 1248254.4257
24 | 2682933.2364 | 1248265.3053
25 | 2682927.7723 | 1248269.5571
26 | 2682967.4505 | 1248262.8741
27 | 2682891.1763 | 1248377.977
28 | 2682879.1642 | 1248390.7875
29 | 2682880.6775 | 1248320.3367
30 | 2682855.0844 | 1248341.1129
31 | 2682864.1802 | 1248333.729
32 | 2682858.2406 | 1248413.2439

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98124 | -0.36087 | 0.0014376 | 0.00036029
1 | 0.98274 | -0.33159 | 0 | 0
2 | 0.98069 | -0.37147 | 0 | 0
3 | 0.98273 | -0.33182 | 0 | 0
4 | 0.98561 | -0.27597 | 0 | 0
5 | 0.98023 | -0.3806 | 0 | 0
6 | 0.98064 | -0.37259 | 0 | 0
7 | 0.98269 | -0.33249 | 0.0025757 | 0.00064553
8 | 0.98784 | -0.23289 | 0 | 0
9 | 0.99502 | -0.094981 | 0 | 0
10 | 0.99367 | -0.12087 | 0 | 0
11 | 0.9957 | -0.082098 | 0.066383 | 0.016637
12 | 0.99199 | -0.15329 | 0.061623 | 0.015444
13 | 0.97972 | -0.39046 | 0.0014511 | 0.00036369
14 | 0.98053 | -0.37474 | 0 | 0
15 | 0.98055 | -0.37436 | 0 | 0
16 | 0.98052 | -0.37486 | 0.0022501 | 0.00056394
17 | 0.98054 | -0.37449 | 0 | 0
18 | 0.9806 | -0.37325 | 0.0011576 | 0.00029013
19 | 0.9904 | -0.18373 | 0.041942 | 0.010512
20 | 0.98059 | -0.37356 | 0 | 0
21 | 0.98059 | -0.37342 | 0 | 0
22 | 0.98058 | -0.37376 | 0.0010497 | 0.00026308
23 | 0.9806 | -0.37324 | 0.00067685 | 0.00016963
24 | 0.98062 | -0.37288 | 0 | 0
25 | 0.98062 | -0.37296 | 0.0006718 | 0.00016837
26 | 0.98054 | -0.37453 | 0.00077799 | 0.00019498
27 | 1 | 0 | -0.24899 | -0.062921
28 | 0.99803 | -0.037561 | 0.012674 | 0.0031765
29 | 0.97698 | -0.44432 | 0.040421 | 0.010131
30 | 0.97673 | -0.44911 | 0.0045496 | 0.0011402
31 | 0.97678 | -0.44813 | 0.0052861 | 0.0013248
32 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.059939 | -0.0151 | 0.060023 | 0.015154 | 8.4079e-05 | 5.3468e-05 | 0.090923 | 0.090923 | 0.090923 | 0.98124 | -0.36087 | 0.98274 | -0.33159 | 24.979
1 | 0.058501 | 0.01474 | -0.058472 | -0.014721 | 2.964e-05 | 1.8843e-05 | 0.088743 | 0.088743 | 0.088743 | 0.98124 | -0.36087 | 0.98069 | -0.37147 | 24.3801
2 | 0.0025758 | 0.00064536 | -0.0025758 | -0.0006454 | 2.8098e-08 | -4.443e-08 | 0.0039001 | 0.0039001 | 0.0039001 | 0.98274 | -0.33159 | 0.98273 | -0.33182 | 1.0715
3 | -0.062599 | -0.015799 | 0.062766 | 0.015906 | 0.00016724 | 0.00010641 | 0.094823 | 0.094823 | 0.094823 | 0.98274 | -0.33159 | 0.98561 | -0.27597 | 26.0504
4 | 0.051887 | 0.013072 | -0.051864 | -0.013058 | 2.2643e-05 | 1.4369e-05 | 0.078753 | 0.078753 | 0.078753 | 0.98069 | -0.37147 | 0.98023 | -0.3806 | 21.6353
5 | 0.0065849 | 0.0016492 | -0.0065846 | -0.0016491 | 3.4949e-07 | 1.0588e-07 | 0.009991 | 0.009991 | 0.009991 | 0.98069 | -0.37147 | 0.98064 | -0.37259 | 2.7448
6 | 0.0025758 | 0.0006454 | -0.0025757 | -0.00064553 | 8.2068e-08 | -1.2976e-07 | 0.0039001 | 0.0039002 | 0.0039002 | 0.98273 | -0.33182 | 0.98269 | -0.33249 | 1.0715
7 | -0.062766 | -0.015906 | 0.062896 | 0.015988 | 0.00013022 | 8.285e-05 | 0.094823 | 0.094823 | 0.094823 | 0.98561 | -0.27597 | 0.98784 | -0.23289 | 26.0503
8 | 0.051864 | 0.013058 | -0.05184 | -0.013042 | 2.4438e-05 | 1.5508e-05 | 0.078753 | 0.078753 | 0.078753 | 0.98023 | -0.3806 | 0.97972 | -0.39046 | 21.6353
9 | 0.0023985 | 0.00060048 | -0.0023984 | -0.00060054 | 3.2851e-08 | -6.2426e-08 | 0.0036392 | 0.0036392 | 0.0036392 | 0.98064 | -0.37259 | 0.98062 | -0.37288 | 0.99979
10 | 0.0041861 | 0.0010486 | -0.004186 | -0.0010486 | 1.3105e-07 | -2.5402e-08 | 0.0063518 | 0.0063519 | 0.0063519 | 0.98064 | -0.37259 | 0.9806 | -0.37325 | 1.745
11 | -0.062896 | -0.015988 | 0.063045 | 0.016083 | 0.0001493 | 9.4985e-05 | 0.094823 | 0.094823 | 0.094823 | 0.98784 | -0.23289 | 0.9904 | -0.18373 | 26.0503
12 | 0.16723 | 0.042436 | -0.16702 | -0.042303 | 0.00020793 | 0.00013261 | 0.25027 | 0.25027 | 0.25027 | 0.99502 | -0.094981 | 0.99367 | -0.12087 | 34.3782
13 | -0.16723 | -0.042436 | 0.16734 | 0.042502 | 0.00010369 | 6.613e-05 | 0.25027 | 0.25027 | 0.25027 | 0.99502 | -0.094981 | 0.9957 | -0.082098 | 34.3782
14 | 0.16702 | 0.042303 | -0.16676 | -0.042137 | 0.00025967 | 0.00016562 | 0.25027 | 0.25027 | 0.25027 | 0.99367 | -0.12087 | 0.99199 | -0.15329 | 34.3782
15 | -0.23372 | -0.059139 | 0.23422 | 0.059459 | 0.00050071 | 0.00031989 | 0.34948 | 0.34948 | 0.34948 | 0.9957 | -0.082098 | 0.99803 | -0.037561 | 48.0053
16 | 0.10514 | 0.026693 | -0.10499 | -0.026595 | 0.00015371 | 9.8164e-05 | 0.15784 | 0.15784 | 0.15784 | 0.99199 | -0.15329 | 0.9904 | -0.18373 | 43.3619
17 | 0.050388 | 0.012679 | -0.050259 | -0.012596 | 0.0001293 | 8.2014e-05 | 0.076549 | 0.076549 | 0.076549 | 0.97972 | -0.39046 | 0.97698 | -0.44432 | 21.0299
18 | -0.0022502 | -0.00056391 | 0.0022502 | 0.00056382 | 4.0233e-08 | -9.0309e-08 | 0.0034147 | 0.0034147 | 0.0034147 | 0.98053 | -0.37474 | 0.98055 | -0.37436 | 0.93812
19 | 0.0022502 | 0.00056391 | -0.0022501 | -0.00056394 | 1.3502e-08 | -3.0305e-08 | 0.0034147 | 0.0034148 | 0.0034148 | 0.98053 | -0.37474 | 0.98052 | -0.37486 | 0.93812
20 | 0.000778 | 0.00019484 | -0.000778 | -0.00019495 | 4.8786e-09 | -1.1461e-07 | 0.0011806 | 0.0011806 | 0.0011806 | 0.98055 | -0.37436 | 0.98054 | -0.37449 | 0.32435
21 | -0.0030282 | -0.00075865 | 0.0030284 | 0.0007585 | 1.6101e-07 | -1.5345e-07 | 0.0045953 | 0.0045952 | 0.0045953 | 0.98055 | -0.37436 | 0.9806 | -0.37325 | 1.2624
22 | 0.000778 | 0.00019495 | -0.00077799 | -0.00019498 | 1.446e-09 | -3.3968e-08 | 0.0011806 | 0.0011806 | 0.0011806 | 0.98054 | -0.37449 | 0.98054 | -0.37453 | 0.32435
23 | -0.0010497 | -0.00026295 | 0.0010497 | 0.00026287 | 6.7245e-09 | -8.4853e-08 | 0.0015929 | 0.0015929 | 0.0015929 | 0.98059 | -0.37356 | 0.98059 | -0.37342 | 0.43761
24 | 0.0010497 | 0.00026295 | -0.0010497 | -0.00026308 | 1.0348e-08 | -1.3057e-07 | 0.0015929 | 0.0015929 | 0.0015929 | 0.98059 | -0.37356 | 0.98058 | -0.37376 | 0.43762
25 | -0.0010497 | -0.00026287 | 0.0010497 | 0.00026276 | 8.9646e-09 | -1.1313e-07 | 0.0015929 | 0.0015928 | 0.0015929 | 0.98059 | -0.37342 | 0.9806 | -0.37324 | 0.4376
26 | -0.0017266 | -0.00043239 | 0.0017266 | 0.00043226 | 3.0208e-08 | -1.2873e-07 | 0.0026199 | 0.0026198 | 0.0026199 | 0.9806 | -0.37324 | 0.98062 | -0.37288 | 0.71975
27 | 0.0006718 | 0.00016828 | -0.0006718 | -0.00016837 | 2.7086e-09 | -8.5955e-08 | 0.0010194 | 0.0010194 | 0.0010194 | 0.98062 | -0.37288 | 0.98062 | -0.37296 | 0.28006
28 | 0.24734 | 0.062921 | -0.24689 | -0.062635 | 0.00044683 | 0.00028551 | 0.36838 | 0.36838 | 0.36838 | 1 | 0 | 0.99803 | -0.037561 | 50.601
29 | 0.0098377 | 0.0024659 | -0.0098359 | -0.002465 | 1.789e-06 | 8.7893e-07 | 0.014984 | 0.014984 | 0.014984 | 0.97698 | -0.44432 | 0.97678 | -0.44813 | 4.1164
30 | -0.0045496 | -0.0011402 | 0.0045498 | 0.0011402 | 2.1106e-07 | -1.1563e-08 | 0.0069311 | 0.0069311 | 0.0069311 | 0.97673 | -0.44911 | 0.97678 | -0.44813 | 1.9042

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.27579 | 0.069639

## res_load
| p_mw | q_mvar
0 | 0.0014376 | 0.00036029
1 | 0.0025757 | 0.00064553
2 | 0.066383 | 0.016637
3 | 0.061623 | 0.015444
4 | 0.0014511 | 0.00036369
5 | 0.0022501 | 0.00056394
6 | 0.0011576 | 0.00029013
7 | 0.041942 | 0.010512
8 | 0.0010497 | 0.00026308
9 | 0.00067685 | 0.00016963
10 | 0.0006718 | 0.00016837
11 | 0.00077799 | 0.00019498
12 | 0.026804 | 0.0067178
13 | 0.012674 | 0.0031765
14 | 0.040421 | 0.010131
15 | 0.0045496 | 0.0011402
16 | 0.0052861 | 0.0013248

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1