## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-770_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-770_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-770_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_261-770_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_261-770_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_261-770_0_3_node_21 | 0.4 | n |  | TRUE
6 | bus_LV_261-770_0_3_node_7 | 0.4 | n |  | TRUE
7 | bus_LV_261-770_0_3_node_10 | 0.4 | n |  | TRUE
8 | bus_LV_261-770_0_3_node_24 | 0.4 | n |  | TRUE
9 | bus_LV_261-770_0_3_node_8 | 0.4 | n |  | TRUE
10 | bus_LV_261-770_0_3_node_9 | 0.4 | n |  | TRUE
11 | bus_LV_261-770_0_3_node_25 | 0.4 | n |  | TRUE
12 | bus_LV_261-770_0_3_node_20 | 0.4 | n |  | TRUE
13 | bus_LV_261-770_0_3_node_29 | 0.4 | n |  | TRUE
14 | bus_LV_261-770_0_3_node_11 | 0.4 | n |  | TRUE
15 | bus_LV_261-770_0_3_node_19 | 0.4 | n |  | TRUE
16 | bus_LV_261-770_0_3_node_18 | 0.4 | n |  | TRUE
17 | bus_LV_261-770_0_3_node_13 | 0.4 | n |  | TRUE
18 | bus_LV_261-770_0_3_node_15 | 0.4 | n |  | TRUE
19 | bus_LV_261-770_0_3_node_27 | 0.4 | n |  | TRUE
20 | bus_LV_261-770_0_3_node_14 | 0.4 | n |  | TRUE
21 | bus_LV_261-770_0_3_node_22 | 0.4 | n |  | TRUE
22 | bus_LV_261-770_0_3_node_16 | 0.4 | n |  | TRUE
23 | bus_LV_261-770_0_3_node_23 | 0.4 | n |  | TRUE
24 | bus_LV_261-770_0_3_node_26 | 0.4 | n |  | TRUE
25 | bus_LV_261-770_0_3_node_28 | 0.4 | n |  | TRUE
26 | bus_LV_261-770_0_3_node_30 | 0.4 | n |  | TRUE
27 | bus_LV_261-770_0_3_node_17 | 0.4 | n |  | TRUE
28 | bus_MV_530_1_node_95 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-770_0_3_load_0 | 0 | 0.02334 | 0.0058494 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-770_0_3_load_1 | 1 | 0.023466 | 0.0058812 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-770_0_3_load_3 | 3 | 0.027813 | 0.0069706 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-770_0_3_load_4 | 4 | 0.029395 | 0.0073671 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-770_0_3_load_21 | 5 | 0.026295 | 0.0065902 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-770_0_3_load_24 | 8 | 0.029599 | 0.0074181 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-770_0_3_load_25 | 11 | 0.014237 | 0.0035682 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-770_0_3_load_20 | 12 | 0.012863 | 0.0032237 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-770_0_3_load_29 | 13 | 0.036302 | 0.0090983 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-770_0_3_load_19 | 15 | 0.015358 | 0.0038492 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-770_0_3_load_18 | 16 | 0.01572 | 0.0039397 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-770_0_3_load_27 | 19 | 0.026447 | 0.0066283 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-770_0_3_load_22 | 21 | 0.016694 | 0.004184 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-770_0_3_load_23 | 23 | 0.032553 | 0.0081585 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-770_0_3_load_26 | 24 | 0.014223 | 0.0035645 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-770_0_3_load_28 | 25 | 0.013969 | 0.003501 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-770_0_3_load_30 | 26 | 0.020431 | 0.0051206 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_261-770_0_3_load_17 | 27 | 0.012619 | 0.0031627 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 5 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-770_0_3_line_0 |  | 0 | 1 | 0.015132 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-770_0_3_line_1 |  | 0 | 2 | 0.010897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-770_0_3_line_2 |  | 1 | 3 | 0.013747 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-770_0_3_line_3 |  | 2 | 4 | 0.013226 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-770_0_3_line_4 |  | 3 | 5 | 0.013558 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_261-770_0_3_line_5 |  | 5 | 20 | 0.0069819 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
6 | LV_261-770_0_3_line_6 |  | 6 | 7 | 0.011981 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_261-770_0_3_line_7 |  | 6 | 8 | 0.0097381 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_261-770_0_3_line_8 |  | 7 | 13 | 0.0090097 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_261-770_0_3_line_9 |  | 8 | 21 | 0.014739 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_261-770_0_3_line_10 |  | 9 | 10 | 0.017896 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_261-770_0_3_line_11 |  | 9 | 11 | 0.010358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_261-770_0_3_line_12 |  | 10 | 12 | 0.02204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-770_0_3_line_13 |  | 11 | 24 | 0.012148 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_261-770_0_3_line_14 |  | 12 | 15 | 0.014768 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_261-770_0_3_line_15 |  | 14 | 15 | 0.016688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_261-770_0_3_line_16 |  | 14 | 16 | 0.013207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_261-770_0_3_line_17 |  | 16 | 27 | 0.01555 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_261-770_0_3_line_18 |  | 17 | 18 | 0.012025 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_261-770_0_3_line_19 |  | 17 | 19 | 0.010191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_261-770_0_3_line_20 |  | 18 | 23 | 0.0085343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_261-770_0_3_line_21 |  | 18 | 24 | 0.021707 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_261-770_0_3_line_22 |  | 19 | 22 | 0.022069 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
23 | LV_261-770_0_3_line_23 |  | 20 | 21 | 0.0073986 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_261-770_0_3_line_24 |  | 20 | 22 | 0.012196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
25 | LV_261-770_0_3_line_25 |  | 22 | 25 | 0.0076355 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_261-770_0_3_line_26 |  | 25 | 26 | 0.00015815 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-770_0_3_trafo_21 | 0.63 MVA 20/0.4 kV | 28 | 5 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3
0 | 2682376.48 | 1248618.7906 | 2682384.3079 | 1248631.7404
1 | 2682370.8426 | 1248609.4646 | 2682376.48 | 1248618.7906
2 | 2682395.6559 | 1248625.9548 | 2682384.8468 | 1248632.6318 | 2682384.3079 | 1248631.7404
3 | 2682370.8426 | 1248609.4646 | 2682382.2753 | 1248602.8147
4 | 2682395.6559 | 1248625.9548 | 2682400.2772 | 1248632.5128 | 2682403.4658 | 1248637.0377
5 | 2682407.4906 | 1248642.7428 | 2682406.6314 | 1248641.53 | 2682403.4658 | 1248637.0377
6 | 2682381.8821 | 1248661.7232 | 2682385.2285 | 1248666.551 | 2682388.7082 | 1248671.5697
7 | 2682381.8821 | 1248661.7232 | 2682389.7057 | 1248655.9246
8 | 2682388.7082 | 1248671.5697 | 2682395.9829 | 1248666.2543
9 | 2682401.5467 | 1248647.1483 | 2682389.7057 | 1248655.9246
10 | 2682413.639 | 1248584.5742 | 2682418.2376 | 1248581.9028 | 2682413.5732 | 1248573.5541 | 2682416.1698 | 1248572.0224
11 | 2682413.639 | 1248584.5742 | 2682418.8127 | 1248593.5471
12 | 2682416.1698 | 1248572.0224 | 2682425.1812 | 1248588.1818 | 2682426.9296 | 1248591.2571
13 | 2682418.8127 | 1248593.5471 | 2682424.8805 | 1248604.0708
14 | 2682426.9296 | 1248591.2571 | 2682434.2281 | 1248604.0954
15 | 2682442.5741 | 1248618.546 | 2682439.8361 | 1248613.9601 | 2682434.2281 | 1248604.0954
16 | 2682442.5741 | 1248618.546 | 2682451.9917 | 1248609.2867
17 | 2682463.0802 | 1248598.3846 | 2682451.9917 | 1248609.2867
18 | 2682435.2606 | 1248623.1143 | 2682438.5115 | 1248629.3753 | 2682440.7988 | 1248633.7881
19 | 2682440.7988 | 1248633.7881 | 2682432.5282 | 1248639.7429
20 | 2682435.2606 | 1248623.1143 | 2682428.2914 | 1248628.0403
21 | 2682435.2606 | 1248623.1143 | 2682432.9961 | 1248618.1458 | 2682424.8805 | 1248604.0708
22 | 2682414.618 | 1248652.638 | 2682432.5282 | 1248639.7429
23 | 2682407.4906 | 1248642.7428 | 2682401.5467 | 1248647.1483
24 | 2682407.4906 | 1248642.7428 | 2682411.1934 | 1248648.0093 | 2682414.618 | 1248652.638
25 | 2682414.618 | 1248652.638 | 2682416.2414 | 1248654.8289 | 2682419.158 | 1248658.7772
26 | 2682419.158 | 1248658.7772 | 2682419.252 | 1248658.9044

## bus_geodata
| x | y | coords
0 | 2682376.48 | 1248618.7906
1 | 2682384.3079 | 1248631.7404
2 | 2682370.8426 | 1248609.4646
3 | 2682395.6559 | 1248625.9548
4 | 2682382.2753 | 1248602.8147
5 | 2682403.4658 | 1248637.0377
6 | 2682381.8821 | 1248661.7232
7 | 2682388.7082 | 1248671.5697
8 | 2682389.7057 | 1248655.9246
9 | 2682413.639 | 1248584.5742
10 | 2682416.1698 | 1248572.0224
11 | 2682418.8127 | 1248593.5471
12 | 2682426.9296 | 1248591.2571
13 | 2682395.9829 | 1248666.2543
14 | 2682442.5741 | 1248618.546
15 | 2682434.2281 | 1248604.0954
16 | 2682451.9917 | 1248609.2867
17 | 2682440.7988 | 1248633.7881
18 | 2682435.2606 | 1248623.1143
19 | 2682432.5281 | 1248639.7429
20 | 2682407.4906 | 1248642.7428
21 | 2682401.5467 | 1248647.1483
22 | 2682414.618 | 1248652.638
23 | 2682428.2914 | 1248628.0403
24 | 2682424.8805 | 1248604.0708
25 | 2682419.158 | 1248658.7772
26 | 2682419.252 | 1248658.9044
27 | 2682463.0802 | 1248598.3846
28 | 2682407.4906 | 1248642.7428

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99704 | -0.056915 | 0.02334 | 0.0058494
1 | 0.99777 | -0.042934 | 0.023466 | 0.0058812
2 | 0.99675 | -0.062533 | 0 | 0
3 | 0.99872 | -0.024612 | 0.027813 | 0.0069706
4 | 0.99639 | -0.069356 | 0.029395 | 0.0073671
5 | 1 | 0 | -0.36825 | -0.092485
6 | 0.99741 | -0.049754 | 0 | 0
7 | 0.99701 | -0.057377 | 0 | 0
8 | 0.99773 | -0.043562 | 0.029599 | 0.0074181
9 | 0.99131 | -0.16689 | 0 | 0
10 | 0.99038 | -0.18486 | 0 | 0
11 | 0.99185 | -0.15651 | 0.014237 | 0.0035682
12 | 0.98924 | -0.20704 | 0.012863 | 0.0032237
13 | 0.99672 | -0.063114 | 0.036302 | 0.0090983
14 | 0.98821 | -0.22698 | 0 | 0
15 | 0.98865 | -0.21854 | 0.015358 | 0.0038492
16 | 0.98787 | -0.23366 | 0.01572 | 0.0039397
17 | 0.99562 | -0.083798 | 0 | 0
18 | 0.99433 | -0.10869 | 0 | 0
19 | 0.99672 | -0.062752 | 0.026447 | 0.0066283
20 | 0.99917 | -0.015896 | 0 | 0
21 | 0.99861 | -0.02657 | 0.016694 | 0.004184
22 | 0.99818 | -0.03491 | 0 | 0
23 | 0.99408 | -0.11359 | 0.032553 | 0.0081585
24 | 0.99264 | -0.14128 | 0.014223 | 0.0035645
25 | 0.99794 | -0.039506 | 0.013969 | 0.003501
26 | 0.99793 | -0.039562 | 0.020431 | 0.0051206
27 | 0.98769 | -0.23717 | 0.012619 | 0.0031627
28 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.052752 | -0.013227 | 0.052787 | 0.01325 | 3.5173e-05 | 2.2314e-05 | 0.078731 | 0.078731 | 0.078731 | 0.99704 | -0.056915 | 0.99777 | -0.042934 | 21.6294
1 | 0.029412 | 0.0073779 | -0.029405 | -0.007373 | 7.8751e-06 | 4.898e-06 | 0.043898 | 0.043898 | 0.043898 | 0.99704 | -0.056915 | 0.99675 | -0.062533 | 12.06
2 | -0.076253 | -0.019131 | 0.07632 | 0.019173 | 6.6675e-05 | 4.2492e-05 | 0.11373 | 0.11373 | 0.11373 | 0.99777 | -0.042934 | 0.99872 | -0.024612 | 31.2438
3 | 0.029405 | 0.007373 | -0.029395 | -0.0073671 | 9.5578e-06 | 5.9447e-06 | 0.043898 | 0.043898 | 0.043898 | 0.99675 | -0.062533 | 0.99639 | -0.069356 | 12.06
4 | -0.10413 | -0.026144 | 0.10426 | 0.026222 | 0.00012241 | 7.8167e-05 | 0.15517 | 0.15517 | 0.15517 | 0.99872 | -0.024612 | 1 | 0 | 42.6283
5 | 0.26234 | 0.066263 | -0.26214 | -0.066135 | 0.00019968 | 0.00012761 | 0.39055 | 0.39055 | 0.39055 | 1 | 0 | 0.99917 | -0.015896 | 53.6475
6 | 0.036326 | 0.0091128 | -0.036312 | -0.0091045 | 1.3197e-05 | 8.2898e-06 | 0.054197 | 0.054197 | 0.054197 | 0.99741 | -0.049754 | 0.99701 | -0.057377 | 14.8892
7 | -0.036326 | -0.0091128 | 0.036336 | 0.0091195 | 1.0726e-05 | 6.7377e-06 | 0.054197 | 0.054197 | 0.054197 | 0.99741 | -0.049754 | 0.99773 | -0.043562 | 14.8892
8 | 0.036312 | 0.0091045 | -0.036302 | -0.0090983 | 9.924e-06 | 6.2339e-06 | 0.054197 | 0.054197 | 0.054197 | 0.99701 | -0.057377 | 0.99672 | -0.063114 | 14.8892
9 | -0.065935 | -0.016538 | 0.065988 | 0.016572 | 5.3451e-05 | 3.4016e-05 | 0.09834 | 0.09834 | 0.09834 | 0.99773 | -0.043562 | 0.99861 | -0.02657 | 27.0165
10 | 0.056715 | 0.014273 | -0.056666 | -0.014242 | 4.8663e-05 | 3.0914e-05 | 0.085153 | 0.085153 | 0.085153 | 0.99131 | -0.16689 | 0.99038 | -0.18486 | 23.3938
11 | -0.056715 | -0.014273 | 0.056743 | 0.014291 | 2.8164e-05 | 1.7891e-05 | 0.085153 | 0.085153 | 0.085153 | 0.99131 | -0.16689 | 0.99185 | -0.15651 | 23.3938
12 | 0.056666 | 0.014242 | -0.056606 | -0.014204 | 5.993e-05 | 3.8072e-05 | 0.085153 | 0.085154 | 0.085154 | 0.99038 | -0.18486 | 0.98924 | -0.20704 | 23.3938
13 | -0.070981 | -0.017859 | 0.071032 | 0.017892 | 5.1681e-05 | 3.2919e-05 | 0.10651 | 0.10651 | 0.10651 | 0.99185 | -0.15651 | 0.99264 | -0.14128 | 29.2618
14 | 0.043744 | 0.010981 | -0.04372 | -0.010965 | 2.3982e-05 | 1.5159e-05 | 0.065806 | 0.065806 | 0.065806 | 0.98924 | -0.20704 | 0.98865 | -0.21854 | 18.0785
15 | -0.02835 | -0.0071092 | 0.028362 | 0.0071163 | 1.1405e-05 | 7.0853e-06 | 0.04269 | 0.04269 | 0.04269 | 0.98821 | -0.22698 | 0.98865 | -0.21854 | 11.728
16 | 0.02835 | 0.0071092 | -0.028341 | -0.0071036 | 9.0258e-06 | 5.6074e-06 | 0.04269 | 0.04269 | 0.04269 | 0.98821 | -0.22698 | 0.98787 | -0.23366 | 11.728
17 | 0.012621 | 0.0031638 | -0.012619 | -0.0031627 | 2.1077e-06 | 1.1499e-06 | 0.019012 | 0.019012 | 0.019012 | 0.98787 | -0.23366 | 0.98769 | -0.23717 | 5.223
18 | 0.11809 | 0.029795 | -0.11795 | -0.029705 | 0.00014057 | 8.9811e-05 | 0.17656 | 0.17656 | 0.17656 | 0.99562 | -0.083798 | 0.99433 | -0.10869 | 48.5058
19 | -0.11809 | -0.029795 | 0.11821 | 0.029871 | 0.00011914 | 7.6116e-05 | 0.17656 | 0.17656 | 0.17656 | 0.99562 | -0.083798 | 0.99672 | -0.062752 | 48.5057
20 | 0.032561 | 0.0081633 | -0.032553 | -0.0081585 | 7.599e-06 | 4.7527e-06 | 0.048728 | 0.048728 | 0.048728 | 0.99433 | -0.10869 | 0.99408 | -0.11359 | 13.3868
21 | 0.085388 | 0.021542 | -0.085255 | -0.021457 | 0.00013302 | 8.4853e-05 | 0.12783 | 0.12783 | 0.12783 | 0.99433 | -0.10869 | 0.99264 | -0.14128 | 35.119
22 | -0.14466 | -0.036499 | 0.14485 | 0.036622 | 0.00019314 | 0.00012303 | 0.21604 | 0.21604 | 0.21604 | 0.99672 | -0.062752 | 0.99818 | -0.03491 | 29.6764
23 | 0.082725 | 0.020783 | -0.082683 | -0.020756 | 4.2122e-05 | 2.6861e-05 | 0.12322 | 0.12322 | 0.12322 | 0.99917 | -0.015896 | 0.99861 | -0.02657 | 33.8506
24 | 0.17942 | 0.045353 | -0.17926 | -0.045248 | 0.00016343 | 0.00010428 | 0.26734 | 0.26734 | 0.26734 | 0.99917 | -0.015896 | 0.99818 | -0.03491 | 36.7222
25 | 0.034408 | 0.0086263 | -0.0344 | -0.0086216 | 7.5336e-06 | 4.7217e-06 | 0.051294 | 0.051294 | 0.051294 | 0.99818 | -0.03491 | 0.99794 | -0.039506 | 14.0918
26 | 0.020431 | 0.0051206 | -0.020431 | -0.0051206 | 5.5045e-08 | 3.3163e-08 | 0.030465 | 0.030465 | 0.030465 | 0.99794 | -0.039506 | 0.99793 | -0.039562 | 8.3696

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.39455 | 0.099075

## res_load
| p_mw | q_mvar
0 | 0.02334 | 0.0058494
1 | 0.023466 | 0.0058812
2 | 0.027813 | 0.0069706
3 | 0.029395 | 0.0073671
4 | 0.026295 | 0.0065902
5 | 0.029599 | 0.0074181
6 | 0.014237 | 0.0035682
7 | 0.012863 | 0.0032237
8 | 0.036302 | 0.0090983
9 | 0.015358 | 0.0038492
10 | 0.01572 | 0.0039397
11 | 0.026447 | 0.0066283
12 | 0.016694 | 0.004184
13 | 0.032553 | 0.0081585
14 | 0.014223 | 0.0035645
15 | 0.013969 | 0.003501
16 | 0.020431 | 0.0051206
17 | 0.012619 | 0.0031627

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1