## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-782_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-782_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-782_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_261-782_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_261-782_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_261-782_0_4_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_261-782_0_4_node_21 | 0.4 | n |  | TRUE
7 | bus_LV_261-782_0_4_node_32 | 0.4 | n |  | TRUE
8 | bus_LV_261-782_0_4_node_9 | 0.4 | n |  | TRUE
9 | bus_LV_261-782_0_4_node_20 | 0.4 | n |  | TRUE
10 | bus_LV_261-782_0_4_node_28 | 0.4 | n |  | TRUE
11 | bus_LV_261-782_0_4_node_10 | 0.4 | n |  | TRUE
12 | bus_LV_261-782_0_4_node_14 | 0.4 | n |  | TRUE
13 | bus_LV_261-782_0_4_node_29 | 0.4 | n |  | TRUE
14 | bus_LV_261-782_0_4_node_11 | 0.4 | n |  | TRUE
15 | bus_LV_261-782_0_4_node_23 | 0.4 | n |  | TRUE
16 | bus_LV_261-782_0_4_node_31 | 0.4 | n |  | TRUE
17 | bus_LV_261-782_0_4_node_22 | 0.4 | n |  | TRUE
18 | bus_LV_261-782_0_4_node_27 | 0.4 | n |  | TRUE
19 | bus_LV_261-782_0_4_node_26 | 0.4 | n |  | TRUE
20 | bus_LV_261-782_0_4_node_18 | 0.4 | n |  | TRUE
21 | bus_LV_261-782_0_4_node_19 | 0.4 | n |  | TRUE
22 | bus_LV_261-782_0_4_node_24 | 0.4 | n |  | TRUE
23 | bus_LV_261-782_0_4_node_30 | 0.4 | n |  | TRUE
24 | bus_LV_261-782_0_4_node_16 | 0.4 | n |  | TRUE
25 | bus_LV_261-782_0_4_node_17 | 0.4 | n |  | TRUE
26 | bus_LV_261-782_0_4_node_25 | 0.4 | n |  | TRUE
27 | bus_MV_536_0_node_70 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-782_0_4_load_0 | 0 | 0.060198 | 0.015087 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-782_0_4_load_3 | 3 | 0.034375 | 0.0086151 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-782_0_4_load_4 | 4 | 0.012857 | 0.0032223 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-782_0_4_load_32 | 7 | 0.021527 | 0.0053952 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-782_0_4_load_28 | 10 | 0.013727 | 0.0034403 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-782_0_4_load_29 | 13 | 0.05148 | 0.012902 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-782_0_4_load_23 | 15 | 0.0096573 | 0.0024203 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-782_0_4_load_31 | 16 | 0.051243 | 0.012843 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-782_0_4_load_22 | 17 | 0.071436 | 0.017904 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-782_0_4_load_27 | 18 | 0.02079 | 0.0052104 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-782_0_4_load_26 | 19 | 0.021208 | 0.0053151 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-782_0_4_load_18 | 20 | 0.011441 | 0.0028675 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-782_0_4_load_24 | 22 | 0.007888 | 0.0019769 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-782_0_4_load_30 | 23 | 0.013987 | 0.0035054 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-782_0_4_load_16 | 24 | 0.0032002 | 0.00080206 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-782_0_4_load_17 | 25 | 0.038111 | 0.0095515 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-782_0_4_load_25 | 26 | 0.020289 | 0.0050848 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 15 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-782_0_4_line_0 |  | 0 | 1 | 0.015439 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-782_0_4_line_1 |  | 0 | 2 | 0.017966 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-782_0_4_line_2 |  | 1 | 3 | 0.017271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-782_0_4_line_3 |  | 1 | 4 | 0.024744 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-782_0_4_line_4 |  | 2 | 5 | 0.046286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_261-782_0_4_line_5 |  | 3 | 6 | 0.012085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_261-782_0_4_line_6 |  | 5 | 7 | 0.017273 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_261-782_0_4_line_7 |  | 6 | 17 | 0.014095 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_261-782_0_4_line_8 |  | 6 | 14 | 0.013717 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
9 | LV_261-782_0_4_line_9 |  | 8 | 9 | 0.004926 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_261-782_0_4_line_10 |  | 8 | 10 | 0.027287 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_261-782_0_4_line_11 |  | 9 | 20 | 0.032812 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_261-782_0_4_line_12 |  | 11 | 12 | 0.011752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-782_0_4_line_13 |  | 11 | 13 | 0.019884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_261-782_0_4_line_14 |  | 12 | 16 | 0.028132 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_261-782_0_4_line_15 |  | 12 | 14 | 0.021186 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
16 | LV_261-782_0_4_line_16 |  | 13 | 21 | 0.038442 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_261-782_0_4_line_17 |  | 14 | 15 | 0.0063829 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
18 | LV_261-782_0_4_line_18 |  | 15 | 22 | 0.0084997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_261-782_0_4_line_19 |  | 18 | 19 | 0.018891 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_261-782_0_4_line_20 |  | 19 | 26 | 0.018715 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_261-782_0_4_line_21 |  | 20 | 24 | 0.02348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_261-782_0_4_line_22 |  | 21 | 23 | 0.01827 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_261-782_0_4_line_23 |  | 21 | 25 | 0.037307 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_261-782_0_4_line_24 |  | 22 | 26 | 0.013063 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_261-782_0_4_line_25 |  | 24 | 25 | 0.010908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-782_0_4_trafo_23 | 0.63 MVA 20/0.4 kV | 27 | 15 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2682373.9245 | 1248172.0962 | 2682364.781 | 1248159.6561
1 | 2682354.1407 | 1248145.1794 | 2682364.781 | 1248159.6561
2 | 2682373.9245 | 1248172.0962 | 2682379.0824 | 1248179.7402 | 2682383.4923 | 1248186.474
3 | 2682373.9245 | 1248172.0962 | 2682380.5704 | 1248166.6957 | 2682392.9488 | 1248158.5728 | 2682394.0181 | 1248157.7092
4 | 2682354.1407 | 1248145.1794 | 2682350.1834 | 1248139.7204 | 2682355.5557 | 1248135.7477 | 2682353.1568 | 1248132.2785 | 2682376.4692 | 1248115.6345
5 | 2682390.0101 | 1248196.6489 | 2682388.3713 | 1248193.9241 | 2682383.4923 | 1248186.474
6 | 2682376.4692 | 1248115.6345 | 2682375.7062 | 1248114.5564 | 2682372.9485 | 1248110.8265 | 2682372.1191 | 1248109.6363 | 2682369.5862 | 1248106.0318 | 2682366.4386 | 1248101.5514
7 | 2682390.0101 | 1248196.6489 | 2682377.8358 | 1248203.7515
8 | 2682390.0101 | 1248196.6489 | 2682401.6077 | 1248189.2713
9 | 2682523.2354 | 1248200.6155 | 2682519.1339 | 1248203.3604
10 | 2682523.2354 | 1248200.6155 | 2682546.0017 | 1248185.5726
11 | 2682519.1339 | 1248203.3604 | 2682514.1323 | 1248206.7377 | 2682492.5833 | 1248222.6327
12 | 2682402.1896 | 1248214.2311 | 2682412.0077 | 1248207.7294
13 | 2682402.1896 | 1248214.2311 | 2682412.9875 | 1248230.9276
14 | 2682412.0077 | 1248207.7294 | 2682435.4745 | 1248192.2139
15 | 2682401.6077 | 1248189.2713 | 2682403.2808 | 1248192.2412 | 2682404.18 | 1248193.8437 | 2682405.0497 | 1248195.3903 | 2682406.9293 | 1248198.7189 | 2682407.0914 | 1248199.0102 | 2682408.1087 | 1248200.8034 | 2682410.8653 | 1248205.7009 | 2682412.0077 | 1248207.7294
16 | 2682433.8634 | 1248263.2074 | 2682412.9875 | 1248230.9276
17 | 2682401.6077 | 1248189.2713 | 2682406.8695 | 1248185.6582
18 | 2682406.8695 | 1248185.6582 | 2682413.8765 | 1248180.847
19 | 2682440.0493 | 1248162.8242 | 2682455.5753 | 1248152.062
20 | 2682440.0493 | 1248162.8242 | 2682432.1933 | 1248168.2698 | 2682424.6455 | 1248173.4524
21 | 2682492.5833 | 1248222.6327 | 2682473.6879 | 1248236.5703
22 | 2682433.8634 | 1248263.2074 | 2682418.0787 | 1248272.4066
23 | 2682433.8634 | 1248263.2074 | 2682440.54 | 1248261.0208 | 2682464.9094 | 1248243.0455
24 | 2682424.6455 | 1248173.4524 | 2682413.8765 | 1248180.847
25 | 2682464.9094 | 1248243.0455 | 2682473.6879 | 1248236.5703

## bus_geodata
| x | y | coords
0 | 2682364.781 | 1248159.6561
1 | 2682373.9245 | 1248172.0962
2 | 2682354.1407 | 1248145.1794
3 | 2682383.4923 | 1248186.474
4 | 2682394.0181 | 1248157.7092
5 | 2682376.4692 | 1248115.6345
6 | 2682390.0101 | 1248196.6489
7 | 2682366.4386 | 1248101.5514
8 | 2682523.2354 | 1248200.6155
9 | 2682519.1339 | 1248203.3604
10 | 2682546.0017 | 1248185.5726
11 | 2682402.1896 | 1248214.2311
12 | 2682412.0077 | 1248207.7294
13 | 2682412.9875 | 1248230.9276
14 | 2682401.6077 | 1248189.2713
15 | 2682406.8695 | 1248185.6582
16 | 2682435.4745 | 1248192.2139
17 | 2682377.8358 | 1248203.7515
18 | 2682455.5753 | 1248152.062
19 | 2682440.0493 | 1248162.8242
20 | 2682492.5833 | 1248222.6327
21 | 2682433.8634 | 1248263.2074
22 | 2682413.8765 | 1248180.847
23 | 2682418.0787 | 1248272.4066
24 | 2682473.6879 | 1248236.5703
25 | 2682464.9094 | 1248243.0455
26 | 2682424.6455 | 1248173.4524
27 | 2682401.6077 | 1248189.2713

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99394 | -0.11652 | 0.060198 | 0.015087
1 | 0.99509 | -0.09428 | 0 | 0
2 | 0.99359 | -0.12334 | 0 | 0
3 | 0.99658 | -0.065569 | 0.034375 | 0.0086151
4 | 0.9948 | -0.099882 | 0.012857 | 0.0032223
5 | 0.99268 | -0.14095 | 0 | 0
6 | 0.998 | -0.038257 | 0 | 0
7 | 0.99234 | -0.14753 | 0.021527 | 0.0053952
8 | 0.98724 | -0.24581 | 0 | 0
9 | 0.9873 | -0.24461 | 0 | 0
10 | 0.9869 | -0.25252 | 0.013727 | 0.0034403
11 | 0.99606 | -0.075374 | 0 | 0
12 | 0.99748 | -0.048171 | 0 | 0
13 | 0.99366 | -0.12158 | 0.05148 | 0.012902
14 | 0.99926 | -0.014236 | 0 | 0
15 | 1 | 0 | -0.45771 | -0.11519
16 | 0.99617 | -0.073458 | 0.051243 | 0.012843
17 | 0.99709 | -0.055893 | 0.071436 | 0.017904
18 | 0.99765 | -0.045229 | 0.02079 | 0.0052104
19 | 0.99801 | -0.038354 | 0.021208 | 0.0053151
20 | 0.98772 | -0.23655 | 0.011441 | 0.0028675
21 | 0.99082 | -0.17634 | 0 | 0
22 | 0.99946 | -0.010402 | 0.007888 | 0.0019769
23 | 0.99059 | -0.18088 | 0.013987 | 0.0035054
24 | 0.98826 | -0.226 | 0.0032002 | 0.00080206
25 | 0.98854 | -0.22048 | 0.038111 | 0.0095515
26 | 0.99872 | -0.02461 | 0.020289 | 0.0050848
27 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.081757 | -0.020502 | 0.081844 | 0.020557 | 8.6741e-05 | 5.5314e-05 | 0.1224 | 0.1224 | 0.1224 | 0.99394 | -0.11652 | 0.99509 | -0.09428 | 33.627
1 | 0.021559 | 0.0054145 | -0.021552 | -0.0054103 | 7.0203e-06 | 4.2602e-06 | 0.03228 | 0.03228 | 0.03228 | 0.99394 | -0.11652 | 0.99359 | -0.12334 | 8.8681
2 | -0.094705 | -0.023781 | 0.094835 | 0.023864 | 0.00012992 | 8.2924e-05 | 0.14163 | 0.14163 | 0.14163 | 0.99509 | -0.09428 | 0.99658 | -0.065569 | 38.9104
3 | 0.012861 | 0.0032242 | -0.012857 | -0.0032223 | 3.4319e-06 | 1.8751e-06 | 0.019232 | 0.019232 | 0.019232 | 0.99509 | -0.09428 | 0.9948 | -0.099882 | 5.2835
4 | 0.021552 | 0.0054103 | -0.021534 | -0.0053993 | 1.8086e-05 | 1.0976e-05 | 0.03228 | 0.03228 | 0.03228 | 0.99359 | -0.12334 | 0.99268 | -0.14095 | 8.8682
5 | -0.12921 | -0.032479 | 0.12938 | 0.032587 | 0.00016874 | 0.00010784 | 0.19296 | 0.19296 | 0.19296 | 0.99658 | -0.065569 | 0.998 | -0.038257 | 53.0108
6 | 0.021534 | 0.0053993 | -0.021527 | -0.0053952 | 6.7495e-06 | 4.0964e-06 | 0.03228 | 0.03228 | 0.03228 | 0.99268 | -0.14095 | 0.99234 | -0.14753 | 8.8682
7 | 0.071496 | 0.017942 | -0.071436 | -0.017904 | 6.0072e-05 | 3.8262e-05 | 0.10661 | 0.10661 | 0.10661 | 0.998 | -0.038257 | 0.99709 | -0.055893 | 29.288
8 | -0.20087 | -0.050529 | 0.20111 | 0.050676 | 0.00023081 | 0.00014736 | 0.29957 | 0.29957 | 0.29957 | 0.998 | -0.038257 | 0.99926 | -0.014236 | 41.1494
9 | -0.013731 | -0.0034428 | 0.013732 | 0.0034432 | 7.913e-07 | 4.4344e-07 | 0.020697 | 0.020697 | 0.020697 | 0.98724 | -0.24581 | 0.9873 | -0.24461 | 5.686
10 | 0.013731 | 0.0034428 | -0.013727 | -0.0034403 | 4.3834e-06 | 2.4566e-06 | 0.020697 | 0.020697 | 0.020697 | 0.98724 | -0.24581 | 0.9869 | -0.25252 | 5.686
11 | -0.013732 | -0.0034432 | 0.013737 | 0.0034462 | 5.2708e-06 | 2.9535e-06 | 0.020697 | 0.020697 | 0.020697 | 0.9873 | -0.24461 | 0.98772 | -0.23655 | 5.686
12 | -0.13262 | -0.0335 | 0.1328 | 0.033611 | 0.00017316 | 0.00011067 | 0.19822 | 0.19822 | 0.19822 | 0.99606 | -0.075374 | 0.99748 | -0.048171 | 54.4562
13 | 0.13262 | 0.0335 | -0.13233 | -0.033313 | 0.00029298 | 0.00018725 | 0.19822 | 0.19822 | 0.19822 | 0.99606 | -0.075374 | 0.99366 | -0.12158 | 54.4562
14 | 0.051305 | 0.012882 | -0.051243 | -0.012843 | 6.181e-05 | 3.9192e-05 | 0.076544 | 0.076544 | 0.076544 | 0.99748 | -0.048171 | 0.99617 | -0.073458 | 21.0287
15 | -0.1841 | -0.046493 | 0.1844 | 0.046684 | 0.0002999 | 0.00019138 | 0.27476 | 0.27476 | 0.27476 | 0.99748 | -0.048171 | 0.99926 | -0.014236 | 37.7424
16 | 0.080852 | 0.020411 | -0.08064 | -0.020276 | 0.00021151 | 0.00013487 | 0.12113 | 0.12113 | 0.12113 | 0.99366 | -0.12158 | 0.99082 | -0.17634 | 33.2772
17 | -0.38551 | -0.097361 | 0.38577 | 0.097529 | 0.00026318 | 0.00016818 | 0.57433 | 0.57433 | 0.57433 | 0.99926 | -0.014236 | 1 | 0 | 52.5945
18 | 0.070285 | 0.017658 | -0.07025 | -0.017636 | 3.4874e-05 | 2.2208e-05 | 0.1046 | 0.1046 | 0.1046 | 1 | 0 | 0.99946 | -0.010402 | 28.7365
19 | -0.02079 | -0.0052104 | 0.020797 | 0.0052145 | 6.8117e-06 | 4.1127e-06 | 0.031008 | 0.031008 | 0.031008 | 0.99765 | -0.045229 | 0.99801 | -0.038354 | 8.5188
20 | -0.042004 | -0.01053 | 0.042032 | 0.010547 | 2.7527e-05 | 1.7372e-05 | 0.062629 | 0.062628 | 0.062629 | 0.99801 | -0.038354 | 0.99872 | -0.02461 | 17.2056
21 | -0.025179 | -0.0063137 | 0.025192 | 0.0063215 | 1.267e-05 | 7.808e-06 | 0.037934 | 0.037934 | 0.037934 | 0.98772 | -0.23655 | 0.98826 | -0.226 | 10.4213
22 | 0.01399 | 0.0035071 | -0.013987 | -0.0035054 | 3.0243e-06 | 1.7003e-06 | 0.02101 | 0.02101 | 0.02101 | 0.99082 | -0.17634 | 0.99059 | -0.18088 | 5.772
23 | 0.066651 | 0.016769 | -0.06651 | -0.01668 | 0.00014024 | 8.9271e-05 | 0.10012 | 0.10012 | 0.10012 | 0.99082 | -0.17634 | 0.98854 | -0.22048 | 27.5053
24 | 0.062362 | 0.015659 | -0.06232 | -0.015632 | 4.2239e-05 | 2.6862e-05 | 0.092857 | 0.092857 | 0.092857 | 0.99946 | -0.010402 | 0.99872 | -0.02461 | 25.5101
25 | -0.028392 | -0.0071235 | 0.028399 | 0.0071282 | 7.4766e-06 | 4.6452e-06 | 0.042752 | 0.042752 | 0.042752 | 0.98826 | -0.226 | 0.98854 | -0.22048 | 11.7451

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.46736 | 0.11761

## res_load
| p_mw | q_mvar
0 | 0.060198 | 0.015087
1 | 0.034375 | 0.0086151
2 | 0.012857 | 0.0032223
3 | 0.021527 | 0.0053952
4 | 0.013727 | 0.0034403
5 | 0.05148 | 0.012902
6 | 0.0096573 | 0.0024203
7 | 0.051243 | 0.012843
8 | 0.071436 | 0.017904
9 | 0.02079 | 0.0052104
10 | 0.021208 | 0.0053151
11 | 0.011441 | 0.0028675
12 | 0.007888 | 0.0019769
13 | 0.013987 | 0.0035054
14 | 0.0032002 | 0.00080206
15 | 0.038111 | 0.0095515
16 | 0.020289 | 0.0050848

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1