## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-786_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-786_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-786_0_4_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_261-786_0_4_node_16 | 0.4 | n |  | TRUE
4 | bus_LV_261-786_0_4_node_13 | 0.4 | n |  | TRUE
5 | bus_LV_261-786_0_4_node_15 | 0.4 | n |  | TRUE
6 | bus_LV_261-786_0_4_node_37 | 0.4 | n |  | TRUE
7 | bus_LV_261-786_0_4_node_35 | 0.4 | n |  | TRUE
8 | bus_LV_261-786_0_4_node_14 | 0.4 | n |  | TRUE
9 | bus_LV_261-786_0_4_node_34 | 0.4 | n |  | TRUE
10 | bus_LV_261-786_0_4_node_33 | 0.4 | n |  | TRUE
11 | bus_LV_261-786_0_4_node_9 | 0.4 | n |  | TRUE
12 | bus_LV_261-786_0_4_node_23 | 0.4 | n |  | TRUE
13 | bus_LV_261-786_0_4_node_26 | 0.4 | n |  | TRUE
14 | bus_LV_261-786_0_4_node_12 | 0.4 | n |  | TRUE
15 | bus_LV_261-786_0_4_node_27 | 0.4 | n |  | TRUE
16 | bus_LV_261-786_0_4_node_32 | 0.4 | n |  | TRUE
17 | bus_LV_261-786_0_4_node_11 | 0.4 | n |  | TRUE
18 | bus_LV_261-786_0_4_node_36 | 0.4 | n |  | TRUE
19 | bus_LV_261-786_0_4_node_7 | 0.4 | n |  | TRUE
20 | bus_LV_261-786_0_4_node_17 | 0.4 | n |  | TRUE
21 | bus_LV_261-786_0_4_node_31 | 0.4 | n |  | TRUE
22 | bus_LV_261-786_0_4_node_8 | 0.4 | n |  | TRUE
23 | bus_LV_261-786_0_4_node_5 | 0.4 | n |  | TRUE
24 | bus_LV_261-786_0_4_node_25 | 0.4 | n |  | TRUE
25 | bus_LV_261-786_0_4_node_24 | 0.4 | n |  | TRUE
26 | bus_LV_261-786_0_4_node_19 | 0.4 | n |  | TRUE
27 | bus_LV_261-786_0_4_node_6 | 0.4 | n |  | TRUE
28 | bus_LV_261-786_0_4_node_21 | 0.4 | n |  | TRUE
29 | bus_LV_261-786_0_4_node_22 | 0.4 | n |  | TRUE
30 | bus_LV_261-786_0_4_node_30 | 0.4 | n |  | TRUE
31 | bus_LV_261-786_0_4_node_20 | 0.4 | n |  | TRUE
32 | bus_LV_261-786_0_4_node_29 | 0.4 | n |  | TRUE
33 | bus_LV_261-786_0_4_node_28 | 0.4 | n |  | TRUE
34 | bus_MV_539_0_node_70 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-786_0_4_load_0 | 0 | 0.04637 | 0.011622 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-786_0_4_load_1 | 1 | 0.02715 | 0.0068044 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-786_0_4_load_37 | 6 | 0.027399 | 0.0068669 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-786_0_4_load_35 | 7 | 0.016292 | 0.0040832 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-786_0_4_load_34 | 9 | 0.0075962 | 0.0019038 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-786_0_4_load_33 | 10 | 0.018501 | 0.0046367 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-786_0_4_load_23 | 12 | 0.015925 | 0.0039913 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-786_0_4_load_26 | 13 | 0.027759 | 0.0069572 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-786_0_4_load_27 | 15 | 0.016554 | 0.0041487 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-786_0_4_load_36 | 18 | 0.029144 | 0.0073041 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-786_0_4_load_31 | 21 | 0.018399 | 0.0046113 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-786_0_4_load_5 | 23 | 0.012825 | 0.0032141 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-786_0_4_load_25 | 24 | 0.012009 | 0.0030098 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-786_0_4_load_24 | 25 | 0.011354 | 0.0028455 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-786_0_4_load_19 | 26 | 0.0077506 | 0.0019425 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-786_0_4_load_6 | 27 | 0.011815 | 0.0029612 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-786_0_4_load_21 | 28 | 0.010909 | 0.0027341 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_261-786_0_4_load_22 | 29 | 0.025648 | 0.006428 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_261-786_0_4_load_30 | 30 | 0.016488 | 0.0041322 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_261-786_0_4_load_20 | 31 | 0.0042996 | 0.0010776 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_261-786_0_4_load_29 | 32 | 0.032379 | 0.008115 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_261-786_0_4_load_28 | 33 | 0.016509 | 0.0041376 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 21 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-786_0_4_line_0 |  | 0 | 1 | 0.041672 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-786_0_4_line_1 |  | 1 | 2 | 0.024636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-786_0_4_line_2 |  | 2 | 3 | 0.019217 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-786_0_4_line_3 |  | 3 | 26 | 0.012234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-786_0_4_line_4 |  | 3 | 5 | 0.010275 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
5 | LV_261-786_0_4_line_5 |  | 4 | 5 | 0.010471 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_261-786_0_4_line_6 |  | 4 | 6 | 0.016139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_261-786_0_4_line_7 |  | 5 | 7 | 0.020938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
8 | LV_261-786_0_4_line_8 |  | 7 | 20 | 0.017037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
9 | LV_261-786_0_4_line_9 |  | 8 | 9 | 0.0088169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_261-786_0_4_line_10 |  | 8 | 10 | 0.016789 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_261-786_0_4_line_11 |  | 10 | 16 | 0.01862 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_261-786_0_4_line_12 |  | 11 | 12 | 0.027633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-786_0_4_line_13 |  | 11 | 13 | 0.016622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_261-786_0_4_line_14 |  | 12 | 29 | 0.021494 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_261-786_0_4_line_15 |  | 13 | 15 | 0.024048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_261-786_0_4_line_16 |  | 14 | 15 | 0.017893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_261-786_0_4_line_17 |  | 14 | 16 | 0.009622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_261-786_0_4_line_18 |  | 16 | 30 | 0.014405 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_261-786_0_4_line_19 |  | 17 | 18 | 0.01827 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_261-786_0_4_line_20 |  | 17 | 19 | 0.01091 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_261-786_0_4_line_21 |  | 19 | 22 | 0.017052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_261-786_0_4_line_22 |  | 19 | 23 | 0.0080917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_261-786_0_4_line_23 |  | 20 | 21 | 0.01026 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
24 | LV_261-786_0_4_line_24 |  | 21 | 32 | 0.023421 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
25 | LV_261-786_0_4_line_25 |  | 22 | 24 | 0.030202 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_261-786_0_4_line_26 |  | 22 | 25 | 0.0081159 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_261-786_0_4_line_27 |  | 23 | 27 | 0.013222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_261-786_0_4_line_28 |  | 25 | 28 | 0.012031 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_261-786_0_4_line_29 |  | 26 | 31 | 0.020333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_261-786_0_4_line_30 |  | 28 | 31 | 0.018149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_261-786_0_4_line_31 |  | 30 | 33 | 0.020158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_261-786_0_4_line_32 |  | 32 | 33 | 0.0035909 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-786_0_4_trafo_31 | 0.63 MVA 20/0.4 kV | 34 | 21 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2684250.0804 | 1246070.5063 | 2684235.6771 | 1246093.9508 | 2684229.8995 | 1246101.2408 | 2684228.9124 | 1246102.6501 | 2684227.2879 | 1246105.33
1 | 2684221.5339 | 1246125.829 | 2684217.6323 | 1246121.2591 | 2684227.2879 | 1246105.33
2 | 2684221.5339 | 1246125.829 | 2684216.6542 | 1246134.2659 | 2684213.0514 | 1246131.535 | 2684210.8496 | 1246132.2932 | 2684208.2284 | 1246132.2559
3 | 2684208.2284 | 1246132.2559 | 2684205.753 | 1246130.9977 | 2684201.3701 | 1246128.4002 | 2684197.4875 | 1246126.4116
4 | 2684203.5577 | 1246141.4075 | 2684205.6948 | 1246137.2236 | 2684208.2284 | 1246132.2559
5 | 2684203.5577 | 1246141.4075 | 2684206.4513 | 1246143.0053 | 2684207.7962 | 1246144.0696 | 2684207.9514 | 1246145.3728 | 2684207.616 | 1246146.6467 | 2684210.2217 | 1246147.7734
6 | 2684210.2217 | 1246147.7734 | 2684204.5145 | 1246162.8702 | 2684204.5145 | 1246162.8702
7 | 2684203.5577 | 1246141.4075 | 2684199.2921 | 1246139.0563 | 2684185.7421 | 1246131.8476 | 2684185.0856 | 1246131.553
8 | 2684169.541 | 1246124.579 | 2684185.0856 | 1246131.553
9 | 2684181.2089 | 1246194.6294 | 2684189.9668 | 1246193.6112
10 | 2684181.2089 | 1246194.6294 | 2684164.4285 | 1246194.0922
11 | 2684145.9122 | 1246192.4158 | 2684155.6159 | 1246193.8101 | 2684164.4285 | 1246194.0922
12 | 2684080.138 | 1246174.7368 | 2684094.5774 | 1246151.1764
13 | 2684080.138 | 1246174.7368 | 2684095.9589 | 1246179.8343
14 | 2684094.5774 | 1246151.1764 | 2684098.7776 | 1246144.3232 | 2684105.6859 | 1246132.7757
15 | 2684118.971 | 1246186.8064 | 2684105.2275 | 1246182.8207 | 2684095.9589 | 1246179.8343
16 | 2684136.4005 | 1246190.7908 | 2684124.3767 | 1246188.3741 | 2684118.971 | 1246186.8064
17 | 2684145.9122 | 1246192.4158 | 2684136.4005 | 1246190.7908
18 | 2684145.9122 | 1246192.4158 | 2684150.6504 | 1246178.8127
19 | 2684122.9199 | 1246104.1693 | 2684133.9569 | 1246108.518 | 2684139.7964 | 1246111.1536
20 | 2684128.6726 | 1246094.8997 | 2684125.2535 | 1246100.5109 | 2684122.9199 | 1246104.1693
21 | 2684128.6726 | 1246094.8997 | 2684133.753 | 1246097.8628 | 2684144.025 | 1246102.3562
22 | 2684128.6726 | 1246094.8997 | 2684132.883 | 1246087.9896
23 | 2684169.541 | 1246124.579 | 2684166.1663 | 1246134.2677
24 | 2684158.4624 | 1246156.3851 | 2684166.1663 | 1246134.2677
25 | 2684162.6085 | 1246089.7662 | 2684151.9951 | 1246085.379 | 2684144.025 | 1246102.3562
26 | 2684144.025 | 1246102.3562 | 2684151.4036 | 1246105.736
27 | 2684132.883 | 1246087.9896 | 2684139.7631 | 1246076.6983
28 | 2684162.3418 | 1246110.7462 | 2684151.4036 | 1246105.736
29 | 2684178.8867 | 1246118.2045 | 2684196.5471 | 1246125.9299 | 2684197.4875 | 1246126.4116
30 | 2684178.8867 | 1246118.2045 | 2684173.0601 | 1246115.6557 | 2684162.3418 | 1246110.7462
31 | 2684150.6504 | 1246178.8127 | 2684157.2812 | 1246159.7761
32 | 2684158.4624 | 1246156.3851 | 2684157.2812 | 1246159.7761

## bus_geodata
| x | y | coords
0 | 2684250.0804 | 1246070.5063
1 | 2684227.2879 | 1246105.33
2 | 2684221.5339 | 1246125.829
3 | 2684208.2284 | 1246132.2559
4 | 2684210.2217 | 1246147.7734
5 | 2684203.5577 | 1246141.4075
6 | 2684204.5145 | 1246162.8702
7 | 2684185.0856 | 1246131.553
8 | 2684181.2089 | 1246194.6294
9 | 2684189.9668 | 1246193.6112
10 | 2684164.4285 | 1246194.0922
11 | 2684080.138 | 1246174.7368
12 | 2684094.5774 | 1246151.1764
13 | 2684095.9589 | 1246179.8343
14 | 2684136.4005 | 1246190.7908
15 | 2684118.971 | 1246186.8064
16 | 2684145.9121 | 1246192.4158
17 | 2684122.9199 | 1246104.1693
18 | 2684139.7964 | 1246111.1536
19 | 2684128.6726 | 1246094.8997
20 | 2684169.541 | 1246124.579
21 | 2684166.1663 | 1246134.2677
22 | 2684144.025 | 1246102.3562
23 | 2684132.883 | 1246087.9896
24 | 2684162.6085 | 1246089.7662
25 | 2684151.4036 | 1246105.736
26 | 2684197.4875 | 1246126.4116
27 | 2684139.7631 | 1246076.6983
28 | 2684162.3418 | 1246110.7462
29 | 2684105.6859 | 1246132.7757
30 | 2684150.6504 | 1246178.8127
31 | 2684178.8867 | 1246118.2045
32 | 2684158.4624 | 1246156.3851
33 | 2684157.2812 | 1246159.7761
34 | 2684169.541 | 1246124.579

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98982 | -0.1958 | 0.04637 | 0.011622
1 | 0.99159 | -0.16148 | 0.02715 | 0.0068044
2 | 0.99324 | -0.12943 | 0 | 0
3 | 0.99454 | -0.1045 | 0 | 0
4 | 0.99509 | -0.093844 | 0 | 0
5 | 0.99536 | -0.088795 | 0 | 0
6 | 0.99469 | -0.10163 | 0.027399 | 0.0068669
7 | 0.99728 | -0.05184 | 0.016292 | 0.0040832
8 | 0.99346 | -0.12551 | 0 | 0
9 | 0.9934 | -0.12669 | 0.0075962 | 0.0019038
10 | 0.99357 | -0.12326 | 0.018501 | 0.0046367
11 | 0.98969 | -0.19833 | 0 | 0
12 | 0.98864 | -0.2188 | 0.015925 | 0.0039913
13 | 0.99032 | -0.18605 | 0.027759 | 0.0069572
14 | 0.99326 | -0.12927 | 0 | 0
15 | 0.99185 | -0.15646 | 0.016554 | 0.0041487
16 | 0.99402 | -0.11468 | 0 | 0
17 | 0.98775 | -0.23576 | 0 | 0
18 | 0.98726 | -0.24528 | 0.029144 | 0.0073041
19 | 0.98804 | -0.23008 | 0 | 0
20 | 0.99898 | -0.019451 | 0 | 0
21 | 1 | 0 | -0.39932 | -0.10083
22 | 0.98888 | -0.21372 | 0 | 0
23 | 0.98786 | -0.23364 | 0.012825 | 0.0032141
24 | 0.98855 | -0.22019 | 0.012009 | 0.0030098
25 | 0.98937 | -0.20421 | 0.011354 | 0.0028455
26 | 0.99341 | -0.12611 | 0.0077506 | 0.0019425
27 | 0.98771 | -0.23644 | 0.011815 | 0.0029612
28 | 0.99022 | -0.1877 | 0.010909 | 0.0027341
29 | 0.98813 | -0.22863 | 0.025648 | 0.006428
30 | 0.99549 | -0.086267 | 0.016488 | 0.0041322
31 | 0.99169 | -0.15933 | 0.0042996 | 0.0010776
32 | 0.9981 | -0.03627 | 0.032379 | 0.008115
33 | 0.99786 | -0.040826 | 0.016509 | 0.0041376
34 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.04637 | -0.011622 | 0.046446 | 0.01167 | 7.5938e-05 | 4.8064e-05 | 0.06971 | 0.06971 | 0.06971 | 0.98982 | -0.1958 | 0.99159 | -0.16148 | 19.151
1 | -0.073596 | -0.018474 | 0.073709 | 0.018546 | 0.00011271 | 7.1813e-05 | 0.11045 | 0.11045 | 0.11045 | 0.99159 | -0.16148 | 0.99324 | -0.12943 | 30.3439
2 | -0.073709 | -0.018546 | 0.073797 | 0.018602 | 8.7917e-05 | 5.6018e-05 | 0.11045 | 0.11045 | 0.11045 | 0.99324 | -0.12943 | 0.99454 | -0.1045 | 30.3439
3 | 0.10064 | 0.025429 | -0.10054 | -0.025362 | 0.00010412 | 6.6478e-05 | 0.15065 | 0.15065 | 0.15065 | 0.99454 | -0.1045 | 0.99341 | -0.12611 | 41.3873
4 | -0.17444 | -0.044031 | 0.17457 | 0.044114 | 0.00013134 | 8.3788e-05 | 0.2611 | 0.2611 | 0.2611 | 0.99454 | -0.1045 | 0.99536 | -0.088795 | 35.8656
5 | -0.02741 | -0.0068732 | 0.027416 | 0.0068773 | 6.5969e-06 | 4.0859e-06 | 0.040988 | 0.040988 | 0.040988 | 0.99509 | -0.093844 | 0.99536 | -0.088795 | 11.2605
6 | 0.02741 | 0.0068732 | -0.027399 | -0.0068669 | 1.0168e-05 | 6.298e-06 | 0.040988 | 0.040988 | 0.040988 | 0.99509 | -0.093844 | 0.99469 | -0.10163 | 11.2605
7 | -0.20198 | -0.050992 | 0.20234 | 0.05122 | 0.00035828 | 0.00022875 | 0.30209 | 0.30209 | 0.30209 | 0.99536 | -0.088795 | 0.99728 | -0.05184 | 41.4958
8 | -0.21863 | -0.055304 | 0.21898 | 0.055521 | 0.00034033 | 0.00021736 | 0.3264 | 0.3264 | 0.3264 | 0.99728 | -0.05184 | 0.99898 | -0.019451 | 44.8349
9 | 0.0075966 | 0.0019039 | -0.0075962 | -0.0019038 | 4.2806e-07 | 1.598e-07 | 0.011378 | 0.011378 | 0.011378 | 0.99346 | -0.12551 | 0.9934 | -0.12669 | 3.1259
10 | -0.0075966 | -0.0019039 | 0.0075974 | 0.0019043 | 8.151e-07 | 3.0425e-07 | 0.011378 | 0.011378 | 0.011378 | 0.99346 | -0.12551 | 0.99357 | -0.12326 | 3.1259
11 | -0.026098 | -0.006541 | 0.026109 | 0.0065476 | 1.0667e-05 | 6.5859e-06 | 0.039086 | 0.039086 | 0.039086 | 0.99357 | -0.12326 | 0.99402 | -0.11468 | 10.7379
12 | 0.041626 | 0.010452 | -0.041585 | -0.010427 | 4.0598e-05 | 2.5628e-05 | 0.062593 | 0.062593 | 0.062593 | 0.98969 | -0.19833 | 0.98864 | -0.2188 | 17.1958
13 | -0.041626 | -0.010452 | 0.04165 | 0.010468 | 2.4421e-05 | 1.5415e-05 | 0.062593 | 0.062593 | 0.062593 | 0.98969 | -0.19833 | 0.99032 | -0.18605 | 17.1958
14 | 0.02566 | 0.0064354 | -0.025648 | -0.006428 | 1.2024e-05 | 7.4198e-06 | 0.038623 | 0.038623 | 0.038623 | 0.98864 | -0.2188 | 0.98813 | -0.22863 | 10.6107
15 | -0.06941 | -0.017425 | 0.069508 | 0.017487 | 9.8105e-05 | 6.2478e-05 | 0.1043 | 0.1043 | 0.1043 | 0.99032 | -0.18605 | 0.99185 | -0.15646 | 28.6546
16 | 0.086174 | 0.021708 | -0.086062 | -0.021636 | 0.00011189 | 7.1381e-05 | 0.12914 | 0.12914 | 0.12914 | 0.99326 | -0.12927 | 0.99185 | -0.15646 | 35.4772
17 | -0.086174 | -0.021708 | 0.086234 | 0.021746 | 6.0172e-05 | 3.8386e-05 | 0.12914 | 0.12914 | 0.12914 | 0.99326 | -0.12927 | 0.99402 | -0.11468 | 35.4772
18 | -0.11234 | -0.028293 | 0.1125 | 0.028391 | 0.00015286 | 9.7646e-05 | 0.16822 | 0.16822 | 0.16822 | 0.99402 | -0.11468 | 0.99549 | -0.086267 | 46.215
19 | 0.029157 | 0.0073123 | -0.029144 | -0.0073041 | 1.3219e-05 | 8.2265e-06 | 0.043926 | 0.043926 | 0.043926 | 0.98775 | -0.23576 | 0.98726 | -0.24528 | 12.0676
20 | -0.029157 | -0.0073123 | 0.029165 | 0.0073172 | 7.8941e-06 | 4.9126e-06 | 0.043926 | 0.043926 | 0.043926 | 0.98775 | -0.23576 | 0.98804 | -0.23008 | 12.0675
21 | -0.05381 | -0.013496 | 0.053852 | 0.013523 | 4.1999e-05 | 2.6661e-05 | 0.081043 | 0.081043 | 0.081043 | 0.98804 | -0.23008 | 0.98888 | -0.21372 | 22.2647
22 | 0.024646 | 0.0061787 | -0.024641 | -0.0061762 | 4.1806e-06 | 2.5719e-06 | 0.037118 | 0.037118 | 0.037118 | 0.98804 | -0.23008 | 0.98786 | -0.23364 | 10.1972
23 | -0.21898 | -0.055521 | 0.21918 | 0.055652 | 0.00020494 | 0.00013089 | 0.3264 | 0.3264 | 0.3264 | 0.99898 | -0.019451 | 1 | 0 | 44.8349
24 | 0.17849 | 0.045174 | -0.17818 | -0.044976 | 0.00031015 | 0.00019788 | 0.26576 | 0.26576 | 0.26576 | 1 | 0 | 0.9981 | -0.03627 | 36.5052
25 | 0.012013 | 0.0030118 | -0.012009 | -0.0030098 | 3.7009e-06 | 1.9813e-06 | 0.018077 | 0.018077 | 0.018077 | 0.98888 | -0.21372 | 0.98855 | -0.22019 | 4.9662
26 | -0.065865 | -0.016534 | 0.065895 | 0.016553 | 2.9901e-05 | 1.9033e-05 | 0.09912 | 0.09912 | 0.09912 | 0.98888 | -0.21372 | 0.98937 | -0.20421 | 27.2308
27 | 0.011817 | 0.002962 | -0.011815 | -0.0029612 | 1.571e-06 | 8.3618e-07 | 0.0178 | 0.0178 | 0.0178 | 0.98786 | -0.23364 | 0.98771 | -0.23644 | 4.8901
28 | -0.077249 | -0.019399 | 0.07731 | 0.019438 | 6.0914e-05 | 3.8831e-05 | 0.1162 | 0.1162 | 0.1162 | 0.98937 | -0.20421 | 0.99022 | -0.1877 | 31.922
29 | 0.092786 | 0.02342 | -0.092638 | -0.023326 | 0.0001474 | 9.4076e-05 | 0.13904 | 0.13904 | 0.13904 | 0.99341 | -0.12611 | 0.99169 | -0.15933 | 38.1979
30 | -0.088219 | -0.022172 | 0.088339 | 0.022248 | 0.00011965 | 7.6339e-05 | 0.13259 | 0.13259 | 0.13259 | 0.99022 | -0.1877 | 0.99169 | -0.15933 | 36.4256
31 | -0.12898 | -0.032523 | 0.12926 | 0.032703 | 0.00028119 | 0.0001797 | 0.19287 | 0.19287 | 0.19287 | 0.99549 | -0.086267 | 0.99786 | -0.040826 | 52.9856
32 | 0.14581 | 0.036861 | -0.14577 | -0.036841 | 3.1847e-05 | 2.0288e-05 | 0.21749 | 0.21749 | 0.21749 | 0.9981 | -0.03627 | 0.99786 | -0.040826 | 29.8744

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.41772 | 0.10544

## res_load
| p_mw | q_mvar
0 | 0.04637 | 0.011622
1 | 0.02715 | 0.0068044
2 | 0.027399 | 0.0068669
3 | 0.016292 | 0.0040832
4 | 0.0075962 | 0.0019038
5 | 0.018501 | 0.0046367
6 | 0.015925 | 0.0039913
7 | 0.027759 | 0.0069572
8 | 0.016554 | 0.0041487
9 | 0.029144 | 0.0073041
10 | 0.018399 | 0.0046113
11 | 0.012825 | 0.0032141
12 | 0.012009 | 0.0030098
13 | 0.011354 | 0.0028455
14 | 0.0077506 | 0.0019425
15 | 0.011815 | 0.0029612
16 | 0.010909 | 0.0027341
17 | 0.025648 | 0.006428
18 | 0.016488 | 0.0041322
19 | 0.0042996 | 0.0010776
20 | 0.032379 | 0.008115
21 | 0.016509 | 0.0041376

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1