## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-80_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-80_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-80_0_2_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_261-80_0_2_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_261-80_0_2_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_261-80_0_2_node_40 | 0.4 | n |  | TRUE
6 | bus_LV_261-80_0_2_node_44 | 0.4 | n |  | TRUE
7 | bus_LV_261-80_0_2_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_261-80_0_2_node_20 | 0.4 | n |  | TRUE
9 | bus_LV_261-80_0_2_node_18 | 0.4 | n |  | TRUE
10 | bus_LV_261-80_0_2_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_261-80_0_2_node_14 | 0.4 | n |  | TRUE
12 | bus_LV_261-80_0_2_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_261-80_0_2_node_13 | 0.4 | n |  | TRUE
14 | bus_LV_261-80_0_2_node_37 | 0.4 | n |  | TRUE
15 | bus_LV_261-80_0_2_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_261-80_0_2_node_25 | 0.4 | n |  | TRUE
17 | bus_LV_261-80_0_2_node_21 | 0.4 | n |  | TRUE
18 | bus_LV_261-80_0_2_node_11 | 0.4 | n |  | TRUE
19 | bus_LV_261-80_0_2_node_38 | 0.4 | n |  | TRUE
20 | bus_LV_261-80_0_2_node_39 | 0.4 | n |  | TRUE
21 | bus_LV_261-80_0_2_node_32 | 0.4 | n |  | TRUE
22 | bus_LV_261-80_0_2_node_12 | 0.4 | n |  | TRUE
23 | bus_LV_261-80_0_2_node_33 | 0.4 | n |  | TRUE
24 | bus_LV_261-80_0_2_node_31 | 0.4 | n |  | TRUE
25 | bus_LV_261-80_0_2_node_16 | 0.4 | n |  | TRUE
26 | bus_LV_261-80_0_2_node_17 | 0.4 | n |  | TRUE
27 | bus_LV_261-80_0_2_node_41 | 0.4 | n |  | TRUE
28 | bus_LV_261-80_0_2_node_19 | 0.4 | n |  | TRUE
29 | bus_LV_261-80_0_2_node_36 | 0.4 | n |  | TRUE
30 | bus_LV_261-80_0_2_node_30 | 0.4 | n |  | TRUE
31 | bus_LV_261-80_0_2_node_28 | 0.4 | n |  | TRUE
32 | bus_LV_261-80_0_2_node_42 | 0.4 | n |  | TRUE
33 | bus_LV_261-80_0_2_node_27 | 0.4 | n |  | TRUE
34 | bus_LV_261-80_0_2_node_26 | 0.4 | n |  | TRUE
35 | bus_LV_261-80_0_2_node_22 | 0.4 | n |  | TRUE
36 | bus_LV_261-80_0_2_node_23 | 0.4 | n |  | TRUE
37 | bus_LV_261-80_0_2_node_24 | 0.4 | n |  | TRUE
38 | bus_LV_261-80_0_2_node_35 | 0.4 | n |  | TRUE
39 | bus_LV_261-80_0_2_node_29 | 0.4 | n |  | TRUE
40 | bus_LV_261-80_0_2_node_34 | 0.4 | n |  | TRUE
41 | bus_LV_261-80_0_2_node_43 | 0.4 | n |  | TRUE
42 | bus_MV_530_0_node_105 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-80_0_2_load_0 | 0 | 0.042165 | 0.010568 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-80_0_2_load_1 | 1 | 0.021846 | 0.005475 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-80_0_2_load_40 | 5 | 0.0063764 | 0.0015981 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-80_0_2_load_44 | 6 | 0.014505 | 0.0036353 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-80_0_2_load_20 | 8 | 0.0069643 | 0.0017454 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-80_0_2_load_18 | 9 | 0.0098558 | 0.0024701 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-80_0_2_load_37 | 14 | 0.027174 | 0.0068105 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-80_0_2_load_21 | 17 | 0.0078698 | 0.0019724 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-80_0_2_load_38 | 19 | 0.010967 | 0.0027485 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-80_0_2_load_39 | 20 | 0.012636 | 0.0031668 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-80_0_2_load_32 | 21 | 0.015791 | 0.0039575 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-80_0_2_load_33 | 23 | 0.0030337 | 0.00076031 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-80_0_2_load_31 | 24 | 0.011796 | 0.0029565 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-80_0_2_load_17 | 26 | 0.031165 | 0.0078106 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-80_0_2_load_41 | 27 | 0.014244 | 0.0035698 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-80_0_2_load_19 | 28 | 0.0094023 | 0.0023564 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-80_0_2_load_36 | 29 | 0.0029702 | 0.0007444 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_261-80_0_2_load_30 | 30 | 0.001415 | 0.00035463 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_261-80_0_2_load_27 | 33 | 0.0029806 | 0.00074701 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_261-80_0_2_load_26 | 34 | 0.0032803 | 0.00082212 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_261-80_0_2_load_23 | 36 | 0.0020148 | 0.00050496 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_261-80_0_2_load_24 | 37 | 0.0061538 | 0.0015423 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_261-80_0_2_load_35 | 38 | 0.0017137 | 0.00042949 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_261-80_0_2_load_29 | 39 | 0.0042409 | 0.0010629 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_261-80_0_2_load_34 | 40 | 0.0059654 | 0.0014951 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_261-80_0_2_load_43 | 41 | 0.026169 | 0.0065587 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 41 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-80_0_2_line_0 |  | 0 | 1 | 0.021206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-80_0_2_line_1 |  | 0 | 2 | 0.044628 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-80_0_2_line_2 |  | 1 | 3 | 0.018901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-80_0_2_line_3 |  | 2 | 4 | 0.077585 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-80_0_2_line_4 |  | 3 | 5 | 0.039493 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_261-80_0_2_line_5 |  | 4 | 6 | 0.012558 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_261-80_0_2_line_6 |  | 5 | 22 | 0.025185 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_261-80_0_2_line_7 |  | 7 | 8 | 0.023037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_261-80_0_2_line_8 |  | 7 | 9 | 0.0097522 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_261-80_0_2_line_9 |  | 8 | 10 | 0.002144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_261-80_0_2_line_10 |  | 9 | 28 | 0.022049 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_261-80_0_2_line_11 |  | 10 | 11 | 0.092196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_261-80_0_2_line_12 |  | 11 | 25 | 0.033657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-80_0_2_line_13 |  | 11 | 26 | 0.023876 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_261-80_0_2_line_14 |  | 12 | 13 | 0.040043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_261-80_0_2_line_15 |  | 12 | 14 | 0.039219 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_261-80_0_2_line_16 |  | 13 | 23 | 0.018473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
17 | LV_261-80_0_2_line_17 |  | 13 | 24 | 0.013108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
18 | LV_261-80_0_2_line_18 |  | 14 | 29 | 0.0059448 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_261-80_0_2_line_19 |  | 15 | 16 | 0.007846 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_261-80_0_2_line_20 |  | 15 | 17 | 0.0048641 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_261-80_0_2_line_21 |  | 16 | 19 | 0.016156 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_261-80_0_2_line_22 |  | 16 | 22 | 0.001445 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_261-80_0_2_line_23 |  | 18 | 19 | 0.020534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_261-80_0_2_line_24 |  | 18 | 20 | 0.023867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_261-80_0_2_line_25 |  | 18 | 21 | 0.018425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_261-80_0_2_line_26 |  | 21 | 24 | 0.032423 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_261-80_0_2_line_27 |  | 23 | 32 | 0.012327 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
28 | LV_261-80_0_2_line_28 |  | 25 | 27 | 0.01259 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_261-80_0_2_line_29 |  | 27 | 32 | 0.033285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_261-80_0_2_line_30 |  | 29 | 40 | 0.0089418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_261-80_0_2_line_31 |  | 30 | 31 | 0.017529 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_261-80_0_2_line_32 |  | 31 | 34 | 0.017439 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_261-80_0_2_line_33 |  | 31 | 39 | 0.016919 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_261-80_0_2_line_34 |  | 32 | 41 | 0.0052297 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
35 | LV_261-80_0_2_line_35 |  | 33 | 34 | 0.029047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_261-80_0_2_line_36 |  | 35 | 36 | 0.012881 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_261-80_0_2_line_37 |  | 35 | 37 | 0.017794 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_261-80_0_2_line_38 |  | 36 | 38 | 0.0060383 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_261-80_0_2_line_39 |  | 37 | 39 | 0.020083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_261-80_0_2_line_40 |  | 38 | 40 | 0.0086895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-80_0_2_trafo_43 | 0.63 MVA 20/0.4 kV | 42 | 41 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12
0 | 2682195.2603 | 1249889.6784 | 2682200.1052 | 1249898.8257 | 2682210.0455 | 1249894.4652
1 | 2682177.0948 | 1249849.0587 | 2682185.8612 | 1249866.9935 | 2682188.03 | 1249875.0295 | 2682191.894 | 1249883.3226 | 2682195.2603 | 1249889.6784
2 | 2682227.3544 | 1249886.8725 | 2682210.0455 | 1249894.4652
3 | 2682177.0948 | 1249849.0587 | 2682144.9409 | 1249864.5912 | 2682148.0102 | 1249875.2083 | 2682159.1769 | 1249899.7368 | 2682162.409 | 1249901.872
4 | 2682227.3544 | 1249886.8725 | 2682244.5278 | 1249922.4367
5 | 2682162.409 | 1249901.872 | 2682150.9737 | 1249907.0618
6 | 2682254.0327 | 1249945.4082 | 2682254.2571 | 1249942.8427 | 2682253.6147 | 1249941.2549 | 2682244.5278 | 1249922.4367
7 | 2682058.1028 | 1249907.1312 | 2682052.7442 | 1249906.9791 | 2682036.4243 | 1249913.7694
8 | 2682058.1028 | 1249907.1312 | 2682062.2588 | 1249915.9536
9 | 2682035.3781 | 1249911.898 | 2682036.4243 | 1249913.7694
10 | 2682071.6551 | 1249935.9004 | 2682062.2588 | 1249915.9536
11 | 2682035.3781 | 1249911.898 | 2682052.0179 | 1249904.356 | 2682055.0205 | 1249903.9862 | 2682060.0238 | 1249903.0881 | 2682063.639 | 1249901.5593 | 2682069.5728 | 1249905.978 | 2682079.2014 | 1249908.5688 | 2682079.831 | 1249908.3551 | 2682080.6284 | 1249910.2009 | 2682084.4938 | 1249918.4049 | 2682080.5571 | 1249920.2518 | 2682083.3276 | 1249926.2835 | 2682092.2028 | 1249946.1878
12 | 2682107.6975 | 1249976.0467 | 2682102.9878 | 1249968.298 | 2682096.106 | 1249954.9261 | 2682092.2028 | 1249946.1878
13 | 2682092.2028 | 1249946.1878 | 2682114.3016 | 1249937.1498
14 | 2682143.2357 | 1250010.976 | 2682137.6955 | 1250004.8614 | 2682144.8012 | 1250001.5352 | 2682163.5946 | 1249992.7669 | 2682162.2913 | 1249989.8356
15 | 2682143.2357 | 1250010.976 | 2682143.2853 | 1250009.5757 | 2682143.7768 | 1250007.8924 | 2682144.5295 | 1250006.4239 | 2682145.7241 | 1250005.2174 | 2682147.6816 | 1250003.988 | 2682163.5027 | 1249996.6685 | 2682175.2423 | 1249991.1494
16 | 2682162.2913 | 1249989.8356 | 2682154.7954 | 1249972.9522
17 | 2682162.2913 | 1249989.8356 | 2682174.1393 | 1249984.2273
18 | 2682180.6223 | 1249988.6201 | 2682175.2423 | 1249991.1494
19 | 2682256.3716 | 1249953.6912 | 2682253.1336 | 1249946.541
20 | 2682256.3716 | 1249953.6912 | 2682251.9427 | 1249955.7024
21 | 2682253.1336 | 1249946.541 | 2682251.1534 | 1249947.77 | 2682238.6575 | 1249953.686
22 | 2682254.0327 | 1249945.4082 | 2682253.1336 | 1249946.541
23 | 2682220.0987 | 1249962.4723 | 2682238.6575 | 1249953.686
24 | 2682210.496 | 1249940.6118 | 2682220.0987 | 1249962.4723
25 | 2682220.0987 | 1249962.4723 | 2682203.4449 | 1249970.3554
26 | 2682174.1393 | 1249984.2273 | 2682203.4449 | 1249970.3554
27 | 2682149.7933 | 1249961.6859 | 2682154.7954 | 1249972.9522
28 | 2682107.6975 | 1249976.0467 | 2682118.9736 | 1249970.4471
29 | 2682149.7933 | 1249961.6859 | 2682135.5069 | 1249963.4115 | 2682119.9999 | 1249970.9356 | 2682119.6565 | 1249970.108 | 2682118.9736 | 1249970.4471
30 | 2682180.6223 | 1249988.6201 | 2682188.7144 | 1249984.8157
31 | 2682237.1431 | 1250022.5977 | 2682220.0377 | 1250026.4257
32 | 2682237.1431 | 1250022.5977 | 2682254.2189 | 1250019.0586
33 | 2682237.1431 | 1250022.5977 | 2682229.9047 | 1250007.305
34 | 2682149.7933 | 1249961.6859 | 2682154.5203 | 1249959.4485
35 | 2682282.6612 | 1250013.1635 | 2682254.2189 | 1250019.0586
36 | 2682213.6999 | 1249973.0692 | 2682202.0428 | 1249978.5496
37 | 2682213.6999 | 1249973.0692 | 2682221.3127 | 1249989.1528
38 | 2682196.5782 | 1249981.1187 | 2682202.0428 | 1249978.5496
39 | 2682221.3127 | 1249989.1528 | 2682229.9047 | 1250007.305
40 | 2682196.5782 | 1249981.1187 | 2682188.7144 | 1249984.8157

## bus_geodata
| x | y | coords
0 | 2682195.2603 | 1249889.6784
1 | 2682210.0455 | 1249894.4652
2 | 2682177.0948 | 1249849.0587
3 | 2682227.3544 | 1249886.8725
4 | 2682162.409 | 1249901.872
5 | 2682244.5278 | 1249922.4367
6 | 2682150.9737 | 1249907.0618
7 | 2682058.1028 | 1249907.1312
8 | 2682036.4243 | 1249913.7694
9 | 2682062.2588 | 1249915.9536
10 | 2682035.3781 | 1249911.898
11 | 2682092.2028 | 1249946.1878
12 | 2682143.2357 | 1250010.976
13 | 2682162.2913 | 1249989.8356
14 | 2682175.2423 | 1249991.1494
15 | 2682256.3716 | 1249953.6912
16 | 2682253.1336 | 1249946.541
17 | 2682251.9427 | 1249955.7024
18 | 2682220.0987 | 1249962.4723
19 | 2682238.6575 | 1249953.686
20 | 2682210.496 | 1249940.6118
21 | 2682203.4449 | 1249970.3554
22 | 2682254.0327 | 1249945.4082
23 | 2682154.7954 | 1249972.9522
24 | 2682174.1393 | 1249984.2273
25 | 2682107.6975 | 1249976.0467
26 | 2682114.3016 | 1249937.1498
27 | 2682118.9736 | 1249970.4471
28 | 2682071.6551 | 1249935.9004
29 | 2682180.6223 | 1249988.6201
30 | 2682220.0377 | 1250026.4257
31 | 2682237.1431 | 1250022.5977
32 | 2682149.7933 | 1249961.6859
33 | 2682282.6612 | 1250013.1635
34 | 2682254.2189 | 1250019.0586
35 | 2682213.6999 | 1249973.0692
36 | 2682202.0428 | 1249978.5496
37 | 2682221.3127 | 1249989.1528
38 | 2682196.5782 | 1249981.1187
39 | 2682229.9047 | 1250007.305
40 | 2682188.7144 | 1249984.8157
41 | 2682154.5203 | 1249959.4485
42 | 2682149.7933 | 1249961.6859

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97883 | -0.40777 | 0.042165 | 0.010568
1 | 0.97995 | -0.38593 | 0.021846 | 0.005475
2 | 0.97823 | -0.41955 | 0 | 0
3 | 0.98132 | -0.35903 | 0 | 0
4 | 0.97719 | -0.44007 | 0 | 0
5 | 0.98419 | -0.30306 | 0.0063764 | 0.0015981
6 | 0.97702 | -0.4434 | 0.014505 | 0.0036353
7 | 0.99207 | -0.15249 | 0 | 0
8 | 0.99248 | -0.14464 | 0.0069643 | 0.0017454
9 | 0.9919 | -0.15582 | 0.0098558 | 0.0024701
10 | 0.99253 | -0.14364 | 0 | 0
11 | 0.99474 | -0.10096 | 0 | 0
12 | 0.99434 | -0.10815 | 0 | 0
13 | 0.99646 | -0.067355 | 0 | 0
14 | 0.99226 | -0.14828 | 0.027174 | 0.0068105
15 | 0.98623 | -0.26358 | 0 | 0
16 | 0.98629 | -0.26247 | 0 | 0
17 | 0.9862 | -0.26426 | 0.0078698 | 0.0019724
18 | 0.98965 | -0.19767 | 0 | 0
19 | 0.98768 | -0.23565 | 0.010967 | 0.0027485
20 | 0.98937 | -0.20304 | 0.012636 | 0.0031668
21 | 0.99163 | -0.15959 | 0.015791 | 0.0039575
22 | 0.98617 | -0.26467 | 0 | 0
23 | 0.99817 | -0.03468 | 0.0030337 | 0.00076031
24 | 0.99559 | -0.083933 | 0.011796 | 0.0029565
25 | 0.9965 | -0.066993 | 0 | 0
26 | 0.99406 | -0.11407 | 0.031165 | 0.0078106
27 | 0.99716 | -0.054318 | 0.014244 | 0.0035698
28 | 0.99171 | -0.15949 | 0.0094023 | 0.0023564
29 | 0.99209 | -0.15151 | 0.0029702 | 0.0007444
30 | 0.99071 | -0.17825 | 0.001415 | 0.00035463
31 | 0.99074 | -0.17781 | 0 | 0
32 | 0.99934 | -0.012612 | 0 | 0
33 | 0.99056 | -0.18128 | 0.0029806 | 0.00074701
34 | 0.99064 | -0.17974 | 0.0032803 | 0.00082212
35 | 0.99137 | -0.16554 | 0 | 0
36 | 0.99158 | -0.16142 | 0.0020148 | 0.00050496
37 | 0.99107 | -0.17125 | 0.0061538 | 0.0015423
38 | 0.99169 | -0.15927 | 0.0017137 | 0.00042949
39 | 0.99086 | -0.1755 | 0.0042409 | 0.0010629
40 | 0.99187 | -0.15591 | 0.0059654 | 0.0014951
41 | 1 | 0 | -0.28119 | -0.071223
42 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.056695 | -0.014217 | 0.056754 | 0.014255 | 5.9075e-05 | 3.7541e-05 | 0.086191 | 0.086191 | 0.086191 | 0.97883 | -0.40777 | 0.97995 | -0.38593 | 23.6787
1 | 0.01453 | 0.0036494 | -0.014522 | -0.0036448 | 8.1672e-06 | 4.6664e-06 | 0.022091 | 0.022091 | 0.022091 | 0.97883 | -0.40777 | 0.97823 | -0.41955 | 6.069
2 | -0.0786 | -0.01973 | 0.078701 | 0.019794 | 0.00010098 | 6.4391e-05 | 0.11936 | 0.11936 | 0.11936 | 0.97995 | -0.38593 | 0.98132 | -0.35903 | 32.7919
3 | 0.014522 | 0.0036448 | -0.014508 | -0.0036367 | 1.4199e-05 | 8.1144e-06 | 0.022091 | 0.022092 | 0.022092 | 0.97823 | -0.41955 | 0.97719 | -0.44007 | 6.0691
4 | -0.078701 | -0.019794 | 0.078912 | 0.019929 | 0.000211 | 0.00013454 | 0.11936 | 0.11936 | 0.11936 | 0.98132 | -0.35903 | 0.98419 | -0.30306 | 32.7918
5 | 0.014508 | 0.0036367 | -0.014505 | -0.0036353 | 2.2983e-06 | 1.3136e-06 | 0.022092 | 0.022092 | 0.022092 | 0.97719 | -0.44007 | 0.97702 | -0.4434 | 6.0691
6 | -0.085288 | -0.021527 | 0.085445 | 0.021627 | 0.00015717 | 0.00010027 | 0.129 | 0.129 | 0.129 | 0.98419 | -0.30306 | 0.98617 | -0.26467 | 35.4403
7 | -0.019263 | -0.0048291 | 0.01927 | 0.0048334 | 7.2117e-06 | 4.3179e-06 | 0.028893 | 0.028893 | 0.028893 | 0.99207 | -0.15249 | 0.99248 | -0.14464 | 7.9376
8 | 0.019263 | 0.0048291 | -0.01926 | -0.0048273 | 3.0529e-06 | 1.828e-06 | 0.028893 | 0.028893 | 0.028893 | 0.99207 | -0.15249 | 0.9919 | -0.15582 | 7.9376
9 | -0.026234 | -0.0065789 | 0.026236 | 0.0065796 | 1.244e-06 | 7.6842e-07 | 0.039334 | 0.039334 | 0.039334 | 0.99248 | -0.14464 | 0.99253 | -0.14364 | 10.8062
10 | 0.0094039 | 0.0023572 | -0.0094023 | -0.0023564 | 1.6456e-06 | 7.6865e-07 | 0.014108 | 0.014108 | 0.014108 | 0.9919 | -0.15582 | 0.99171 | -0.15949 | 3.8757
11 | -0.026236 | -0.0065796 | 0.026289 | 0.0066127 | 5.3491e-05 | 3.304e-05 | 0.039334 | 0.039334 | 0.039334 | 0.99253 | -0.14364 | 0.99474 | -0.10096 | 10.8062
12 | -0.057473 | -0.014435 | 0.057567 | 0.014495 | 9.3314e-05 | 5.9283e-05 | 0.085985 | 0.085985 | 0.085985 | 0.99474 | -0.10096 | 0.9965 | -0.066993 | 23.6222
13 | 0.031184 | 0.0078228 | -0.031165 | -0.0078106 | 1.9485e-05 | 1.2161e-05 | 0.046651 | 0.046651 | 0.046651 | 0.99474 | -0.10096 | 0.99406 | -0.11407 | 12.8162
14 | -0.058049 | -0.0146 | 0.058162 | 0.014672 | 0.00011336 | 7.2032e-05 | 0.086888 | 0.086887 | 0.086888 | 0.99434 | -0.10815 | 0.99646 | -0.067355 | 23.8702
15 | 0.058049 | 0.0146 | -0.057938 | -0.01453 | 0.00011103 | 7.0552e-05 | 0.086888 | 0.086888 | 0.086888 | 0.99434 | -0.10815 | 0.99226 | -0.14828 | 23.8703
16 | -0.20381 | -0.05183 | 0.20413 | 0.052035 | 0.00032139 | 0.00020521 | 0.30462 | 0.30462 | 0.30462 | 0.99646 | -0.067355 | 0.99817 | -0.03468 | 41.8428
17 | 0.14565 | 0.037158 | -0.14553 | -0.037083 | 0.00011651 | 7.4228e-05 | 0.21773 | 0.21773 | 0.21773 | 0.99646 | -0.067355 | 0.99559 | -0.083933 | 29.9077
18 | 0.030763 | 0.0077191 | -0.030759 | -0.0077161 | 4.7453e-06 | 2.9602e-06 | 0.046137 | 0.046137 | 0.046137 | 0.99226 | -0.14828 | 0.99209 | -0.15151 | 12.6749
19 | -0.00787 | -0.0019725 | 0.0078704 | 0.0019726 | 4.1485e-07 | 1.6538e-07 | 0.011874 | 0.011874 | 0.011874 | 0.98623 | -0.26358 | 0.98629 | -0.26247 | 3.2622
20 | 0.00787 | 0.0019725 | -0.0078698 | -0.0019724 | 2.5719e-07 | 1.0253e-07 | 0.011874 | 0.011874 | 0.011874 | 0.98623 | -0.26358 | 0.9862 | -0.26426 | 3.2622
21 | -0.093325 | -0.023605 | 0.093445 | 0.023682 | 0.00012024 | 7.6747e-05 | 0.14088 | 0.14088 | 0.14088 | 0.98629 | -0.26247 | 0.98768 | -0.23565 | 38.7024
22 | 0.085454 | 0.021633 | -0.085445 | -0.021627 | 9.0177e-06 | 5.7529e-06 | 0.129 | 0.129 | 0.129 | 0.98629 | -0.26247 | 0.98617 | -0.26467 | 35.4403
23 | 0.1046 | 0.026552 | -0.10441 | -0.026431 | 0.00019077 | 0.00012183 | 0.1574 | 0.1574 | 0.1574 | 0.98965 | -0.19767 | 0.98768 | -0.23565 | 43.2415
24 | 0.012639 | 0.0031685 | -0.012636 | -0.0031668 | 3.2323e-06 | 1.7621e-06 | 0.019004 | 0.019004 | 0.019004 | 0.98965 | -0.19767 | 0.98937 | -0.20304 | 5.2209
25 | -0.11724 | -0.029721 | 0.11746 | 0.029858 | 0.00021501 | 0.00013737 | 0.1764 | 0.1764 | 0.1764 | 0.98965 | -0.19767 | 0.99163 | -0.15959 | 48.4623
26 | -0.13325 | -0.033816 | 0.13373 | 0.034127 | 0.00048682 | 0.00031114 | 0.2001 | 0.2001 | 0.2001 | 0.99163 | -0.15959 | 0.99559 | -0.083933 | 54.9718
27 | -0.20716 | -0.052795 | 0.20738 | 0.052936 | 0.00022088 | 0.00014104 | 0.30914 | 0.30914 | 0.30914 | 0.99817 | -0.03468 | 0.99934 | -0.012612 | 42.4639
28 | -0.057567 | -0.014495 | 0.057601 | 0.014517 | 3.4905e-05 | 2.2175e-05 | 0.085985 | 0.085984 | 0.085985 | 0.9965 | -0.066993 | 0.99716 | -0.054318 | 23.6221
29 | -0.071845 | -0.018087 | 0.071989 | 0.018178 | 0.00014354 | 9.1433e-05 | 0.10724 | 0.10724 | 0.10724 | 0.99716 | -0.054318 | 0.99934 | -0.012612 | 29.4614
30 | 0.027788 | 0.0069717 | -0.027783 | -0.0069681 | 5.8257e-06 | 3.613e-06 | 0.041682 | 0.041682 | 0.041682 | 0.99209 | -0.15151 | 0.99187 | -0.15591 | 11.451
31 | -0.001415 | -0.00035463 | 0.001415 | 0.00035442 | 2.9688e-08 | -2.0672e-07 | 0.0021253 | 0.0021252 | 0.0021253 | 0.99071 | -0.17825 | 0.99074 | -0.17781 | 0.58386
32 | 0.0062617 | 0.001569 | -0.0062611 | -0.0015689 | 5.7839e-07 | 1.4563e-07 | 0.0094045 | 0.0094046 | 0.0094046 | 0.99074 | -0.17781 | 0.99064 | -0.17974 | 2.5837
33 | -0.0076767 | -0.0019235 | 0.0076775 | 0.0019238 | 8.4342e-07 | 3.2189e-07 | 0.01153 | 0.01153 | 0.01153 | 0.99074 | -0.17781 | 0.99086 | -0.1755 | 3.1675
34 | -0.27937 | -0.071115 | 0.27954 | 0.071223 | 0.00017 | 0.00010866 | 0.41638 | 0.41638 | 0.41638 | 0.99934 | -0.012612 | 1 | 0 | 57.1946
35 | -0.0029806 | -0.00074701 | 0.0029808 | 0.00074678 | 2.1836e-07 | -2.3419e-07 | 0.0044775 | 0.0044773 | 0.0044775 | 0.99056 | -0.18128 | 0.99064 | -0.17974 | 1.2301
36 | -0.01808 | -0.0045331 | 0.018083 | 0.0045352 | 3.5573e-06 | 2.1106e-06 | 0.027138 | 0.027137 | 0.027138 | 0.99137 | -0.16554 | 0.99158 | -0.16142 | 7.4554
37 | 0.01808 | 0.0045331 | -0.018075 | -0.0045302 | 4.9142e-06 | 2.9157e-06 | 0.027138 | 0.027138 | 0.027138 | 0.99137 | -0.16554 | 0.99107 | -0.17125 | 7.4554
38 | -0.020098 | -0.0050402 | 0.0201 | 0.0050414 | 2.0599e-06 | 1.2404e-06 | 0.030161 | 0.030161 | 0.030161 | 0.99158 | -0.16142 | 0.99169 | -0.15927 | 8.286
39 | 0.011921 | 0.0029879 | -0.011918 | -0.0029866 | 2.4126e-06 | 1.2853e-06 | 0.017898 | 0.017898 | 0.017898 | 0.99107 | -0.17125 | 0.99086 | -0.1755 | 4.9171
40 | -0.021814 | -0.0054709 | 0.021817 | 0.0054731 | 3.4912e-06 | 2.1223e-06 | 0.032732 | 0.032732 | 0.032732 | 0.99169 | -0.15927 | 0.99187 | -0.15591 | 8.9924

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.30736 | 0.077782

## res_load
| p_mw | q_mvar
0 | 0.042165 | 0.010568
1 | 0.021846 | 0.005475
2 | 0.0063764 | 0.0015981
3 | 0.014505 | 0.0036353
4 | 0.0069643 | 0.0017454
5 | 0.0098558 | 0.0024701
6 | 0.027174 | 0.0068105
7 | 0.0078698 | 0.0019724
8 | 0.010967 | 0.0027485
9 | 0.012636 | 0.0031668
10 | 0.015791 | 0.0039575
11 | 0.0030337 | 0.00076031
12 | 0.011796 | 0.0029565
13 | 0.031165 | 0.0078106
14 | 0.014244 | 0.0035698
15 | 0.0094023 | 0.0023564
16 | 0.0029702 | 0.0007444
17 | 0.001415 | 0.00035463
18 | 0.0029806 | 0.00074701
19 | 0.0032803 | 0.00082212
20 | 0.0020148 | 0.00050496
21 | 0.0061538 | 0.0015423
22 | 0.0017137 | 0.00042949
23 | 0.0042409 | 0.0010629
24 | 0.0059654 | 0.0014951
25 | 0.026169 | 0.0065587

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1