## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-812_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-812_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-812_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_261-812_0_5_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_261-812_0_5_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_261-812_0_5_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_261-812_0_5_node_55 | 0.4 | n |  | TRUE
7 | bus_LV_261-812_0_5_node_6 | 0.4 | n |  | TRUE
8 | bus_LV_261-812_0_5_node_35 | 0.4 | n |  | TRUE
9 | bus_LV_261-812_0_5_node_23 | 0.4 | n |  | TRUE
10 | bus_LV_261-812_0_5_node_11 | 0.4 | n |  | TRUE
11 | bus_LV_261-812_0_5_node_37 | 0.4 | n |  | TRUE
12 | bus_LV_261-812_0_5_node_7 | 0.4 | n |  | TRUE
13 | bus_LV_261-812_0_5_node_58 | 0.4 | n |  | TRUE
14 | bus_LV_261-812_0_5_node_8 | 0.4 | n |  | TRUE
15 | bus_LV_261-812_0_5_node_52 | 0.4 | n |  | TRUE
16 | bus_LV_261-812_0_5_node_10 | 0.4 | n |  | TRUE
17 | bus_LV_261-812_0_5_node_54 | 0.4 | n |  | TRUE
18 | bus_LV_261-812_0_5_node_51 | 0.4 | n |  | TRUE
19 | bus_LV_261-812_0_5_node_53 | 0.4 | n |  | TRUE
20 | bus_LV_261-812_0_5_node_50 | 0.4 | n |  | TRUE
21 | bus_LV_261-812_0_5_node_14 | 0.4 | n |  | TRUE
22 | bus_LV_261-812_0_5_node_49 | 0.4 | n |  | TRUE
23 | bus_LV_261-812_0_5_node_48 | 0.4 | n |  | TRUE
24 | bus_LV_261-812_0_5_node_15 | 0.4 | n |  | TRUE
25 | bus_LV_261-812_0_5_node_30 | 0.4 | n |  | TRUE
26 | bus_LV_261-812_0_5_node_31 | 0.4 | n |  | TRUE
27 | bus_LV_261-812_0_5_node_29 | 0.4 | n |  | TRUE
28 | bus_LV_261-812_0_5_node_16 | 0.4 | n |  | TRUE
29 | bus_LV_261-812_0_5_node_41 | 0.4 | n |  | TRUE
30 | bus_LV_261-812_0_5_node_38 | 0.4 | n |  | TRUE
31 | bus_LV_261-812_0_5_node_19 | 0.4 | n |  | TRUE
32 | bus_LV_261-812_0_5_node_22 | 0.4 | n |  | TRUE
33 | bus_LV_261-812_0_5_node_33 | 0.4 | n |  | TRUE
34 | bus_LV_261-812_0_5_node_36 | 0.4 | n |  | TRUE
35 | bus_LV_261-812_0_5_node_47 | 0.4 | n |  | TRUE
36 | bus_LV_261-812_0_5_node_27 | 0.4 | n |  | TRUE
37 | bus_LV_261-812_0_5_node_40 | 0.4 | n |  | TRUE
38 | bus_LV_261-812_0_5_node_39 | 0.4 | n |  | TRUE
39 | bus_LV_261-812_0_5_node_28 | 0.4 | n |  | TRUE
40 | bus_LV_261-812_0_5_node_46 | 0.4 | n |  | TRUE
41 | bus_LV_261-812_0_5_node_56 | 0.4 | n |  | TRUE
42 | bus_LV_261-812_0_5_node_57 | 0.4 | n |  | TRUE
43 | bus_LV_261-812_0_5_node_24 | 0.4 | n |  | TRUE
44 | bus_LV_261-812_0_5_node_25 | 0.4 | n |  | TRUE
45 | bus_LV_261-812_0_5_node_26 | 0.4 | n |  | TRUE
46 | bus_LV_261-812_0_5_node_34 | 0.4 | n |  | TRUE
47 | bus_LV_261-812_0_5_node_32 | 0.4 | n |  | TRUE
48 | bus_LV_261-812_0_5_node_45 | 0.4 | n |  | TRUE
49 | bus_LV_261-812_0_5_node_44 | 0.4 | n |  | TRUE
50 | bus_LV_261-812_0_5_node_42 | 0.4 | n |  | TRUE
51 | bus_LV_261-812_0_5_node_43 | 0.4 | n |  | TRUE
52 | bus_MV_542_0_node_98 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-812_0_5_load_0 | 0 | 0.013091 | 0.003281 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-812_0_5_load_1 | 1 | 0.01003 | 0.0025137 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-812_0_5_load_3 | 3 | 0.010055 | 0.0025201 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-812_0_5_load_55 | 6 | 0.010216 | 0.0025603 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-812_0_5_load_35 | 8 | 0.034056 | 0.0085351 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-812_0_5_load_23 | 9 | 0.0068678 | 0.0017212 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-812_0_5_load_37 | 11 | 0.025412 | 0.0063687 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-812_0_5_load_58 | 13 | 0.0044603 | 0.0011179 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-812_0_5_load_52 | 15 | 0.0072919 | 0.0018275 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-812_0_5_load_54 | 17 | 0.01201 | 0.0030101 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-812_0_5_load_51 | 18 | 0.0049362 | 0.0012371 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-812_0_5_load_53 | 19 | 0.0069046 | 0.0017304 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-812_0_5_load_50 | 20 | 0.010088 | 0.0025283 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-812_0_5_load_49 | 22 | 0.024371 | 0.006108 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-812_0_5_load_48 | 23 | 0.019239 | 0.0048219 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-812_0_5_load_30 | 25 | 0.012704 | 0.003184 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-812_0_5_load_31 | 26 | 0.01166 | 0.0029222 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_261-812_0_5_load_29 | 27 | 0.013929 | 0.0034909 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_261-812_0_5_load_41 | 29 | 0.0049938 | 0.0012516 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_261-812_0_5_load_38 | 30 | 0.0060189 | 0.0015085 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_261-812_0_5_load_22 | 32 | 0.0050125 | 0.0012563 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_261-812_0_5_load_33 | 33 | 0.018623 | 0.0046675 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_261-812_0_5_load_36 | 34 | 0.024527 | 0.006147 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_261-812_0_5_load_47 | 35 | 0.016171 | 0.0040528 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_261-812_0_5_load_39 | 38 | 0.004837 | 0.0012123 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_261-812_0_5_load_46 | 40 | 0.0088342 | 0.002214 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_261-812_0_5_load_56 | 41 | 0.024401 | 0.0061155 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_261-812_0_5_load_57 | 42 | 0.049306 | 0.012357 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_261-812_0_5_load_24 | 43 | 0.0071583 | 0.001794 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_261-812_0_5_load_25 | 44 | 0.0078675 | 0.0019718 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_261-812_0_5_load_26 | 45 | 0.024868 | 0.0062325 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_261-812_0_5_load_34 | 46 | 0.013224 | 0.0033143 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_261-812_0_5_load_32 | 47 | 0.026994 | 0.0067654 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_261-812_0_5_load_45 | 48 | 0.024264 | 0.0060811 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_261-812_0_5_load_44 | 49 | 0.034954 | 0.0087604 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_261-812_0_5_load_42 | 50 | 0.028497 | 0.0071421 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_261-812_0_5_load_43 | 51 | 0.021911 | 0.0054914 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 51 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-812_0_5_line_0 |  | 0 | 1 | 0.016166 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-812_0_5_line_1 |  | 0 | 2 | 0.013747 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-812_0_5_line_2 |  | 1 | 3 | 0.017891 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-812_0_5_line_3 |  | 2 | 4 | 0.032279 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-812_0_5_line_4 |  | 2 | 5 | 0.042052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_261-812_0_5_line_5 |  | 3 | 6 | 0.017979 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_261-812_0_5_line_6 |  | 4 | 7 | 0.005207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
7 | LV_261-812_0_5_line_7 |  | 4 | 8 | 0.010689 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_261-812_0_5_line_8 |  | 5 | 9 | 0.02337 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_261-812_0_5_line_9 |  | 7 | 10 | 0.025377 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_261-812_0_5_line_10 |  | 7 | 11 | 0.022295 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
11 | LV_261-812_0_5_line_11 |  | 8 | 33 | 0.02032 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_261-812_0_5_line_12 |  | 9 | 31 | 0.033985 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-812_0_5_line_13 |  | 10 | 15 | 0.011711 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_261-812_0_5_line_14 |  | 10 | 20 | 0.012771 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_261-812_0_5_line_15 |  | 11 | 34 | 0.015141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
16 | LV_261-812_0_5_line_16 |  | 12 | 13 | 0.026722 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_261-812_0_5_line_17 |  | 12 | 14 | 0.011715 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_261-812_0_5_line_18 |  | 14 | 15 | 0.0026185 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_261-812_0_5_line_19 |  | 16 | 17 | 0.004615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_261-812_0_5_line_20 |  | 16 | 18 | 0.009276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_261-812_0_5_line_21 |  | 16 | 19 | 0.02239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_261-812_0_5_line_22 |  | 18 | 20 | 0.013157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_261-812_0_5_line_23 |  | 21 | 22 | 0.040064 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_261-812_0_5_line_24 |  | 21 | 23 | 0.017015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_261-812_0_5_line_25 |  | 22 | 36 | 0.027674 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_261-812_0_5_line_26 |  | 23 | 35 | 0.021974 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_261-812_0_5_line_27 |  | 24 | 25 | 0.010164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
28 | LV_261-812_0_5_line_28 |  | 24 | 26 | 0.010154 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
29 | LV_261-812_0_5_line_29 |  | 24 | 27 | 0.024094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_261-812_0_5_line_30 |  | 25 | 34 | 0.015509 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
31 | LV_261-812_0_5_line_31 |  | 26 | 37 | 0.01323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
32 | LV_261-812_0_5_line_32 |  | 28 | 29 | 0.0076344 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_261-812_0_5_line_33 |  | 28 | 30 | 0.0086999 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_261-812_0_5_line_34 |  | 30 | 38 | 0.011465 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_261-812_0_5_line_35 |  | 31 | 32 | 0.023171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_261-812_0_5_line_36 |  | 33 | 47 | 0.013931 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_261-812_0_5_line_37 |  | 36 | 39 | 0.05043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_261-812_0_5_line_38 |  | 36 | 40 | 0.01616 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_261-812_0_5_line_39 |  | 37 | 49 | 0.028028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
40 | LV_261-812_0_5_line_40 |  | 37 | 50 | 0.01295 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
41 | LV_261-812_0_5_line_41 |  | 37 | 38 | 0.016923 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_261-812_0_5_line_42 |  | 39 | 41 | 0.006022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_261-812_0_5_line_43 |  | 39 | 42 | 0.007217 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_261-812_0_5_line_44 |  | 40 | 48 | 0.015829 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
45 | LV_261-812_0_5_line_45 |  | 43 | 44 | 0.017916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_261-812_0_5_line_46 |  | 44 | 45 | 0.0091671 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_261-812_0_5_line_47 |  | 45 | 46 | 0.010653 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_261-812_0_5_line_48 |  | 46 | 47 | 0.013238 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_261-812_0_5_line_49 |  | 48 | 49 | 0.012058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
50 | LV_261-812_0_5_line_50 |  | 50 | 51 | 0.028754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-812_0_5_trafo_43 | 0.63 MVA 20/0.4 kV | 52 | 51 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2683219.1112 | 1250181.3237 | 2683225.3449 | 1250196.2396
1 | 2683212.4534 | 1250169.5839 | 2683214.2026 | 1250170.8316 | 2683216.4402 | 1250174.9327 | 2683219.1112 | 1250181.3237
2 | 2683225.3449 | 1250196.2396 | 2683232.2438 | 1250212.7471
3 | 2683196.7554 | 1250142.2655 | 2683202.9366 | 1250155.3286 | 2683208.8025 | 1250167.7313 | 2683211.631 | 1250169.0052 | 2683212.4534 | 1250169.5839
4 | 2683184.2303 | 1250194.3729 | 2683190.0385 | 1250185.6145 | 2683199.959 | 1250171.1208 | 2683202.717 | 1250168.8133 | 2683205.9491 | 1250167.6912 | 2683208.8025 | 1250167.7313 | 2683211.631 | 1250169.0052 | 2683212.4534 | 1250169.5839
5 | 2683232.2438 | 1250212.7471 | 2683239.1767 | 1250229.3357
6 | 2683197.6805 | 1250137.1413 | 2683196.7554 | 1250142.2655
7 | 2683196.7554 | 1250142.2655 | 2683192.6159 | 1250152.12
8 | 2683184.2303 | 1250194.3729 | 2683171.316 | 1250213.8506
9 | 2683197.6805 | 1250137.1413 | 2683204.3259 | 1250134.3658 | 2683210.0917 | 1250131.856 | 2683213.2533 | 1250130.3771 | 2683215.591 | 1250129.5092 | 2683221.0072 | 1250127.1613
10 | 2683197.6805 | 1250137.1413 | 2683193.4391 | 1250121.9594 | 2683190.9083 | 1250115.9384
11 | 2683184.3992 | 1250170.6181 | 2683186.2538 | 1250168.0261 | 2683189.7252 | 1250159.0015 | 2683192.6159 | 1250152.12
12 | 2683152.536 | 1250242.1749 | 2683171.316 | 1250213.8506
13 | 2683221.0072 | 1250127.1613 | 2683223.0054 | 1250128.9574 | 2683226.0362 | 1250130.3454 | 2683229.8916 | 1250131.0778 | 2683231.654 | 1250130.9638
14 | 2683221.0072 | 1250127.1613 | 2683219.2061 | 1250124.2338 | 2683215.8014 | 1250115.6018 | 2683215.7784 | 1250115.5525
15 | 2683190.9083 | 1250115.9384 | 2683185.0414 | 1250101.9807
16 | 2683238.1395 | 1250101.8386 | 2683245.5478 | 1250127.5172
17 | 2683245.5478 | 1250127.5172 | 2683234.2671 | 1250130.7946
18 | 2683234.2671 | 1250130.7946 | 2683231.654 | 1250130.9638
19 | 2683209.5427 | 1250094.0758 | 2683205.2379 | 1250095.7722
20 | 2683205.2379 | 1250095.7722 | 2683209.8687 | 1250103.8096
21 | 2683205.2379 | 1250095.7722 | 2683196.3997 | 1250075.2009
22 | 2683215.7784 | 1250115.5525 | 2683212.1293 | 1250107.7333 | 2683209.8687 | 1250103.8096
23 | 2683053.3467 | 1250070.2121 | 2683076.6826 | 1250102.7778
24 | 2683053.3467 | 1250070.2121 | 2683059.0222 | 1250066.0663 | 2683067.1332 | 1250060.2409
25 | 2683092.8019 | 1250125.2726 | 2683076.6826 | 1250102.7778
26 | 2683067.1332 | 1250060.2409 | 2683074.2839 | 1250055.1053 | 2683084.9895 | 1250047.4336
27 | 2683175.0935 | 1250078.3139 | 2683179.0319 | 1250087.6835
28 | 2683175.0935 | 1250078.3139 | 2683171.2808 | 1250079.9172 | 2683165.7211 | 1250082.2195
29 | 2683175.0935 | 1250078.3139 | 2683166.3159 | 1250055.8754
30 | 2683185.0414 | 1250101.9807 | 2683179.0319 | 1250087.6835
31 | 2683153.4147 | 1250087.0719 | 2683160.269 | 1250084.4772 | 2683165.7211 | 1250082.2195
32 | 2683142.8398 | 1250051.8974 | 2683137.624 | 1250046.3225
33 | 2683142.8398 | 1250051.8974 | 2683142.3851 | 1250055.7828 | 2683143.9769 | 1250060.2984
34 | 2683147.7885 | 1250071.1112 | 2683143.9769 | 1250060.2984
35 | 2683152.536 | 1250242.1749 | 2683171.6918 | 1250255.2117
36 | 2683184.3992 | 1250170.6181 | 2683179.6923 | 1250177.1964 | 2683176.4523 | 1250182.0582
37 | 2683092.8019 | 1250125.2726 | 2683098.5137 | 1250133.0695 | 2683099.8397 | 1250138.6478 | 2683097.7191 | 1250144.5002 | 2683121.4619 | 1250160.8119
38 | 2683092.8019 | 1250125.2726 | 2683105.8793 | 1250115.7798
39 | 2683153.4147 | 1250087.0719 | 2683135.5713 | 1250094.2269 | 2683128.4469 | 1250099.3984
40 | 2683153.4147 | 1250087.0719 | 2683158.3461 | 1250099.0463
41 | 2683153.4147 | 1250087.0719 | 2683147.7885 | 1250071.1112
42 | 2683121.4619 | 1250160.8119 | 2683118.1672 | 1250165.8583
43 | 2683121.4619 | 1250160.8119 | 2683125.562 | 1250154.865
44 | 2683118.6889 | 1250106.4816 | 2683105.8793 | 1250115.7798
45 | 2683158.1196 | 1250209.5671 | 2683148.1842 | 1250224.4755
46 | 2683158.1196 | 1250209.5671 | 2683163.2033 | 1250201.9388
47 | 2683169.1111 | 1250193.0739 | 2683163.2033 | 1250201.9388
48 | 2683169.1111 | 1250193.0739 | 2683176.4523 | 1250182.0582
49 | 2683118.6889 | 1250106.4816 | 2683128.4469 | 1250099.3984
50 | 2683164.27 | 1250125.9308 | 2683166.3526 | 1250118.4878 | 2683158.3461 | 1250099.0463

## bus_geodata
| x | y | coords
0 | 2683219.1112 | 1250181.3237
1 | 2683225.3449 | 1250196.2396
2 | 2683212.4534 | 1250169.5839
3 | 2683232.2438 | 1250212.7471
4 | 2683196.7554 | 1250142.2655
5 | 2683184.2303 | 1250194.3729
6 | 2683239.1767 | 1250229.3357
7 | 2683197.6805 | 1250137.1413
8 | 2683192.6159 | 1250152.12
9 | 2683171.316 | 1250213.8506
10 | 2683221.0072 | 1250127.1613
11 | 2683190.9083 | 1250115.9384
12 | 2683245.5478 | 1250127.5172
13 | 2683238.1395 | 1250101.8386
14 | 2683234.2671 | 1250130.7946
15 | 2683231.654 | 1250130.9638
16 | 2683205.2379 | 1250095.7722
17 | 2683209.5427 | 1250094.0758
18 | 2683209.8687 | 1250103.8096
19 | 2683196.3997 | 1250075.2009
20 | 2683215.7784 | 1250115.5525
21 | 2683053.3467 | 1250070.2121
22 | 2683076.6826 | 1250102.7778
23 | 2683067.1332 | 1250060.2409
24 | 2683175.0935 | 1250078.3139
25 | 2683179.0319 | 1250087.6835
26 | 2683165.7211 | 1250082.2195
27 | 2683166.3159 | 1250055.8754
28 | 2683142.8398 | 1250051.8974
29 | 2683137.624 | 1250046.3225
30 | 2683143.9769 | 1250060.2984
31 | 2683152.536 | 1250242.1749
32 | 2683171.6918 | 1250255.2117
33 | 2683184.3992 | 1250170.6181
34 | 2683185.0414 | 1250101.9807
35 | 2683084.9895 | 1250047.4336
36 | 2683092.8019 | 1250125.2726
37 | 2683153.4147 | 1250087.0719
38 | 2683147.7885 | 1250071.1112
39 | 2683121.4619 | 1250160.8119
40 | 2683105.8793 | 1250115.7798
41 | 2683118.1672 | 1250165.8583
42 | 2683125.562 | 1250154.865
43 | 2683148.1842 | 1250224.4755
44 | 2683158.1196 | 1250209.5671
45 | 2683163.2033 | 1250201.9388
46 | 2683169.1111 | 1250193.0739
47 | 2683176.4523 | 1250182.0582
48 | 2683118.6889 | 1250106.4816
49 | 2683128.4469 | 1250099.3984
50 | 2683158.3461 | 1250099.0463
51 | 2683164.27 | 1250125.9308
52 | 2683153.4147 | 1250087.0719

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98725 | -0.24521 | 0.013091 | 0.003281
1 | 0.9868 | -0.25397 | 0.01003 | 0.0025137
2 | 0.98779 | -0.23455 | 0 | 0
3 | 0.98646 | -0.26047 | 0.010055 | 0.0025201
4 | 0.98943 | -0.20273 | 0 | 0
5 | 0.98734 | -0.24348 | 0 | 0
6 | 0.98629 | -0.26376 | 0.010216 | 0.0025603
7 | 0.98988 | -0.19401 | 0 | 0
8 | 0.98813 | -0.22803 | 0.034056 | 0.0085351
9 | 0.98708 | -0.24844 | 0.0068678 | 0.0017212
10 | 0.98882 | -0.21466 | 0 | 0
11 | 0.99228 | -0.14777 | 0.025412 | 0.0063687
12 | 0.98864 | -0.21826 | 0 | 0
13 | 0.98853 | -0.22038 | 0.0044603 | 0.0011179
14 | 0.98868 | -0.21732 | 0 | 0
15 | 0.98869 | -0.21712 | 0.0072919 | 0.0018275
16 | 0.98797 | -0.23112 | 0 | 0
17 | 0.98792 | -0.23211 | 0.01201 | 0.0030101
18 | 0.98814 | -0.22799 | 0.0049362 | 0.0012371
19 | 0.98783 | -0.23388 | 0.0069046 | 0.0017304
20 | 0.98842 | -0.22239 | 0.010088 | 0.0025283
21 | 0.98849 | -0.22131 | 0 | 0
22 | 0.98979 | -0.19604 | 0.024371 | 0.006108
23 | 0.98793 | -0.23207 | 0.019239 | 0.0048219
24 | 0.99436 | -0.10772 | 0 | 0
25 | 0.99381 | -0.11835 | 0.012704 | 0.003184
26 | 0.99494 | -0.096616 | 0.01166 | 0.0029222
27 | 0.99406 | -0.11364 | 0.013929 | 0.0034909
28 | 0.99533 | -0.089328 | 0 | 0
29 | 0.99529 | -0.089999 | 0.0049938 | 0.0012516
30 | 0.99536 | -0.088563 | 0.0060189 | 0.0015085
31 | 0.98692 | -0.25149 | 0 | 0
32 | 0.98682 | -0.25357 | 0.0050125 | 0.0012563
33 | 0.98628 | -0.26391 | 0.018623 | 0.0046675
34 | 0.993 | -0.13389 | 0.024527 | 0.006147
35 | 0.98761 | -0.23842 | 0.016171 | 0.0040528
36 | 0.99131 | -0.16665 | 0 | 0
37 | 0.99572 | -0.081625 | 0 | 0
38 | 0.99548 | -0.086342 | 0.004837 | 0.0012123
39 | 0.98789 | -0.23281 | 0 | 0
40 | 0.99329 | -0.12847 | 0.0088342 | 0.002214
41 | 0.98776 | -0.23543 | 0.024401 | 0.0061155
42 | 0.98757 | -0.23916 | 0.049306 | 0.012357
43 | 0.98397 | -0.309 | 0.0071583 | 0.001794
44 | 0.98409 | -0.30669 | 0.0078675 | 0.0019718
45 | 0.98421 | -0.30421 | 0.024868 | 0.0062325
46 | 0.98461 | -0.29657 | 0.013224 | 0.0033143
47 | 0.98525 | -0.28393 | 0.026994 | 0.0067654
48 | 0.99432 | -0.10859 | 0.024264 | 0.0060811
49 | 0.99469 | -0.10151 | 0.034954 | 0.0087604
50 | 0.99701 | -0.057097 | 0.028497 | 0.0071421
51 | 1 | 0 | -0.57497 | -0.14579
52 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.030321 | 0.0076066 | -0.030309 | -0.0075987 | 1.2663e-05 | 7.8979e-06 | 0.045704 | 0.045704 | 0.045704 | 0.98725 | -0.24521 | 0.9868 | -0.25397 | 12.5561
1 | -0.043413 | -0.010888 | 0.043435 | 0.010902 | 2.2074e-05 | 1.3951e-05 | 0.065436 | 0.065436 | 0.065436 | 0.98725 | -0.24521 | 0.98779 | -0.23455 | 17.9769
2 | 0.020279 | 0.005085 | -0.020273 | -0.0050812 | 6.2741e-06 | 3.7869e-06 | 0.03058 | 0.03058 | 0.03058 | 0.9868 | -0.25397 | 0.98646 | -0.26047 | 8.4012
3 | -0.055324 | -0.013883 | 0.055408 | 0.013937 | 8.4088e-05 | 5.3402e-05 | 0.083347 | 0.083347 | 0.083347 | 0.98779 | -0.23455 | 0.98943 | -0.20273 | 22.8975
4 | 0.011889 | 0.0029817 | -0.011884 | -0.002979 | 5.0589e-06 | 2.6997e-06 | 0.017911 | 0.017911 | 0.017911 | 0.98779 | -0.23455 | 0.98734 | -0.24348 | 4.9206
5 | 0.010217 | 0.0025611 | -0.010216 | -0.0025603 | 1.6016e-06 | 7.9552e-07 | 0.015413 | 0.015413 | 0.015413 | 0.98646 | -0.26047 | 0.98629 | -0.26376 | 4.2342
6 | -0.18866 | -0.047508 | 0.18874 | 0.047558 | 7.8636e-05 | 5.0193e-05 | 0.2838 | 0.2838 | 0.2838 | 0.98943 | -0.20273 | 0.98988 | -0.19401 | 38.9838
7 | 0.13325 | 0.033572 | -0.13309 | -0.033469 | 0.00016106 | 0.00010294 | 0.20046 | 0.20046 | 0.20046 | 0.98943 | -0.20273 | 0.98813 | -0.22803 | 55.0701
8 | 0.011884 | 0.002979 | -0.011882 | -0.0029775 | 2.8115e-06 | 1.5006e-06 | 0.017911 | 0.017911 | 0.017911 | 0.98734 | -0.24348 | 0.98708 | -0.24844 | 4.9207
9 | 0.045762 | 0.011495 | -0.045717 | -0.011466 | 4.5044e-05 | 2.8503e-05 | 0.068799 | 0.068799 | 0.068799 | 0.98988 | -0.19401 | 0.98882 | -0.21466 | 18.9009
10 | -0.2345 | -0.059053 | 0.23502 | 0.059385 | 0.00051972 | 0.00033204 | 0.3526 | 0.3526 | 0.3526 | 0.98988 | -0.19401 | 0.99228 | -0.14777 | 48.4342
11 | 0.099031 | 0.024933 | -0.098862 | -0.024825 | 0.00016956 | 0.00010826 | 0.14917 | 0.14917 | 0.14917 | 0.98813 | -0.22803 | 0.98628 | -0.26391 | 40.9811
12 | 0.0050137 | 0.0012563 | -0.005013 | -0.0012563 | 7.2802e-07 | 3.1592e-08 | 0.0075581 | 0.0075582 | 0.0075582 | 0.98708 | -0.24844 | 0.98692 | -0.25149 | 2.0764
13 | 0.011754 | 0.002946 | -0.011753 | -0.0029453 | 1.374e-06 | 7.2917e-07 | 0.017688 | 0.017688 | 0.017688 | 0.98882 | -0.21466 | 0.98869 | -0.21712 | 4.8595
14 | 0.033962 | 0.00852 | -0.03395 | -0.0085121 | 1.251e-05 | 7.843e-06 | 0.051111 | 0.051111 | 0.051111 | 0.98882 | -0.21466 | 0.98842 | -0.22239 | 14.0414
15 | -0.26043 | -0.065754 | 0.2606 | 0.065864 | 0.00017334 | 0.00010996 | 0.39071 | 0.39071 | 0.39071 | 0.99228 | -0.14777 | 0.993 | -0.13389 | 21.4674
16 | 0.0044608 | 0.0011178 | -0.0044603 | -0.0011179 | 4.5171e-07 | -5.3517e-08 | 0.0067139 | 0.0067141 | 0.0067141 | 0.98864 | -0.21826 | 0.98853 | -0.22038 | 1.8445
17 | -0.0044608 | -0.0011178 | 0.004461 | 0.0011178 | 1.9803e-07 | -2.3489e-08 | 0.0067139 | 0.0067139 | 0.0067139 | 0.98864 | -0.21826 | 0.98868 | -0.21732 | 1.8445
18 | -0.004461 | -0.0011178 | 0.004461 | 0.0011178 | 4.4263e-08 | -5.2527e-09 | 0.0067139 | 0.0067139 | 0.0067139 | 0.98868 | -0.21732 | 0.98869 | -0.21712 | 1.8445
19 | 0.012011 | 0.0030104 | -0.01201 | -0.0030101 | 5.6635e-07 | 3.0337e-07 | 0.01809 | 0.01809 | 0.01809 | 0.98797 | -0.23112 | 0.98792 | -0.23211 | 4.9698
20 | -0.018916 | -0.0047411 | 0.018919 | 0.0047428 | 2.8235e-06 | 1.6883e-06 | 0.028491 | 0.028491 | 0.028491 | 0.98797 | -0.23112 | 0.98814 | -0.22799 | 7.8271
21 | 0.0069055 | 0.0017307 | -0.0069046 | -0.0017304 | 9.0823e-07 | 2.9459e-07 | 0.010401 | 0.010401 | 0.010401 | 0.98797 | -0.23112 | 0.98783 | -0.23388 | 2.8573
22 | -0.023855 | -0.00598 | 0.023862 | 0.0059839 | 6.3674e-06 | 3.9065e-06 | 0.035924 | 0.035924 | 0.035924 | 0.98814 | -0.22799 | 0.98842 | -0.22239 | 9.8692
23 | -0.035433 | -0.0088889 | 0.035476 | 0.0089158 | 4.2749e-05 | 2.6845e-05 | 0.053343 | 0.053342 | 0.053343 | 0.98849 | -0.22131 | 0.98979 | -0.19604 | 14.6545
24 | 0.035433 | 0.0088889 | -0.035415 | -0.0088775 | 1.8155e-05 | 1.1401e-05 | 0.053343 | 0.053343 | 0.053343 | 0.98849 | -0.22131 | 0.98793 | -0.23207 | 14.6546
25 | -0.059847 | -0.015024 | 0.059931 | 0.015077 | 8.4024e-05 | 5.3419e-05 | 0.089981 | 0.089981 | 0.089981 | 0.98979 | -0.19604 | 0.99131 | -0.16665 | 24.7201
26 | 0.016176 | 0.0040556 | -0.016171 | -0.0040528 | 4.8917e-06 | 2.8494e-06 | 0.024364 | 0.024364 | 0.024364 | 0.98793 | -0.23207 | 0.98761 | -0.23842 | 6.6935
27 | 0.2982 | 0.075426 | -0.29804 | -0.07533 | 0.00015196 | 9.6593e-05 | 0.44648 | 0.44648 | 0.44648 | 0.99436 | -0.10772 | 0.99381 | -0.11835 | 24.532
28 | -0.31213 | -0.078919 | 0.3123 | 0.079025 | 0.00016632 | 0.00010578 | 0.46733 | 0.46733 | 0.46733 | 0.99436 | -0.10772 | 0.99494 | -0.096616 | 25.6776
29 | 0.013933 | 0.0034931 | -0.013929 | -0.0034909 | 3.9279e-06 | 2.2014e-06 | 0.02085 | 0.02085 | 0.02085 | 0.99436 | -0.10772 | 0.99406 | -0.11364 | 5.7281
30 | 0.28534 | 0.072146 | -0.28513 | -0.072011 | 0.00021254 | 0.00013502 | 0.42746 | 0.42746 | 0.42746 | 0.99381 | -0.11835 | 0.993 | -0.13389 | 23.4868
31 | -0.32396 | -0.081947 | 0.32419 | 0.082096 | 0.00023318 | 0.00014838 | 0.48477 | 0.48477 | 0.48477 | 0.99494 | -0.096616 | 0.99572 | -0.081625 | 26.6357
32 | 0.004994 | 0.0012516 | -0.0049938 | -0.0012516 | 1.5958e-07 | 2.9138e-09 | 0.0074661 | 0.0074661 | 0.0074661 | 0.99533 | -0.089328 | 0.99529 | -0.089999 | 2.0511
33 | -0.004994 | -0.0012516 | 0.0049942 | 0.0012516 | 1.8185e-07 | 3.3108e-09 | 0.0074661 | 0.007466 | 0.0074661 | 0.99533 | -0.089328 | 0.99536 | -0.088563 | 2.0511
34 | -0.011013 | -0.0027601 | 0.011014 | 0.0027606 | 1.1654e-06 | 5.968e-07 | 0.016464 | 0.016464 | 0.016464 | 0.99536 | -0.088563 | 0.99548 | -0.086342 | 4.523
35 | 0.005013 | 0.0012563 | -0.0050125 | -0.0012563 | 4.9639e-07 | 2.163e-08 | 0.0075582 | 0.0075583 | 0.0075583 | 0.98692 | -0.25149 | 0.98682 | -0.25357 | 2.0765
36 | 0.080238 | 0.020158 | -0.080162 | -0.020109 | 7.6581e-05 | 4.8834e-05 | 0.12107 | 0.12107 | 0.12107 | 0.98628 | -0.26391 | 0.98525 | -0.28393 | 33.2621
37 | 0.073958 | 0.018633 | -0.073725 | -0.018484 | 0.00023322 | 0.00014861 | 0.11105 | 0.11105 | 0.11105 | 0.99131 | -0.16665 | 0.98789 | -0.23281 | 30.5085
38 | -0.13389 | -0.03371 | 0.13413 | 0.033866 | 0.0002449 | 0.00015653 | 0.20103 | 0.20103 | 0.20103 | 0.99131 | -0.16665 | 0.99329 | -0.12847 | 55.2285
39 | 0.20257 | 0.051166 | -0.20238 | -0.051044 | 0.00019282 | 0.00012158 | 0.30287 | 0.30287 | 0.30287 | 0.99572 | -0.081625 | 0.99469 | -0.10151 | 16.641
40 | -0.54262 | -0.13724 | 0.54326 | 0.13764 | 0.00063934 | 0.00040833 | 0.81133 | 0.81133 | 0.81133 | 0.99572 | -0.081625 | 0.99701 | -0.057097 | 44.5785
41 | 0.015855 | 0.003975 | -0.015851 | -0.0039729 | 3.5628e-06 | 2.0601e-06 | 0.023694 | 0.023694 | 0.023694 | 0.99572 | -0.081625 | 0.99548 | -0.086342 | 6.5094
42 | 0.024404 | 0.0061174 | -0.024401 | -0.0061155 | 3.0514e-06 | 1.8758e-06 | 0.036759 | 0.036759 | 0.036759 | 0.98789 | -0.23281 | 0.98776 | -0.23543 | 10.0987
43 | 0.049321 | 0.012367 | -0.049306 | -0.012357 | 1.4937e-05 | 9.4674e-06 | 0.074292 | 0.074292 | 0.074292 | 0.98789 | -0.23281 | 0.98757 | -0.23916 | 20.4098
44 | -0.14297 | -0.03608 | 0.1431 | 0.036167 | 0.00013625 | 8.6792e-05 | 0.21427 | 0.21427 | 0.21427 | 0.99329 | -0.12847 | 0.99432 | -0.10859 | 29.4321
45 | -0.0071583 | -0.001794 | 0.0071591 | 0.0017943 | 7.8729e-07 | 2.7627e-07 | 0.010825 | 0.010825 | 0.010825 | 0.98397 | -0.309 | 0.98409 | -0.30669 | 2.974
46 | -0.015027 | -0.0037661 | 0.015028 | 0.0037671 | 1.7747e-06 | 1.0193e-06 | 0.022721 | 0.022721 | 0.022721 | 0.98409 | -0.30669 | 0.98421 | -0.30421 | 6.2422
47 | -0.039897 | -0.0099997 | 0.039911 | 0.010009 | 1.4535e-05 | 9.1671e-06 | 0.060319 | 0.060319 | 0.060319 | 0.98421 | -0.30421 | 0.98461 | -0.29657 | 16.5712
48 | -0.053135 | -0.013323 | 0.053167 | 0.013343 | 3.2013e-05 | 2.032e-05 | 0.080305 | 0.080305 | 0.080305 | 0.98461 | -0.29657 | 0.98525 | -0.28393 | 22.0617
49 | -0.16737 | -0.042248 | 0.16743 | 0.042284 | 5.6782e-05 | 3.5558e-05 | 0.25058 | 0.25058 | 0.25058 | 0.99432 | -0.10859 | 0.99469 | -0.10151 | 13.768
50 | -0.57175 | -0.14479 | 0.57332 | 0.14579 | 0.0015723 | 0.0010044 | 0.85386 | 0.85386 | 0.85386 | 0.99701 | -0.057097 | 1 | 0 | 46.9154

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.59689 | 0.15128

## res_load
| p_mw | q_mvar
0 | 0.013091 | 0.003281
1 | 0.01003 | 0.0025137
2 | 0.010055 | 0.0025201
3 | 0.010216 | 0.0025603
4 | 0.034056 | 0.0085351
5 | 0.0068678 | 0.0017212
6 | 0.025412 | 0.0063687
7 | 0.0044603 | 0.0011179
8 | 0.0072919 | 0.0018275
9 | 0.01201 | 0.0030101
10 | 0.0049362 | 0.0012371
11 | 0.0069046 | 0.0017304
12 | 0.010088 | 0.0025283
13 | 0.024371 | 0.006108
14 | 0.019239 | 0.0048219
15 | 0.012704 | 0.003184
16 | 0.01166 | 0.0029222
17 | 0.013929 | 0.0034909
18 | 0.0049938 | 0.0012516
19 | 0.0060189 | 0.0015085
20 | 0.0050125 | 0.0012563
21 | 0.018623 | 0.0046675
22 | 0.024527 | 0.006147
23 | 0.016171 | 0.0040528
24 | 0.004837 | 0.0012123
25 | 0.0088342 | 0.002214
26 | 0.024401 | 0.0061155
27 | 0.049306 | 0.012357
28 | 0.0071583 | 0.001794
29 | 0.0078675 | 0.0019718
30 | 0.024868 | 0.0062325
31 | 0.013224 | 0.0033143
32 | 0.026994 | 0.0067654
33 | 0.024264 | 0.0060811
34 | 0.034954 | 0.0087604
35 | 0.028497 | 0.0071421
36 | 0.021911 | 0.0054914

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1