## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-815_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-815_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-815_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_261-815_0_3_node_21 | 0.4 | n |  | TRUE
4 | bus_LV_261-815_0_3_node_17 | 0.4 | n |  | TRUE
5 | bus_LV_261-815_0_3_node_3 | 0.4 | n |  | TRUE
6 | bus_LV_261-815_0_3_node_5 | 0.4 | n |  | TRUE
7 | bus_LV_261-815_0_3_node_12 | 0.4 | n |  | TRUE
8 | bus_LV_261-815_0_3_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_261-815_0_3_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_261-815_0_3_node_29 | 0.4 | n |  | TRUE
11 | bus_LV_261-815_0_3_node_8 | 0.4 | n |  | TRUE
12 | bus_LV_261-815_0_3_node_20 | 0.4 | n |  | TRUE
13 | bus_LV_261-815_0_3_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_261-815_0_3_node_22 | 0.4 | n |  | TRUE
15 | bus_LV_261-815_0_3_node_28 | 0.4 | n |  | TRUE
16 | bus_LV_261-815_0_3_node_10 | 0.4 | n |  | TRUE
17 | bus_LV_261-815_0_3_node_24 | 0.4 | n |  | TRUE
18 | bus_LV_261-815_0_3_node_13 | 0.4 | n |  | TRUE
19 | bus_LV_261-815_0_3_node_16 | 0.4 | n |  | TRUE
20 | bus_LV_261-815_0_3_node_23 | 0.4 | n |  | TRUE
21 | bus_LV_261-815_0_3_node_30 | 0.4 | n |  | TRUE
22 | bus_LV_261-815_0_3_node_19 | 0.4 | n |  | TRUE
23 | bus_LV_261-815_0_3_node_25 | 0.4 | n |  | TRUE
24 | bus_LV_261-815_0_3_node_27 | 0.4 | n |  | TRUE
25 | bus_LV_261-815_0_3_node_26 | 0.4 | n |  | TRUE
26 | bus_MV_548_0_node_62 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-815_0_3_load_0 | 0 | 0.052479 | 0.013152 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-815_0_3_load_2 | 2 | 0.051296 | 0.012856 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-815_0_3_load_21 | 3 | 0.021469 | 0.0053806 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-815_0_3_load_3 | 5 | 0.0035448 | 0.0008884 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-815_0_3_load_29 | 10 | 0.017764 | 0.0044522 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-815_0_3_load_20 | 12 | 0.0099044 | 0.0024823 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-815_0_3_load_22 | 14 | 0.015127 | 0.0037911 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-815_0_3_load_28 | 15 | 0.038443 | 0.0096346 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-815_0_3_load_24 | 17 | 0.010982 | 0.0027523 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-815_0_3_load_23 | 20 | 0.020692 | 0.0051858 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-815_0_3_load_30 | 21 | 0.0030865 | 0.00077354 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-815_0_3_load_19 | 22 | 0.0086198 | 0.0021603 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-815_0_3_load_25 | 23 | 0.017887 | 0.0044828 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-815_0_3_load_27 | 24 | 0.035271 | 0.0088398 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-815_0_3_load_26 | 25 | 0.035288 | 0.0088441 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 0 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-815_0_3_line_0 |  | 0 | 1 | 0.010052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
1 | LV_261-815_0_3_line_1 |  | 1 | 2 | 0.0070127 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
2 | LV_261-815_0_3_line_2 |  | 2 | 3 | 0.0099281 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
3 | LV_261-815_0_3_line_3 |  | 3 | 4 | 0.0079968 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
4 | LV_261-815_0_3_line_4 |  | 4 | 18 | 0.040642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
5 | LV_261-815_0_3_line_5 |  | 5 | 6 | 0.0076029 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_261-815_0_3_line_6 |  | 6 | 7 | 0.024855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_261-815_0_3_line_7 |  | 7 | 15 | 0.020526 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_261-815_0_3_line_8 |  | 7 | 16 | 0.012245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_261-815_0_3_line_9 |  | 8 | 9 | 0.018734 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_261-815_0_3_line_10 |  | 8 | 10 | 0.038727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_261-815_0_3_line_11 |  | 9 | 11 | 0.002491 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_261-815_0_3_line_12 |  | 9 | 12 | 0.028916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-815_0_3_line_13 |  | 11 | 13 | 0.017036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
14 | LV_261-815_0_3_line_14 |  | 11 | 14 | 0.012781 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
15 | LV_261-815_0_3_line_15 |  | 12 | 22 | 0.025652 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_261-815_0_3_line_16 |  | 13 | 15 | 0.011465 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
17 | LV_261-815_0_3_line_17 |  | 14 | 20 | 0.028978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
18 | LV_261-815_0_3_line_18 |  | 16 | 17 | 0.0031113 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_261-815_0_3_line_19 |  | 17 | 23 | 0.014297 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_261-815_0_3_line_20 |  | 18 | 19 | 0.027926 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_261-815_0_3_line_21 |  | 18 | 20 | 0.042718 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
22 | LV_261-815_0_3_line_22 |  | 19 | 21 | 0.034929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_261-815_0_3_line_23 |  | 23 | 25 | 0.01198 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_261-815_0_3_line_24 |  | 24 | 25 | 0.011997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-815_0_3_trafo_0 | 0.63 MVA 20/0.4 kV | 26 | 0 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12
0 | 2683932.163 | 1247143.4206 | 2683925.2827 | 1247150.7491
1 | 2683932.163 | 1247143.4206 | 2683936.9179 | 1247138.2661
2 | 2683936.9179 | 1247138.2661 | 2683943.6495 | 1247130.9687
3 | 2683949.0716 | 1247125.0908 | 2683943.6495 | 1247130.9687
4 | 2683918.4588 | 1247102.4298 | 2683920.2096 | 1247100.4197 | 2683923.4043 | 1247103.1336 | 2683926.5937 | 1247105.6917 | 2683930.5444 | 1247108.8945 | 2683932.0455 | 1247110.1166 | 2683943.4382 | 1247120.163 | 2683944.5348 | 1247121.1348 | 2683949.0716 | 1247125.0908
5 | 2683863.6936 | 1247221.365 | 2683861.2735 | 1247217.8282 | 2683859.1577 | 1247215.2732
6 | 2683863.6936 | 1247221.365 | 2683864.7133 | 1247220.8346 | 2683865.7102 | 1247220.315 | 2683866.1821 | 1247220.0659 | 2683867.742 | 1247219.2652 | 2683870.1545 | 1247217.9983 | 2683870.7024 | 1247217.717 | 2683871.9808 | 1247217.0568 | 2683877.3519 | 1247211.6955 | 2683878.5345 | 1247210.8672 | 2683879.8392 | 1247209.9516 | 2683882.6315 | 1247208.0008 | 2683883.8446 | 1247207.1506
7 | 2683883.8446 | 1247207.1506 | 2683880.5222 | 1247202.2556 | 2683874.6039 | 1247192.8983 | 2683872.936 | 1247189.7776
8 | 2683883.8446 | 1247207.1506 | 2683885.8356 | 1247210.0476 | 2683888.1244 | 1247212.1815 | 2683890.7682 | 1247213.2531 | 2683893.5352 | 1247213.0921
9 | 2683844.4184 | 1247173.6796 | 2683846.0644 | 1247172.6688 | 2683846.2702 | 1247172.5382 | 2683847.055 | 1247172.0601 | 2683854.0123 | 1247167.7775 | 2683855.986 | 1247166.5601 | 2683856.1841 | 1247166.4406 | 2683857.3653 | 1247165.7123 | 2683859.2498 | 1247166.5284 | 2683860.6878 | 1247166.8712
10 | 2683844.4184 | 1247173.6796 | 2683842.5147 | 1247169.9499 | 2683835.3234 | 1247158.1951 | 2683832.0383 | 1247158.1376 | 2683828.2414 | 1247157.9393 | 2683821.4578 | 1247146.0685
11 | 2683863.0839 | 1247166.2269 | 2683861.6639 | 1247166.7516 | 2683860.6878 | 1247166.8712
12 | 2683860.6878 | 1247166.8712 | 2683846.4873 | 1247141.6821
13 | 2683863.0839 | 1247166.2269 | 2683863.8286 | 1247166.9824 | 2683865.8023 | 1247168.9673 | 2683868.1334 | 1247171.3242 | 2683868.8633 | 1247172.0573 | 2683866.916 | 1247174.0757 | 2683866.1249 | 1247176.066 | 2683866.5924 | 1247177.7294 | 2683867.1429 | 1247178.8602 | 2683867.5319 | 1247179.6663
14 | 2683863.0839 | 1247166.2269 | 2683864.4577 | 1247164.7007 | 2683871.4863 | 1247156.5958
15 | 2683834.5882 | 1247118.962 | 2683842.9063 | 1247135.3299 | 2683846.4873 | 1247141.6821
16 | 2683867.5319 | 1247179.6663 | 2683872.936 | 1247189.7776
17 | 2683871.4863 | 1247156.5958 | 2683890.4714 | 1247134.7032
18 | 2683893.5352 | 1247213.0921 | 2683896.5047 | 1247212.1633
19 | 2683910.2001 | 1247208.0603 | 2683898.3988 | 1247211.5709 | 2683896.5047 | 1247212.1633
20 | 2683918.4588 | 1247102.4298 | 2683897.0026 | 1247084.4797
21 | 2683918.4588 | 1247102.4298 | 2683890.4714 | 1247134.7032
22 | 2683872.9016 | 1247109.8241 | 2683897.0026 | 1247084.4797
23 | 2683921.6842 | 1247204.6487 | 2683918.9868 | 1247205.4465 | 2683910.2001 | 1247208.0603
24 | 2683933.1889 | 1247201.2459 | 2683921.6842 | 1247204.6487

## bus_geodata
| x | y | coords
0 | 2683925.2827 | 1247150.7491
1 | 2683932.163 | 1247143.4206
2 | 2683936.9179 | 1247138.2661
3 | 2683943.6495 | 1247130.9687
4 | 2683949.0716 | 1247125.0908
5 | 2683859.1577 | 1247215.2732
6 | 2683863.6936 | 1247221.365
7 | 2683883.8446 | 1247207.1506
8 | 2683844.4184 | 1247173.6796
9 | 2683860.6878 | 1247166.8712
10 | 2683821.4577 | 1247146.0685
11 | 2683863.0839 | 1247166.2269
12 | 2683846.4873 | 1247141.6821
13 | 2683867.5319 | 1247179.6663
14 | 2683871.4863 | 1247156.5958
15 | 2683872.936 | 1247189.7776
16 | 2683893.5352 | 1247213.0921
17 | 2683896.5047 | 1247212.1633
18 | 2683918.4588 | 1247102.4298
19 | 2683897.0026 | 1247084.4797
20 | 2683890.4714 | 1247134.7032
21 | 2683872.9016 | 1247109.8241
22 | 2683834.5882 | 1247118.962
23 | 2683910.2001 | 1247208.0603
24 | 2683933.1889 | 1247201.2459
25 | 2683921.6842 | 1247204.6487
26 | 2683921.7783 | 1247154.4818

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 1 | 0 | -0.29392 | -0.074364
1 | 0.99911 | -0.016916 | 0 | 0
2 | 0.99849 | -0.028735 | 0.051296 | 0.012856
3 | 0.99777 | -0.042521 | 0.021469 | 0.0053806
4 | 0.99723 | -0.052636 | 0 | 0
5 | 0.98578 | -0.27316 | 0.0035448 | 0.0008884
6 | 0.98581 | -0.27267 | 0 | 0
7 | 0.98589 | -0.27109 | 0 | 0
8 | 0.98894 | -0.21202 | 0 | 0
9 | 0.98924 | -0.20609 | 0 | 0
10 | 0.98831 | -0.22429 | 0.017764 | 0.0044522
11 | 0.98932 | -0.20448 | 0 | 0
12 | 0.98875 | -0.21564 | 0.0099044 | 0.0024823
13 | 0.98858 | -0.2188 | 0 | 0
14 | 0.99002 | -0.19101 | 0.015127 | 0.0037911
15 | 0.98784 | -0.23326 | 0.038443 | 0.0096346
16 | 0.98476 | -0.29295 | 0 | 0
17 | 0.98448 | -0.29851 | 0.010982 | 0.0027523
18 | 0.99453 | -0.10421 | 0 | 0
19 | 0.99445 | -0.10573 | 0 | 0
20 | 0.99174 | -0.15794 | 0.020692 | 0.0051858
21 | 0.99436 | -0.10763 | 0.0030865 | 0.00077354
22 | 0.98855 | -0.21958 | 0.0086198 | 0.0021603
23 | 0.98331 | -0.32128 | 0.017887 | 0.0044828
24 | 0.98214 | -0.34417 | 0.035271 | 0.0088398
25 | 0.98253 | -0.33653 | 0.035288 | 0.0088441
26 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.29227 | 0.074364 | -0.29203 | -0.074212 | 0.00023808 | 0.00015198 | 0.43529 | 0.43529 | 0.43529 | 1 | 0 | 0.99911 | -0.016916 | 39.8618
1 | 0.29203 | 0.074212 | -0.29186 | -0.074106 | 0.00016609 | 0.00010602 | 0.43529 | 0.43529 | 0.43529 | 0.99911 | -0.016916 | 0.99849 | -0.028735 | 39.8618
2 | 0.24057 | 0.06125 | -0.24041 | -0.061148 | 0.00015981 | 0.00010189 | 0.35885 | 0.35885 | 0.35885 | 0.99849 | -0.028735 | 0.99777 | -0.042521 | 32.8615
3 | 0.21894 | 0.055768 | -0.21883 | -0.0557 | 0.00010677 | 6.8023e-05 | 0.32683 | 0.32683 | 0.32683 | 0.99777 | -0.042521 | 0.99723 | -0.052636 | 29.9295
4 | 0.21883 | 0.0557 | -0.21829 | -0.055354 | 0.00054266 | 0.00034571 | 0.32683 | 0.32683 | 0.32683 | 0.99723 | -0.052636 | 0.99453 | -0.10421 | 29.9295
5 | -0.0035448 | -0.0008884 | 0.0035448 | 0.00088836 | 8.1628e-08 | -4.4689e-08 | 0.0053507 | 0.0053507 | 0.0053507 | 0.98578 | -0.27316 | 0.98581 | -0.27267 | 1.47
6 | -0.0035448 | -0.00088836 | 0.0035451 | 0.00088821 | 2.6684e-07 | -1.4613e-07 | 0.0053507 | 0.0053506 | 0.0053507 | 0.98581 | -0.27267 | 0.98589 | -0.27109 | 1.47
7 | -0.10326 | -0.025993 | 0.10345 | 0.026112 | 0.00018708 | 0.00011947 | 0.1559 | 0.1559 | 0.1559 | 0.98589 | -0.27109 | 0.98784 | -0.23326 | 42.8291
8 | 0.099719 | 0.025104 | -0.099615 | -0.025038 | 0.00010407 | 6.6451e-05 | 0.15055 | 0.15055 | 0.15055 | 0.98589 | -0.27109 | 0.98476 | -0.29295 | 41.3592
9 | -0.017775 | -0.0044583 | 0.01778 | 0.0044613 | 5.0255e-06 | 2.9759e-06 | 0.026746 | 0.026746 | 0.026746 | 0.98894 | -0.21202 | 0.98924 | -0.20609 | 7.3479
10 | 0.017775 | 0.0044583 | -0.017764 | -0.0044522 | 1.0389e-05 | 6.1525e-06 | 0.026746 | 0.026746 | 0.026746 | 0.98894 | -0.21202 | 0.98831 | -0.22429 | 7.3479
11 | -0.036314 | -0.0091096 | 0.036317 | 0.0091114 | 2.7875e-06 | 1.752e-06 | 0.054626 | 0.054626 | 0.054626 | 0.98924 | -0.20609 | 0.98932 | -0.20448 | 15.0073
12 | 0.018534 | 0.0046483 | -0.018526 | -0.0046433 | 8.4288e-06 | 5.0234e-06 | 0.02788 | 0.02788 | 0.02788 | 0.98924 | -0.20609 | 0.98875 | -0.21564 | 7.6594
13 | 0.14209 | 0.035871 | -0.14199 | -0.035809 | 9.7347e-05 | 6.1647e-05 | 0.2138 | 0.21381 | 0.21381 | 0.98932 | -0.20448 | 0.98858 | -0.2188 | 19.5792
14 | -0.17841 | -0.044982 | 0.17852 | 0.045056 | 0.00011512 | 7.3185e-05 | 0.26843 | 0.26843 | 0.26843 | 0.98932 | -0.20448 | 0.99002 | -0.19101 | 24.5816
15 | 0.0086214 | 0.002161 | -0.0086198 | -0.0021603 | 1.6194e-06 | 7.075e-07 | 0.012975 | 0.012975 | 0.012975 | 0.98875 | -0.21564 | 0.98855 | -0.21958 | 3.5645
16 | 0.14199 | 0.035809 | -0.14189 | -0.035747 | 9.8266e-05 | 6.2597e-05 | 0.21381 | 0.21381 | 0.21381 | 0.98858 | -0.2188 | 0.98784 | -0.23326 | 29.3689
17 | -0.19365 | -0.048847 | 0.19395 | 0.049042 | 0.00030709 | 0.00019542 | 0.29117 | 0.29117 | 0.29117 | 0.99002 | -0.19101 | 0.99174 | -0.15794 | 26.6636
18 | 0.099615 | 0.025038 | -0.099588 | -0.025021 | 2.6444e-05 | 1.6884e-05 | 0.15055 | 0.15055 | 0.15055 | 0.98476 | -0.29295 | 0.98448 | -0.29851 | 41.3592
19 | 0.088606 | 0.022269 | -0.08851 | -0.022207 | 9.6195e-05 | 6.1383e-05 | 0.13395 | 0.13395 | 0.13395 | 0.98448 | -0.29851 | 0.98331 | -0.32128 | 36.7991
20 | 0.003087 | 0.00077304 | -0.0030867 | -0.00077326 | 2.2338e-07 | -2.1938e-07 | 0.0046185 | 0.0046186 | 0.0046186 | 0.99453 | -0.10421 | 0.99445 | -0.10573 | 1.2688
21 | 0.2152 | 0.054581 | -0.21465 | -0.054228 | 0.00055438 | 0.00035315 | 0.32221 | 0.32221 | 0.32221 | 0.99453 | -0.10421 | 0.99174 | -0.15794 | 29.5066
22 | 0.0030867 | 0.00077326 | -0.0030865 | -0.00077354 | 2.7942e-07 | -2.743e-07 | 0.0046186 | 0.0046188 | 0.0046188 | 0.99445 | -0.10573 | 0.99436 | -0.10763 | 1.2689
23 | 0.070624 | 0.017725 | -0.070572 | -0.017692 | 5.1321e-05 | 3.2694e-05 | 0.10688 | 0.10688 | 0.10688 | 0.98331 | -0.32128 | 0.98253 | -0.33653 | 29.363
24 | -0.035271 | -0.0088398 | 0.035284 | 0.0088478 | 1.2848e-05 | 8.0706e-06 | 0.053438 | 0.053438 | 0.053438 | 0.98214 | -0.34417 | 0.98253 | -0.33653 | 14.6809

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.3464 | 0.087517

## res_load
| p_mw | q_mvar
0 | 0.052479 | 0.013152
1 | 0.051296 | 0.012856
2 | 0.021469 | 0.0053806
3 | 0.0035448 | 0.0008884
4 | 0.017764 | 0.0044522
5 | 0.0099044 | 0.0024823
6 | 0.015127 | 0.0037911
7 | 0.038443 | 0.0096346
8 | 0.010982 | 0.0027523
9 | 0.020692 | 0.0051858
10 | 0.0030865 | 0.00077354
11 | 0.0086198 | 0.0021603
12 | 0.017887 | 0.0044828
13 | 0.035271 | 0.0088398
14 | 0.035288 | 0.0088441

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1